## Sheet3
BaseLine
| Boiler No | Pressure | Installed capacity TPH | Operating Capacity TPH | Steam flow to process TPH | Steam raising ratio | No of days operation | Bagasse consumpation
Season | 1 | 64 | 80 | 85 | 85 | 1.5 | 170 | 231200
| 2 | 64 | 80 | 85 |  | 1.5 | 170 | 231200
| PRDS-1 |  |  |  | 23
| PRDS-2 |  |  |  | 62
| Desuperheating Water |  |  |  | 18
Total Steam flow to process |  |  |  |  | 188
Total Bagasse Consumed in season | [7 empty] | 462400
Bagasse generation- base line
Capacity TCD | Steam requirement TPH | Bagasse generation TPH |  | Operating days | Bagasse generated MT
9000 | 188 | 114.375 |  | 170 | 466650
Bagasse Available |  |  |  |  | 466650
Project Activity
| Boiler No | Pressure |  | Capacity TPH | Steam Flow to process TPH | Steam raising ratio | Steam generated TPH | No of days operation | Bagasse consumpation TPH | PLF | Bagasse consumpation MT
Season | 1 | 64 | 80 | 80 | 88 | 2.08 | 60.5 | 170 | 29.0865 | 100% | 118673.0769
| 2 | 64 | 80 | 80 |  | 2.08 | 60.5 | 170 | 29.0865 | 100% | 118673.0769
| PRDS-2 |  |  |  | 33
| Desuperheating Water |  |  |  | 9
| From 170 TPH (Project) boiler |  |  |  | 27 | 2.8 | 134.5 | 170 | 48.0357 | 80% | 156788.5714
Total Steam flow to process |  |  |  |  | 157
Total Bagasse Consumed in season | [7 empty] | 170 | 106.2088 |  | 394134.7253
Surplus Bagasse | [10 empty] | 72515.2747
Off Season | From project boiler |  |  |  |  | 2.8 | 101.5 | 104.1886 | 36.25 | 80% | 72515.2747
Validation comment:-
In the project activity, Steam supplied through PRDS 1 will be catered by new boiler(Project activity).
Total steam consumption pre-project was 188 MT. The company has inititated steam conservation efforts.
Refer the attached annexure on Effiiciency improvement.
Steam requirement for the project acitivity during the off season is only 102 TPH. This is mainly due to
only power during the off-season.
PDD has given a model calculation for emission reduction for 300 days. However the above balance has given the
estimate that total power generation would be 274 days only. Hence the emission reduction can vary depending on the actual operating days.
Actual certified may be decided at the time verification.
Note on F4: shwetasingh: In the base case existing boiler will be marginally overloaded for which features are available as the boilers were originally designed for high ash coal. As per initial assesment upto 15% overloading can be done with marginal panelaty on efficiency
Note on F5: shwetasingh: In the base case existing boiler will be marginally overloaded for which features are available as the boilers were originally designed for high ash coal. As per initial assesment upto 15% overloading can be done with marginal panelaty on efficiency
Note on G27: I,provements in steam consumption has resulted in 31 t reduction in steam consumption. Refer the annexure.
Note on H21: shwetasingh: Efficiency enhancement of the boilers partly due to new measures and partly due to more optimum loading
Note on H22: shwetasingh: Efficiency enhancement of the boilers partly due to new measures and partly due to more optimum loading
Note on H25: shwetasingh: New project designed for high efficiency
Note on J10: shwetasingh: Bagasse generation is marginally higher. This amount accounts for wastage which happens due to offseasonal storage