## Calculations (2)
Pre Project Steam and Bagasse balance
| Boiler No | Pressure | TPH | Steam to process TPH | Steam raising ratio | Operating capacity | No of days operation | Bagasse consumpation
| 1 |  | 80 | 297 | 1.8 | 100% | 160 | 170666.6667
| 2 | 32 | 50 |  | 1.7 | 100% | 160 | 112941.1765
| 3 | 32 | 60 |  | 1.7 | 100% | 160 | 135529.4118
Season | 4 | 32 | 20 |  | 1.7 | 100% | 160 | 45176.4706
| 5 | 21 | 30 |  | 1.7 | 100% | 160 | 67764.7059
| 6 | 21 | 20 |  | 1.7 | 100% | 160 | 45176.4706
| 7 | 21 | 25 |  | 1.7 | 100% | 160 | 56470.5882
|  |  | 285 |  | $
Off season |  |  |  | 40 | 1.7 | 100% | 140 | 79058.8235
712784.3137
$ increase is due to desuperheating
40 T of steam is supplied to Chemical Plant through PRDS.
Post Project Steam and Bagasse Balance with existing system
| Boiler No | Pressure | TPH | steam to process TPH | Steam raising ratio(Guranteed) | Operating capacity | No of days operation | Bagasse consumpation
| 1 | 64 | 80 | 257.075 | 2.075 | 81% | 160 | 119919.0361
| 2 | 32 | 50 |  | 2.075 | 81% | 160 | 74949.3976
| 3 | 32 | 60 |  | 2.075 | 81% | 160 | 89939.2771
Season | 4 | 32 | 20 |  | 2.075 | 81% | 160 | 29979.759
| 5 | 21 | 30 |  | 2.075 | 81% | 160 | 44969.6386
| 6 | 21 | 20 |  | 2.075 | 81% | 160 | 29979.759
| 7 | 21 | 25 |  | 2.075 | 81% | 160 | 37474.6988
Total |  |  |  | 257.075 |  |  |  | 427211.5663
|  |  | Net bagasse available for project activity |  |  |  |  | 285572.7475
Efficiency improvements has enhanced the steam ratio to 2.075
Efficiecncy improvements include reducing steam leakages from pipelines and improvement in Insultations.
Balance for project activity
| Steam Requirement for the turbine |  |  | 139 | TPH |  | Guranteed
| Steam Raising Ratio |  |  | 2.8 |  |  | Guranteed
| Bagasse Requirement |  |  | 49.6429 | TPH
| Bagasse Requirement |  |  | 1191.4286 | TPD
| Net Bagasse available |  |  | 285572.7475 | MT
| No of days at 100% PLF |  |  | 239.6894 | Days
| No of days at 80% PLF |  |  | 299.6117 | Days
40 T steam to Chemical Plant is supplied from project activity.
Note:-
| Total steam |  | 257 | TPH
| Desuperheating |  | 26 | TPH
| Actual steam |  | 231 | TPH
| Peak boiler loading |  | 87%
| Assumed PLF |  | 80%
Cane crushing capacity of the Sugar plant: |  |  |  | 13500 | TCD
| Bagasse availability for the year |  |  | 712800 | T
12.5MW
10 MW
15 MW
2.5 MW
Sugar +Chemical= 20MW
Power togrid 21.4MW
Power 41.4MW
To Process (Sugar + Chemical) steam = 297TPH
30 MW
HP-LP Heater & Dearator
170TPH-105kg/cm2
30 MW
HP-LP Heater & Dearator
Chemical Plant
Plant 4MW
Grid 25.6MW