## Medidor caudal antorcha
FAILURES IN THE FLOW METER OF THE FLARE
Date of the missing record | Duration | Flow during the 7 days after Average | [6 empty] | Average calculated | Average estimated
| from __ h | date | date | date | date | date | date | date | Nm3/h
| until __ h | 2007-11-06 | 2007-11-07 | 2007-11-08 | 2007-11-09 | 2007-11-10 | 2007-11-11 | 2007-11-12 |  | Nm3
|  | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h
2007-11-13 | 02:00 – 10:00 | 2076 | 2205 | 2223 | 2155 | 2169 | 2124 | 2134 | 2155 | 17240
Fail Flow meter:
13/11/2007: Evidenced fail at 2:00h until 10:00h while the flare continue in operation but the flow meter does not register correctly the biogass (Nm3/h). Total average of the last 7 days was calculated.

## 13-11-07
Date | Amount of landfill gas collected from project wells | Methane fraction in the landfill gas | Amount of landfill gas used for electricity generation | Amount of landfill gas flared | Amount of electricity generated | Combustion efficiencia | Flare 1 working hours | Flare 2 working hours | Flare 3 working hours | Flare 4 working hours | Flare 5 working hours | Flare 1 temperature | Flare 2 temperature | Flare 3 temperature | Flare 4 temperature | Flare 5 temperature | Amount of CERs
| [Nmc] | [%] | [Nmc] | [Nmc] | [KW*h] | [%] | [h] | [h] | [h] | [h] | [h] | [°C] | [°C] | [°C] | [°C] | [°C] | [tCO2e]
2007-11-13 | 18004805 | 40.2 | 526889 | 17477916 | 519279 | 1 | 5008 | 4415 | 6079 | 3599 | 3259 | 998.8 | 999.6 | 999.6 | 0 | 0 | 139564
2007-11-13 01:00 | 18007025 | 40.1 | 526889 | 17480136 | 519279 | 1 | 5009 | 4416 | 6080 | 3599 | 3259 | 998.8 | 999.6 | 999.6 | 0 | 0 | 139578
2007-11-13 02:00 | 18008385 | 39.3 | 526889 | 17481496 | 519279 | 1 | 5010 | 4417 | 6081 | 3599 | 3259 | 998.8 | 999.6 | 999.6 | 0 | 0 | 139587
2007-11-13 03:00 | 18008385 | 39.1 | 526889 | 17481496 | 519279 | 1 | 5011 | 4418 | 6082 | 3599 | 3259 | 999.2 | 999.6 | 999.6 | 0 | 0 | 139587
2007-11-13 04:00 | 18008385 | 39.4 | 526889 | 17481496 | 519279 | 1 | 5012 | 4419 | 6083 | 3599 | 3259 | 999.2 | 999.6 | 999.6 | 0 | 0 | 139587
2007-11-13 05:00 | 18008385 | 38.6 | 526889 | 17481496 | 519279 | 1 | 5013 | 4420 | 6084 | 3599 | 3259 | 997.6 | 999.6 | 999.6 | 0 | 0 | 139587
2007-11-13 06:00 | 18008385 | 39.1 | 526889 | 17481496 | 519279 | 1 | 5014 | 4421 | 6085 | 3599 | 3259 | 998 | 999.6 | 999.6 | 0 | 0 | 139587
2007-11-13 07:00 | 18008385 | 39.4 | 526889 | 17481496 | 519279 | 1 | 5015 | 4422 | 6086 | 3599 | 3259 | 998 | 999.6 | 999.6 | 0 | 0 | 139587
2007-11-13 08:00 | 18008385 | 41 | 526889 | 17481496 | 519279 | 1 | 5016 | 4423 | 6087 | 3599 | 3259 | 996.4 | 999.6 | 999.6 | 0 | 0 | 139587
2007-11-13 09:00 | 18008385 | 40.5 | 526889 | 17481516 | 519279 | 1 | 5017 | 4424 | 6088 | 3599 | 3259 | 990.4 | 990.8 | 990.4 | 0 | 0 | 139587
2007-11-13 10:00 | 18008385 | 40.5 | 526889 | 17481516 | 519279 | 1 | 5017 | 4424 | 6088 | 3599 | 3259 | 990.4 | 990.8 | 990.4 | 0 | 0 | 139587
2007-11-13 11:00 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2007-11-13 12:00 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2007-11-13 13:00 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2007-11-13 14:00 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2007-11-13 15:00 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2007-11-13 16:00 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2007-11-13 17:00 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2007-11-13 18:00 | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A | #N/A
2007-11-13 19:00 | 18010525 | 48.6 | 526889 | 17483646 | 519279 | 1 | 5018 | 4425 | 6089 | 3599 | 3259 | 982.8 | 948 | 969.2 | 0 | 0 | 139596
2007-11-13 20:00 | 18012715 | 46.9 | 526889 | 17485826 | 519279 | 1 | 5019 | 4426 | 6090 | 3599 | 3259 | 998.8 | 940.4 | 998 | 0 | 0 | 139613
2007-11-13 21:00 | 18014905 | 46.1 | 526889 | 17488016 | 519279 | 1 | 5020 | 4427 | 6091 | 3599 | 3259 | 999.6 | 978 | 999.6 | 0 | 0 | 139629
2007-11-13 22:00 | 18017055 | 45.4 | 526889 | 17490166 | 519279 | 1 | 5021 | 4428 | 6092 | 3599 | 3259 | 997.2 | 935.6 | 999.6 | 0 | 0 | 139645
2007-11-13 23:00 | 18019225 | 44.6 | 526889 | 17492336 | 519279 | 1 | 5022 | 4429 | 6093 | 3599 | 3259 | 999.6 | 917.2 | 999.6 | 0 | 0 | 139661
Note on B10: garciam: El registro de caudal se detiene, la Planta sigue funcionando (ver T° antorchas y aumento de horas de funcionamiento)

## Medidor caudal GE
FAILURES IN THE FLOW METER OF THE ENGINE
Date of the missing record | Duration | Flow during the 7 days after Average | [6 empty] | Average calculated | avegare estimated
| from __ h | Date 22/04 | Date 23/04 | Date 24/04 | Date 25/04 | Date 26/04 | Date 27/04 | Date 28/04 | Nm3/h
| until __ h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h |  | Nm3
2007-04-29 | 02:00-24:00 | 59 | 57 | 56 | 37 | 55 | 55 | 77 | 57 | 1198
|  | Datos 23/04 | Datos 24/04 | Datos 25/04 | Datos 26/04 | Datos 27/04 | Datos 28/04 | Datos 29/04
|  | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h
2007-04-30 | 00:00-24:00 | 57 | 56 | 39 | 55 | 55 | 75 | 57 | 56 | 1302
|  | Datos 24/04 | Datos 25/04 | Datos 26/04 | Datos 27/04 | Datos 28/04 | Datos 29/04 | Datos 30/04
|  | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h
2007-05-01 | 00:00-24:00 | 56 | 39 | 55 | 55 | 75 | 57 | 56 | 56 | 1308
|  | Datos 25/04 | Datos 26/04 | Datos 27/04 | Datos 28/04 | Datos 29/04 | Datos 30/04 | Datos 01/05
|  | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h
2007-05-02 | 00:00-24:00 | 39 | 55 | 55 | 75 | 57 | 56 | 56 | 56.1429 | 1333.4286
|  | Datos 26/04 | Datos 27/04 | Datos 28/04 | Datos 29/04 | Datos 30/04 | Datos 01/05 | Datos 02/05
|  | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h
2007-05-03 | 00:00-24:00 | 55 | 55 | 75 | 57 | 56 | 56 | 56 | 59 | 1416
|  | Datos 27/04 | Datos 28/04 | Datos 29/04 | Datos 30/04 | Datos 01/04 | Datos 02/05 | Datos 03/05
|  | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h | Nm3/h
2007-05-04 | 00:00-17:00 | 55 | 55 | 57 | 56 | 56 | 56 | 59 | 56 | 952
Fail Flow meter:
29/4/2007: Evidenced fail at 3:00h while the electric energy continue to be generated but the flow meter does not register correctly the biogass (Nm3/h). Total efective registered is 56Nm3/h that should be deducted in the spreadsheet.
30/4/2007: Evidenced fail all day while the electric energy continue to be generated but the flow meter does not register correctly the biogass (Nm3/h). Total efective registered is 42Nm3/h that should be deducted in the spreadsheet.
01/5/2007: Evidenced fail all day while the electric energy continue to be generated but the flow meter does not register correctly the biogass (Nm3/h). Total efective registered is 36Nm3/h that should be deducted in the spreadsheet.
02/5/2007: Evidenced fail all day while the electric energy continue to be generated but the flow meter does not register correctly the biogass (Nm3/h). Total efective registered is 14Nm3/h that should be deducted in the spreadsheet.
03/5/2007: Evidenced fail all day while the electric energy continue to be generated but the flow meter does not register correctly the biogass (Nm3/h). Total efective registered is 0Nm3/h. Nothing to be deducted in the spreadsheet.
04/5/2007: Evidenced fail for 17h while the electric energy continue to be generated but the flow meter does not register correctly the biogass (Nm3/h). Total efective registered is 0Nm3/h. Nothing to be deducted in the spreadsheet.
Note on K5: garciam: (Valor promedio horario*22hs de fallas de registro)-caudal contabilizado. See spreadsheet 29-4-07, 22h is correctly used.

## 29-4-07
Date | Amount of landfill gas collected from project wells | Methane fraction in the landfill gas | Amount of landfill gas used for electricity generation | Amount of landfill gas flared | Amount of electricity generated | Combustion efficiencia | Flare 1 working hours | Flare 2 working hours | Flare 3 working hours | Flare 4 working hours | Flare 5 working hours | Flare 1 temperature | Flare 2 temperature | Flare 3 temperature | Flare 4 temperature | Flare 5 temperature | Amount of CERs
| [Nmc] | [%] | [Nmc] | [Nmc] | [KW*h] | [%] | [h] | [h] | [h] | [h] | [h] | [°C] | [°C] | [°C] | [°C] | [°C] | [tCO2e]
2007-04-29 | 9494987 | 51.6 | 278621 | 9216366 | 286925 | 1 | 2770 | 3022 | 3580 | 1472 | 1303 | 9.2 | 999.6 | 12.8 | 1027.6 | 9.6 | 76161
2007-04-29 01:00 | 9496526 | 51.6 | 278730 | 9217796 | 286976 | 1 | 2770 | 3023 | 3580 | 1473 | 1303 | 9.6 | 999.6 | 12.4 | 1024.4 | 9.6 | 76174
2007-04-29 02:00 | 9498091 | 51.4 | 278855 | 9219236 | 287028 | 1 | 2770 | 3024 | 3580 | 1474 | 1303 | 10.4 | 999.6 | 12 | 1020.4 | 10.4 | 76186
2007-04-29 03:00 | 9499552 | 51.5 | 278876 | 9220676 | 287079 | 1 | 2770 | 3025 | 3580 | 1475 | 1303 | 10.8 | 1000 | 13.2 | 1023.2 | 10.8 | 76198
2007-04-29 04:00 | 9501003 | 51.3 | 278877 | 9222126 | 287130 | 1 | 2770 | 3026 | 3580 | 1476 | 1303 | 10 | 999.6 | 12.4 | 1024.8 | 10 | 76210
2007-04-29 05:00 | 9502458 | 51.5 | 278892 | 9223566 | 287182 | 1 | 2770 | 3027 | 3580 | 1477 | 1303 | 9.6 | 999.6 | 11.6 | 1026.4 | 9.6 | 76222
2007-04-29 06:00 | 9503898 | 51.4 | 278892 | 9225006 | 287232 | 1 | 2770 | 3028 | 3580 | 1478 | 1303 | 9.6 | 999.6 | 11.2 | 1014.4 | 9.2 | 76234
2007-04-29 07:00 | 9505320 | 51.2 | 278894 | 9226426 | 287283 | 1 | 2770 | 3029 | 3580 | 1479 | 1303 | 9.2 | 999.6 | 11.2 | 1015.6 | 8.8 | 76246
2007-04-29 08:00 | 9506760 | 51.3 | 278894 | 9227866 | 287330 | 1 | 2770 | 3030 | 3580 | 1480 | 1303 | 8.8 | 1000 | 10.8 | 1024.4 | 8.4 | 76258
2007-04-29 09:00 | 9508180 | 51.7 | 278894 | 9229286 | 287374 | 1 | 2770 | 3031 | 3580 | 1481 | 1303 | 10 | 999.6 | 12.4 | 1014.8 | 10.8 | 76270
2007-04-29 10:00 | 9509580 | 52 | 278894 | 9230686 | 287418 | 1 | 2770 | 3032 | 3580 | 1482 | 1303 | 12.4 | 999.6 | 14.4 | 1020 | 12.8 | 76281
2007-04-29 11:00 | 9510980 | 52.2 | 278894 | 9232086 | 287462 | 1 | 2770 | 3033 | 3580 | 1483 | 1303 | 13.6 | 999.6 | 16.4 | 1019.2 | 14.4 | 76293
2007-04-29 12:00 | 9512380 | 52.3 | 278894 | 9233486 | 287507 | 1 | 2770 | 3034 | 3580 | 1484 | 1303 | 15.2 | 999.6 | 18 | 1016.8 | 16 | 76305
2007-04-29 13:00 | 9513770 | 52.7 | 278894 | 9234876 | 287551 | 1 | 2770 | 3035 | 3580 | 1485 | 1303 | 16 | 999.6 | 19.2 | 1016.8 | 17.2 | 76317
2007-04-29 14:00 | 9515152 | 53 | 278896 | 9236256 | 287596 | 1 | 2770 | 3036 | 3580 | 1486 | 1303 | 16.8 | 999.6 | 20 | 1015.6 | 18 | 76329
2007-04-29 15:00 | 9516543 | 52.9 | 278897 | 9237656 | 287640 | 1 | 2770 | 3037 | 3580 | 1487 | 1303 | 17.2 | 999.6 | 20.8 | 1019.2 | 18.4 | 76341
2007-04-29 16:00 | 9517933 | 52.6 | 278897 | 9239036 | 287683 | 1 | 2770 | 3038 | 3580 | 1488 | 1303 | 17.6 | 1000 | 20.8 | 1023.6 | 19.2 | 76352
2007-04-29 17:00 | 9519335 | 52.4 | 278899 | 9240436 | 287727 | 1 | 2770 | 3039 | 3580 | 1489 | 1303 | 17.2 | 999.6 | 19.6 | 1022.4 | 18 | 76364
2007-04-29 18:00 | 9520755 | 52.2 | 278899 | 9241856 | 287771 | 1 | 2770 | 3040 | 3580 | 1490 | 1303 | 15.6 | 999.6 | 18.4 | 1013.6 | 16.8 | 76377
2007-04-29 19:00 | 9522185 | 51.4 | 278899 | 9243286 | 287817 | 1 | 2770 | 3041 | 3580 | 1491 | 1303 | 14 | 999.6 | 16.4 | 1030 | 14.8 | 76389
2007-04-29 20:00 | 9523625 | 51.7 | 278899 | 9244726 | 287867 | 1 | 2770 | 3042 | 3580 | 1492 | 1303 | 12.8 | 999.6 | 15.2 | 1028 | 13.2 | 76400
2007-04-29 21:00 | 9525055 | 51.7 | 278899 | 9246156 | 287917 | 1 | 2770 | 3043 | 3580 | 1493 | 1303 | 12 | 999.6 | 14.8 | 1020.8 | 12.4 | 76413
2007-04-29 22:00 | 9526487 | 51.3 | 278911 | 9247576 | 287966 | 1 | 2770 | 3044 | 3580 | 1494 | 1303 | 13.6 | 999.2 | 16 | 1025.6 | 14.4 | 76425
2007-04-29 23:00 | 9527907 | 51.5 | 278911 | 9248996 | 288015 | 1 | 2770 | 3045 | 3580 | 1495 | 1303 | 11.6 | 999.6 | 14 | 1016.8 | 12 | 76437
2007-04-30 | 9529327 | 51.5 | 278911 | 9250416 | 288066 | 1 | 2770 | 3046 | 3580 | 1496 | 1303 | 12.8 | 999.6 | 15.6 | 1026 | 13.2 | 76448
2007-04-28 02:00 |  |  | 125 |  | 52
2007-04-29 03:00 |  |  | 21 |  | 51 |  | Evidenced fail at 3:00h while the electric energy continue to be generated but the flow meter does not register correctly the biogass (Nm3/h). Total efective registered is 56Nm3/h that should be deducted in the spreadsheet.
2007-04-29 04:00 |  |  | 1 |  | 51
2007-04-29 05:00 |  |  | 15 |  | 52
2007-04-29 06:00 |  |  | 0 |  | 50
2007-04-29 07:00 |  |  | 2 |  | 51
2007-04-29 08:00 |  |  | 0 |  | 47
2007-04-29 09:00 |  |  | 0 |  | 44
2007-04-29 10:00 |  |  | 0 |  | 44
2007-04-29 11:00 |  |  | 0 |  | 44
2007-04-29 12:00 |  |  | 0 |  | 45
2007-04-29 13:00 |  |  | 0 |  | 44
2007-04-29 14:00 |  |  | 2 |  | 45
2007-04-29 15:00 |  |  | 1 |  | 44
2007-04-29 16:00 |  |  | 0 |  | 43
2007-04-29 17:00 |  |  | 2 |  | 44
2007-04-29 18:00 |  |  | 0 |  | 44
2007-04-29 19:00 |  |  | 0 |  | 46
2007-04-29 20:00 |  |  | 0 |  | 50
2007-04-29 21:00 |  |  | 0 |  | 50
2007-04-29 22:00 |  |  | 12 |  | 49
2007-04-29 23:00 |  |  | 0 |  | 49
2007-04-30 |  |  | 0 |  | 51
| Total = |  | 56

## 30-4-07
Date | Amount of landfill gas collected from project wells | Methane fraction in the landfill gas | Amount of landfill gas used for electricity generation | Amount of landfill gas flared | Amount of electricity generated | Combustion efficiencia | Flare 1 working hours | Flare 2 working hours | Flare 3 working hours | Flare 4 working hours | Flare 5 working hours | Flare 1 temperature | Flare 2 temperature | Flare 3 temperature | Flare 4 temperature | Flare 5 temperature | Amount of CERs
| [Nmc] | [%] | [Nmc] | [Nmc] | [KW*h] | [%] | [h] | [h] | [h] | [h] | [h] | [°C] | [°C] | [°C] | [°C] | [°C] | [tCO2e]
2007-04-30 | 9529327 | 51.5 | 278911 | 9250416 | 288066 | 1 | 2770 | 3046 | 3580 | 1496 | 1303 | 12.8 | 999.6 | 15.6 | 1026 | 13.2 | 76448
2007-04-30 01:00 | 9530740 | 51.6 | 278914 | 9251826 | 288117 | 1 | 2770 | 3047 | 3580 | 1497 | 1303 | 12.8 | 999.6 | 15.2 | 1021.2 | 12.8 | 76460
2007-04-30 02:00 | 9532170 | 51.5 | 278914 | 9253256 | 288168 | 1 | 2770 | 3048 | 3580 | 1498 | 1303 | 12.4 | 1000 | 14.8 | 1014 | 12.8 | 76472
2007-04-30 03:00 | 9533580 | 51.5 | 278914 | 9254666 | 288218 | 1 | 2770 | 3049 | 3580 | 1499 | 1303 | 12.4 | 999.6 | 14.8 | 1022 | 12.4 | 76484
2007-04-30 04:00 | 9535000 | 51.9 | 278914 | 9256086 | 288268 | 1 | 2770 | 3050 | 3580 | 1500 | 1303 | 12 | 999.6 | 14.4 | 1013.2 | 12 | 76496
2007-04-30 05:00 | 9536420 | 51.7 | 278914 | 9257506 | 288318 | 1 | 2770 | 3051 | 3580 | 1501 | 1303 | 10.8 | 999.6 | 14 | 1020 | 12 | 76508
2007-04-30 06:00 | 9537830 | 51.4 | 278914 | 9258916 | 288369 | 1 | 2770 | 3052 | 3580 | 1502 | 1303 | 11.2 | 999.6 | 13.6 | 1017.6 | 11.2 | 76520
2007-04-30 07:00 | 9539240 | 51.1 | 278914 | 9260326 | 288419 | 1 | 2770 | 3053 | 3580 | 1503 | 1303 | 10.8 | 999.6 | 13.6 | 1023.2 | 10.8 | 76531
2007-04-30 08:00 | 9540660 | 51.3 | 278914 | 9261746 | 288466 | 1 | 2770 | 3054 | 3580 | 1504 | 1303 | 11.2 | 999.6 | 12.8 | 1019.2 | 11.2 | 76543
2007-04-30 09:00 | 9542056 | 51.3 | 278920 | 9263136 | 288511 | 1 | 2770 | 3055 | 3580 | 1505 | 1303 | 12.8 | 999.6 | 15.2 | 1018.8 | 12.8 | 76555
2007-04-30 10:00 | 9543476 | 51.9 | 278920 | 9264556 | 288557 | 1 | 2770 | 3056 | 3580 | 1506 | 1303 | 14 | 999.6 | 16.4 | 1029.6 | 14.8 | 76567
2007-04-30 11:00 | 9544926 | 52.1 | 278920 | 9266006 | 288603 | 1 | 2770 | 3057 | 3580 | 1507 | 1303 | 15.6 | 999.6 | 17.6 | 1030 | 16 | 76579
2007-04-30 12:00 | 9546366 | 52.6 | 278920 | 9267446 | 288649 | 1 | 2770 | 3058 | 3580 | 1508 | 1303 | 16.8 | 999.6 | 19.6 | 1028 | 17.6 | 76591
2007-04-30 13:00 | 9547806 | 53 | 278920 | 9268886 | 288694 | 1 | 2770 | 3059 | 3580 | 1509 | 1303 | 18.4 | 999.6 | 21.6 | 1030 | 19.2 | 76603
2007-04-30 14:00 | 9549256 | 53.4 | 278920 | 9270336 | 288739 | 1 | 2770 | 3060 | 3580 | 1510 | 1303 | 18.8 | 999.6 | 22.8 | 1022 | 20.4 | 76616
2007-04-30 15:00 | 9550721 | 53.2 | 278925 | 9271796 | 288785 | 1 | 2770 | 3061 | 3580 | 1511 | 1303 | 20 | 999.6 | 23.2 | 1038.4 | 21.6 | 76629
2007-04-30 16:00 | 9552179 | 52.7 | 278933 | 9273246 | 288832 | 1 | 2770 | 3062 | 3580 | 1512 | 1303 | 19.2 | 999.6 | 22.4 | 1024 | 20.8 | 76641
2007-04-30 17:00 | 9553639 | 52.6 | 278933 | 9274706 | 288877 | 1 | 2770 | 3063 | 3580 | 1513 | 1303 | 19.6 | 999.6 | 22.4 | 1024.8 | 20.8 | 76654
2007-04-30 18:00 | 9555089 | 52 | 278933 | 9276156 | 288922 | 1 | 2770 | 3064 | 3580 | 1514 | 1303 | 18.8 | 999.6 | 21.6 | 1024.4 | 19.6 | 76666
2007-04-30 19:00 | 9556532 | 51.4 | 278936 | 9277596 | 288970 | 1 | 2770 | 3065 | 3580 | 1515 | 1303 | 18 | 999.6 | 20.4 | 1018.8 | 18.8 | 76679
2007-04-30 20:00 | 9557992 | 50.8 | 278936 | 9279056 | 289022 | 1 | 2770 | 3066 | 3580 | 1516 | 1303 | 17.6 | 999.6 | 20 | 1015.2 | 18 | 76691
2007-04-30 21:00 | 9559452 | 51 | 278936 | 9280516 | 289074 | 1 | 2770 | 3067 | 3580 | 1517 | 1303 | 16.8 | 999.6 | 19.2 | 1015.6 | 17.6 | 76703
2007-04-30 22:00 | 9560894 | 50.8 | 278938 | 9281956 | 289125 | 1 | 2770 | 3068 | 3580 | 1518 | 1303 | 17.2 | 999.6 | 19.6 | 1013.2 | 17.6 | 76715
2007-04-30 23:00 | 9562345 | 51.1 | 278939 | 9283406 | 289175 | 1 | 2770 | 3069 | 3580 | 1519 | 1303 | 17.2 | 999.6 | 19.6 | 1016.8 | 17.2 | 76727

## 01-5-07
Date | Amount of landfill gas collected from project wells | Methane fraction in the landfill gas | Amount of landfill gas used for electricity generation | Amount of landfill gas flared | Amount of electricity generated | Combustion efficiencia | Flare 1 working hours | Flare 2 working hours | Flare 3 working hours | Flare 4 working hours | Flare 5 working hours | Flare 1 temperature | Flare 2 temperature | Flare 3 temperature | Flare 4 temperature | Flare 5 temperature | CO2 eg at the moment | Amount of CERs
| [Nmc] | [%] | [Nmc] | [Nmc] | [KW*h] | [%] | [h] | [h] | [h] | [h] | [h] | [°C] | [°C] | [°C] | [°C] | [°C] | [tco2e/h] | [tCO2e]
2007-05-01 | 9563809 | 50.8 | 278953 | 9284856 | 289226 | 1 | 2770 | 3070 | 3580 | 1520 | 1303 | 17.2 | 999.6 | 19.6 | 1017.2 | 17.6 | 12.1894 | 76739
2007-05-01 01:00 | 9565264 | 51.2 | 278958 | 9286306 | 289276 | 1 | 2770 | 3071 | 3580 | 1521 | 1303 | 16.8 | 1132.4 | 18.8 | 1017.6 | 17.2 | 12.0567 | 76751
2007-05-01 02:00 | 9566719 | 51.2 | 278963 | 9287756 | 289327 | 1 | 2770 | 3072 | 3580 | 1522 | 1303 | 17.2 | 1132 | 18.8 | 1016 | 17.2 | 12.0872 | 76763
2007-05-01 03:00 | 9568163 | 51.2 | 278967 | 9289196 | 289377 | 1 | 2770 | 3073 | 3580 | 1523 | 1303 | 16.4 | 1128 | 18.8 | 1016.4 | 17.2 | 12.1212 | 76775
2007-05-01 04:00 | 9569614 | 51.5 | 278968 | 9290646 | 289426 | 1 | 2770 | 3074 | 3580 | 1524 | 1303 | 16.8 | 1135.2 | 18.8 | 1019.6 | 16.8 | 12.1371 | 76787
2007-05-01 05:00 | 9571067 | 51.5 | 278971 | 9292096 | 289475 | 1 | 2770 | 3075 | 3580 | 1525 | 1303 | 16 | 1136 | 18.4 | 1018 | 16.4 | 12.1849 | 76800
2007-05-01 06:00 | 9572508 | 51.3 | 278972 | 9293536 | 289524 | 1 | 2770 | 3076 | 3580 | 1526 | 1303 | 15.6 | 1126.8 | 18.4 | 1025.6 | 16.4 | 12.1289 | 76812
2007-05-01 07:00 | 9573960 | 51.2 | 278974 | 9294986 | 289573 | 1 | 2770 | 3077 | 3580 | 1527 | 1303 | 15.2 | 1122 | 18.4 | 1028 | 16.4 | 12.1178 | 76824
2007-05-01 08:00 | 9575402 | 51.2 | 278976 | 9296426 | 289619 | 1 | 2770 | 3078 | 3580 | 1528 | 1303 | 15.6 | 1128 | 18.4 | 1020 | 16.4 | 12.1076 | 76836
2007-05-01 09:00 | 9576842 | 51.4 | 278976 | 9297866 | 289663 | 1 | 2770 | 3079 | 3580 | 1529 | 1303 | 16.4 | 1134 | 18.8 | 1020 | 16.8 | 12.0399 | 76848
2007-05-01 10:00 | 9578273 | 51.7 | 278977 | 9299296 | 289707 | 1 | 2770 | 3080 | 3580 | 1530 | 1303 | 16.8 | 1138.4 | 19.6 | 1024.4 | 17.6 | 12.035 | 76860
2007-05-01 11:00 | 9579713 | 52 | 278977 | 9300736 | 289750 | 1 | 2770 | 3081 | 3580 | 1531 | 1303 | 17.6 | 1144.8 | 20.4 | 1023.2 | 18.8 | 12.082 | 76872
2007-05-01 12:00 | 9581133 | 52.5 | 278977 | 9302156 | 289794 | 1 | 2770 | 3082 | 3580 | 1532 | 1303 | 19.2 | 1139.6 | 22 | 1027.2 | 20.4 | 12.2399 | 76884
2007-05-01 13:00 | 9582581 | 52.5 | 278985 | 9303596 | 289839 | 1 | 2770 | 3083 | 3580 | 1533 | 1303 | 20.8 | 1138 | 24 | 1025.6 | 22 | 12.4445 | 76897
2007-05-01 14:00 | 9584043 | 52.5 | 278987 | 9305056 | 289884 | 1 | 2770 | 3084 | 3580 | 1534 | 1303 | 20.8 | 1132.8 | 24.4 | 1015.2 | 22.4 | 12.4819 | 76909
2007-05-01 15:00 | 9585493 | 54 | 278987 | 9306506 | 289929 | 1 | 2770 | 3085 | 3580 | 1535 | 1303 | 17.2 | 1148.4 | 19.2 | 1024 | 18 | 12.4429 | 76922
2007-05-01 16:00 | 9586943 | 57.3 | 278987 | 9307956 | 289973 | 1 | 2770 | 3085 | 3580 | 1536 | 1303 | 17.2 | 138.4 | 19.6 | 1078 | 18 | 13.4717 | 76935
2007-05-01 17:00 | 9588383 | 56.9 | 278987 | 9309396 | 290018 | 1 | 2770 | 3086 | 3580 | 1537 | 1303 | 16 | 1148 | 19.2 | 1024 | 18.4 | 13.5452 | 76949
2007-05-01 18:00 | 9589823 | 56.2 | 278987 | 9310836 | 290063 | 1 | 2770 | 3087 | 3580 | 1538 | 1303 | 16 | 1185.6 | 20.4 | 1020.8 | 18 | 13.4223 | 76962
2007-05-01 19:00 | 9591273 | 55.7 | 278987 | 9312286 | 290112 | 1 | 2770 | 3088 | 3580 | 1539 | 1303 | 16 | 1175.2 | 19.6 | 1016.8 | 17.2 | 13.2968 | 76976
2007-05-01 20:00 | 9592723 | 55.4 | 278987 | 9313736 | 290163 | 1 | 2770 | 3089 | 3580 | 1540 | 1303 | 16 | 1187.6 | 18.4 | 1011.6 | 16.8 | 13.1329 | 76989
2007-05-01 21:00 | 9594163 | 55.4 | 278987 | 9315176 | 290213 | 1 | 2770 | 3090 | 3580 | 1541 | 1303 | 16 | 1183.6 | 18.4 | 1013.6 | 16 | 13.0183 | 77002
2007-05-01 22:00 | 9595603 | 54.9 | 278987 | 9316616 | 290263 | 1 | 2770 | 3091 | 3580 | 1542 | 1303 | 15.6 | 1170.8 | 18.4 | 1020 | 16 | 12.9383 | 77015
2007-05-01 23:00 | 9597044 | 54.9 | 278988 | 9318056 | 290313 | 1 | 2770 | 3092 | 3580 | 1543 | 1303 | 16 | 1177.6 | 18.4 | 1016.8 | 15.6 | 12.8967 | 77028

## 02-5-07
Date | Amount of landfill gas collected from project wells | Methane fraction in the landfill gas | Amount of landfill gas used for electricity generation | Amount of landfill gas flared | Amount of electricity generated | Combustion efficiencia | Flare 1 working hours | Flare 2 working hours | Flare 3 working hours | Flare 4 working hours | Flare 5 working hours | Flare 1 temperature | Flare 2 temperature | Flare 3 temperature | Flare 4 temperature | Flare 5 temperature | Amount of CERs
| [Nmc] | [%] | [Nmc] | [Nmc] | [KW*h] | [%] | [h] | [h] | [h] | [h] | [h] | [°C] | [°C] | [°C] | [°C] | [°C] | [tCO2e]
2007-05-02 | 9598475 | 54.9 | 278989 | 9319486 | 290363 | 1 | 2770 | 3093 | 3580 | 1544 | 1303 | 15.6 | 1171.2 | 17.6 | 1017.6 | 15.6 | 77040
2007-05-02 01:00 | 9599925 | 54.9 | 278989 | 9320936 | 290412 | 1 | 2770 | 3093 | 3580 | 1545 | 1303 | 15.2 | 113.6 | 17.6 | 1062 | 15.2 | 77053
2007-05-02 02:00 | 9601367 | 54.3 | 278991 | 9322376 | 290462 | 1 | 2770 | 3094 | 3580 | 1546 | 1303 | 15.2 | 1160.8 | 17.6 | 1018.4 | 15.2 | 77066
2007-05-02 03:00 | 9602797 | 54.4 | 278991 | 9323806 | 290512 | 1 | 2770 | 3095 | 3580 | 1547 | 1303 | 15.2 | 1170 | 17.2 | 1040.8 | 14.8 | 77079
2007-05-02 04:00 | 9604240 | 54.9 | 278994 | 9325246 | 290561 | 1 | 2770 | 3096 | 3580 | 1548 | 1303 | 15.2 | 1169.6 | 16.8 | 1012.4 | 14.4 | 77092
2007-05-02 05:00 | 9605674 | 54.9 | 278998 | 9326676 | 290610 | 1 | 2770 | 3097 | 3580 | 1549 | 1303 | 14.8 | 1167.2 | 18.4 | 1011.2 | 14.4 | 77105
2007-05-02 06:00 | 9607114 | 55.4 | 278998 | 9328116 | 290660 | 1 | 2770 | 3098 | 3580 | 1550 | 1303 | 14.4 | 1164 | 17.2 | 1013.6 | 14.4 | 77118
2007-05-02 07:00 | 9608544 | 55.5 | 278998 | 9329546 | 290709 | 1 | 2770 | 3099 | 3580 | 1551 | 1303 | 14 | 1164.8 | 16 | 1022.4 | 13.2 | 77131
2007-05-02 08:00 | 9609974 | 55.1 | 278998 | 9330976 | 290757 | 1 | 2770 | 3100 | 3580 | 1552 | 1303 | 14.4 | 972 | 16.4 | 1019.6 | 92 | 77143
2007-05-02 09:00 | 9611479 | 54.3 | 279003 | 9332476 | 290761 | 1 | 2770 | 3100 | 3580 | 1553 | 1304 | 14 | 90.8 | 16.8 | 1021.2 | 879 | 77156
2007-05-02 10:00 | 9612969 | 54.9 | 279003 | 9333966 | 290761 | 1 | 2770 | 3100 | 3580 | 1554 | 1305 | 14.8 | 54.4 | 17.6 | 1049.6 | 883 | 77170
2007-05-02 11:00 | 9614469 | 54.9 | 279003 | 9335466 | 290761 | 1 | 2770 | 3100 | 3580 | 1555 | 1306 | 16 | 39.2 | 18.4 | 1002.4 | 922.4 | 77183
2007-05-02 12:00 | 9615979 | 55.2 | 279003 | 9336976 | 290761 | 1 | 2770 | 3100 | 3580 | 1556 | 1307 | 16 | 32.8 | 18.8 | 1006.4 | 999.6 | 77196
2007-05-02 13:00 | 9617479 | 55.6 | 279003 | 9338476 | 290761 | 1 | 2770 | 3100 | 3580 | 1557 | 1308 | 16.4 | 28.4 | 19.2 | 1006 | 999.6 | 77210
2007-05-02 14:00 | 9618989 | 55.3 | 279003 | 9339986 | 290761 | 1 | 2770 | 3100 | 3580 | 1558 | 1309 | 16.8 | 26 | 19.6 | 1008 | 999.6 | 77224
2007-05-02 15:00 | 9620489 | 55.1 | 279003 | 9341486 | 290761 | 1 | 2770 | 3100 | 3580 | 1559 | 1310 | 16.4 | 24.4 | 19.6 | 1006.8 | 999.2 | 77237
2007-05-02 16:00 | 9621969 | 55 | 279003 | 9342966 | 290776 | 1 | 2770 | 3100 | 3580 | 1560 | 1311 | 16.4 | 23.6 | 20 | 890.4 | 802.8 | 77250
2007-05-02 17:00 | 9623439 | 54.2 | 279003 | 9344436 | 290822 | 1 | 2770 | 3100 | 3580 | 1561 | 1312 | 16 | 21.6 | 19.6 | 1006.8 | 906.8 | 77262
2007-05-02 18:00 | 9624899 | 53.4 | 279003 | 9345896 | 290866 | 1 | 2770 | 3100 | 3580 | 1562 | 1313 | 15.6 | 20.4 | 18.8 | 999.2 | 998.8 | 77276
2007-05-02 19:00 | 9626379 | 52.8 | 279003 | 9347376 | 290914 | 1 | 2770 | 3100 | 3580 | 1563 | 1314 | 15.2 | 20 | 18.8 | 999.6 | 998.4 | 77288
2007-05-02 20:00 | 9627849 | 52.5 | 279003 | 9348846 | 290965 | 1 | 2770 | 3100 | 3580 | 1564 | 1315 | 15.2 | 19.2 | 18 | 1000 | 998.4 | 77301
2007-05-02 21:00 | 9629319 | 52.5 | 279003 | 9350316 | 291016 | 1 | 2770 | 3100 | 3580 | 1565 | 1316 | 15.2 | 19.2 | 18 | 999.6 | 998.4 | 77313
2007-05-02 22:00 | 9630799 | 52.3 | 279003 | 9351796 | 291067 | 1 | 2770 | 3100 | 3580 | 1566 | 1317 | 15.2 | 18.8 | 17.6 | 999.2 | 998.4 | 77326
2007-05-02 23:00 | 9632269 | 52.5 | 279003 | 9353266 | 291117 | 1 | 2770 | 3100 | 3580 | 1567 | 1318 | 15.2 | 18.8 | 17.6 | 1000 | 998.4 | 77338

## 03-5-07
Date | Amount of landfill gas collected from project wells | Methane fraction in the landfill gas | Amount of landfill gas used for electricity generation | Amount of landfill gas flared | Amount of electricity generated | Combustion efficiencia | Flare 1 working hours | Flare 2 working hours | Flare 3 working hours | Flare 4 working hours | Flare 5 working hours | Flare 1 temperature | Flare 2 temperature | Flare 3 temperature | Flare 4 temperature | Flare 5 temperature | Amount of CERs
| [Nmc] | [%] | [Nmc] | [Nmc] | [KW*h] | [%] | [h] | [h] | [h] | [h] | [h] | [°C] | [°C] | [°C] | [°C] | [°C] | [tCO2e]
2007-05-03 | 9633739 | 52.7 | 279003 | 9354746 | 291168 | 1 | 2770 | 3100 | 3580 | 1568 | 1319 | 15.2 | 18.8 | 18 | 1000.4 | 998.8 | 77351
2007-05-03 01:00 | 9635219 | 52.8 | 279003 | 9356216 | 291219 | 1 | 2770 | 3100 | 3580 | 1569 | 1320 | 15.2 | 18.4 | 17.2 | 999.2 | 999.2 | 77364
2007-05-03 02:00 | 9636699 | 52.8 | 279003 | 9357696 | 291270 | 1 | 2770 | 3100 | 3580 | 1570 | 1321 | 15.6 | 18.8 | 18 | 999.6 | 998.8 | 77376
2007-05-03 03:00 | 9638169 | 52.9 | 279003 | 9359166 | 291321 | 1 | 2770 | 3100 | 3580 | 1571 | 1322 | 15.2 | 18.4 | 17.6 | 999.2 | 998.8 | 77389
2007-05-03 04:00 | 9639649 | 53 | 279003 | 9360646 | 291372 | 1 | 2770 | 3100 | 3580 | 1572 | 1323 | 14.8 | 18 | 17.2 | 1000.4 | 998.8 | 77401
2007-05-03 05:00 | 9641119 | 53 | 279003 | 9362116 | 291422 | 1 | 2770 | 3100 | 3580 | 1573 | 1324 | 14.8 | 17.6 | 17.2 | 999.6 | 998.4 | 77414
2007-05-03 06:00 | 9642579 | 52.7 | 279003 | 9363576 | 291472 | 1 | 2770 | 3100 | 3580 | 1574 | 1325 | 14.4 | 18 | 16.8 | 998.8 | 998.4 | 77427
2007-05-03 07:00 | 9644049 | 52.5 | 279003 | 9365046 | 291523 | 1 | 2770 | 3100 | 3580 | 1575 | 1326 | 14.8 | 17.6 | 16.8 | 999.2 | 998.4 | 77439
2007-05-03 08:00 | 9645519 | 52.2 | 279003 | 9366516 | 291571 | 1 | 2770 | 3100 | 3580 | 1576 | 1327 | 14 | 17.2 | 16.8 | 998 | 998 | 77452
2007-05-03 09:00 | 9646989 | 52.5 | 279003 | 9367986 | 291615 | 1 | 2770 | 3100 | 3580 | 1577 | 1328 | 14.8 | 17.6 | 17.2 | 998.8 | 998.8 | 77464
2007-05-03 10:00 | 9648459 | 52.7 | 279003 | 9369456 | 291660 | 1 | 2770 | 3100 | 3580 | 1578 | 1329 | 14.8 | 17.6 | 17.6 | 999.2 | 998.8 | 77477
2007-05-03 11:00 | 9649919 | 52.9 | 279003 | 9370916 | 291705 | 1 | 2770 | 3100 | 3580 | 1579 | 1330 | 14.8 | 18 | 18 | 999.6 | 998.8 | 77489
2007-05-03 12:00 | 9651389 | 53.5 | 279003 | 9372386 | 291750 | 1 | 2770 | 3100 | 3580 | 1580 | 1331 | 16 | 18.8 | 18.4 | 999.6 | 998.8 | 77502
2007-05-03 13:00 | 9652859 | 53.9 | 279003 | 9373856 | 291794 | 1 | 2770 | 3100 | 3580 | 1581 | 1332 | 16.8 | 19.2 | 18.8 | 999.6 | 998.4 | 77515
2007-05-03 14:00 | 9654319 | 53.8 | 279003 | 9375316 | 291838 | 1 | 2770 | 3100 | 3580 | 1582 | 1333 | 17.2 | 20 | 19.6 | 999.6 | 998.8 | 77528
2007-05-03 15:00 | 9655779 | 53.7 | 279003 | 9376776 | 291883 | 1 | 2770 | 3100 | 3580 | 1583 | 1334 | 17.2 | 20.4 | 20 | 999.6 | 999.2 | 77540
2007-05-03 16:00 | 9657239 | 53.7 | 279003 | 9378236 | 291927 | 1 | 2770 | 3100 | 3580 | 1584 | 1335 | 18 | 20.8 | 20.8 | 998.8 | 999.2 | 77553
2007-05-03 17:00 | 9658699 | 53.5 | 279003 | 9379696 | 291972 | 1 | 2770 | 3100 | 3580 | 1585 | 1336 | 18.4 | 20.8 | 20.8 | 998.8 | 999.2 | 77566
2007-05-03 18:00 | 9660169 | 53.8 | 279003 | 9381166 | 292016 | 1 | 2770 | 3100 | 3580 | 1586 | 1337 | 18.4 | 20.8 | 20.4 | 998.4 | 998.4 | 77579
2007-05-03 19:00 | 9661629 | 53.5 | 279003 | 9382626 | 292065 | 1 | 2770 | 3100 | 3580 | 1587 | 1338 | 18.4 | 20.8 | 20.4 | 999.6 | 999.2 | 77591
2007-05-03 20:00 | 9663089 | 54 | 279003 | 9384086 | 292116 | 1 | 2770 | 3100 | 3580 | 1588 | 1339 | 18.8 | 20.8 | 20.4 | 1000 | 999.2 | 77604
2007-05-03 21:00 | 9664549 | 53.7 | 279003 | 9385546 | 292166 | 1 | 2770 | 3100 | 3580 | 1589 | 1340 | 18.4 | 20.4 | 20.4 | 999.2 | 999.2 | 77617
2007-05-03 22:00 | 9665999 | 53.6 | 279003 | 9386996 | 292216 | 1 | 2770 | 3100 | 3580 | 1590 | 1341 | 17.6 | 20 | 20 | 999.2 | 998.8 | 77630
2007-05-03 23:00 | 9667439 | 57.5 | 279003 | 9388436 | 292265 | 1 | 2770 | 3100 | 3580 | 1591 | 1342 | 16.4 | 19.2 | 18.4 | 1000.8 | 997.2 | 77642

## 04-5-07
Date | Amount of landfill gas collected from project wells | Methane fraction in the landfill gas | Amount of landfill gas used for electricity generation | Amount of landfill gas flared | Amount of electricity generated | Combustion efficiencia | Flare 1 working hours | Flare 2 working hours | Flare 3 working hours | Flare 4 working hours | Flare 5 working hours | Flare 1 temperature | Flare 2 temperature | Flare 3 temperature | Flare 4 temperature | Flare 5 temperature | Amount of CERs
| [Nmc] | [%] | [Nmc] | [Nmc] | [KW*h] | [%] | [h] | [h] | [h] | [h] | [h] | [°C] | [°C] | [°C] | [°C] | [°C] | [tCO2e]
2007-05-04 | 9668879 | 58.1 | 279003 | 9389876 | 292314 | 1 | 2770 | 3100 | 3580 | 1592 | 1343 | 16.4 | 18.8 | 18.4 | 1000 | 999.2 | 77656
2007-05-04 01:00 | 9670319 | 58.5 | 279003 | 9391316 | 292363 | 1 | 2770 | 3100 | 3580 | 1593 | 1344 | 16.4 | 19.2 | 18.4 | 1002 | 999.6 | 77670
2007-05-04 02:00 | 9671759 | 59.3 | 279003 | 9392756 | 292412 | 1 | 2770 | 3100 | 3580 | 1594 | 1345 | 16.8 | 18.8 | 18.4 | 1000.4 | 999.6 | 77683
2007-05-04 03:00 | 9673189 | 60 | 279003 | 9394186 | 292460 | 1 | 2770 | 3100 | 3580 | 1595 | 1346 | 16.8 | 19.2 | 18.8 | 1002 | 999.6 | 77697
2007-05-04 04:00 | 9674619 | 60.2 | 279003 | 9395616 | 292509 | 1 | 2770 | 3100 | 3580 | 1596 | 1347 | 16.4 | 18.8 | 18.8 | 1000.8 | 999.2 | 77711
2007-05-04 05:00 | 9676049 | 60.3 | 279003 | 9397046 | 292559 | 1 | 2770 | 3100 | 3580 | 1597 | 1348 | 16.4 | 19.2 | 18.8 | 1006 | 999.2 | 77725
2007-05-04 06:00 | 9677469 | 60.5 | 279003 | 9398466 | 292608 | 1 | 2770 | 3100 | 3580 | 1598 | 1349 | 16.8 | 19.2 | 18.4 | 1002 | 999.6 | 77739
2007-05-04 07:00 | 9678899 | 60.7 | 279003 | 9399896 | 292657 | 1 | 2770 | 3100 | 3580 | 1599 | 1350 | 16.8 | 19.2 | 18.4 | 1025.6 | 999.6 | 77753
2007-05-04 08:00 | 9680309 | 60.6 | 279003 | 9401306 | 292704 | 1 | 2770 | 3100 | 3580 | 1600 | 1351 | 16.4 | 19.2 | 18.8 | 1008.8 | 998.4 | 77768
2007-05-04 09:00 | 9681729 | 57.2 | 279003 | 9402726 | 292748 | 1 | 2770 | 3100 | 3580 | 1601 | 1352 | 16.4 | 19.6 | 19.2 | 1003.2 | 999.2 | 77781
2007-05-04 10:00 | 9683149 | 56.8 | 279003 | 9404146 | 292792 | 1 | 2770 | 3100 | 3580 | 1602 | 1353 | 16.8 | 19.2 | 18.4 | 1022.8 | 999.2 | 77794
2007-05-04 11:00 | 9684559 | 56.8 | 279003 | 9405556 | 292838 | 1 | 2770 | 3100 | 3580 | 1603 | 1354 | 16.8 | 19.6 | 18.8 | 1013.2 | 999.6 | 77807
2007-05-04 12:00 | 9685979 | 57.1 | 279003 | 9406976 | 292883 | 1 | 2770 | 3100 | 3580 | 1604 | 1355 | 16.8 | 19.6 | 19.2 | 1012.8 | 999.6 | 77820
2007-05-04 13:00 | 9687399 | 57.2 | 279003 | 9408396 | 292928 | 1 | 2770 | 3100 | 3580 | 1605 | 1356 | 16.8 | 19.6 | 18.8 | 1010 | 999.6 | 77833
2007-05-04 14:00 | 9688819 | 57.4 | 279003 | 9409816 | 292974 | 1 | 2770 | 3100 | 3580 | 1606 | 1357 | 17.2 | 19.6 | 19.2 | 1029.2 | 999.6 | 77846
2007-05-04 15:00 | 9690229 | 57.1 | 279003 | 9411226 | 293019 | 1 | 2770 | 3100 | 3580 | 1607 | 1358 | 16.4 | 20 | 19.2 | 1056.4 | 999.6 | 77860
2007-05-04 16:00 | 9691639 | 56.9 | 279003 | 9412636 | 293064 | 1 | 2770 | 3100 | 3580 | 1608 | 1359 | 17.2 | 20 | 19.2 | 1028 | 999.6 | 77873
2007-05-04 17:00 | 9693089 | 56.7 | 279003 | 9414086 | 293081 | 1 | 2770 | 3100 | 3580 | 1609 | 1360 | 17.2 | 20 | 19.6 | 1022.4 | 999.6 | 77887
2007-05-04 18:00 | 9694547 | 60.3 | 279061 | 9415486 | 293136 | 1 | 2770 | 3100 | 3580 | 1610 | 1361 | 16.8 | 20 | 19.6 | 1007.6 | 949.6 | 77898
2007-05-04 19:00 | 9696057 | 56.2 | 279121 | 9416936 | 293209 | 1 | 2770 | 3100 | 3580 | 1611 | 1362 | 17.6 | 20 | 19.6 | 1001.2 | 997.2 | 77912
2007-05-04 20:00 | 9697559 | 56 | 279183 | 9418386 | 293285 | 1 | 2770 | 3100 | 3580 | 1612 | 1363 | 17.6 | 19.6 | 19.6 | 1001.6 | 996.4 | 77926
2007-05-04 21:00 | 9699061 | 55.8 | 279245 | 9419816 | 293362 | 1 | 2770 | 3100 | 3580 | 1613 | 1364 | 16.8 | 19.6 | 19.6 | 1001.6 | 996.8 | 77940
2007-05-04 22:00 | 9700572 | 55.8 | 279306 | 9421266 | 293438 | 1 | 2770 | 3100 | 3580 | 1614 | 1365 | 17.2 | 20 | 19.2 | 1000.8 | 996.8 | 77953
2007-05-04 23:00 | 9702072 | 55.7 | 279366 | 9422706 | 293513 | 1 | 2770 | 3100 | 3580 | 1615 | 1366 | 16.8 | 19.6 | 19.2 | 1001.6 | 998 | 77967

## Calculo CERs
Date | Methane fraction in the landfill gas | Amount of landfill gas used for electricity generation | Amount of landfill gas flared | Combustion efficiency | CERs
| [%] | [Nm3] | [Nm3] | [%] | [tCO2e]
2007-04-29 | 51.87 | 1198 |  |  | 9.3538
2007-04-30 | 51.78 | 1302 |  |  | 10.1482
2007-05-01 | 53.27 | 1308 |  |  | 10.4884
2007-05-02 | 54.27 | 1333.4286 |  |  | 10.893
2007-05-03 | 53.6 | 1416 |  |  | 11.4247
2007-05-04 | 58.43 | 952 |  |  | 8.3732
2007-11-13 | 39.7 |  | 17240 |  | 103.0256
TOTAL |  |  |  |  | 163.7069