## CU SUMMARY
| Site | Aquascalientes, Cumbres flare |  | from | 2007-09-07 23:59
| CMD ID | CDM0425 |  | to | 2006-10-18 00:11
| Methodology | ACM0001 v2 |  | days | -324.9917
MONITORED DATA
| ID | variable | unit | value | remarks
| LFGtotal | Total amount of landfill gas captured | m3 | 1714420.1318 | 1
| LFGflare | Amount of landfill gas flared | m3 | 1714420.1318 | 2
| LFGelectricity | Amount of landfill gas combusted in power plant | m3 | 0 | 3
| LFGthermal | Amount of methane combusted in boiler | m3 | 0 | 4
| FE | Flare/combustion efficiency, determined by the operation hours (1) and the methane content in the exhaust gas (2) | % | 99.8 | 5
| Wch4 | Methane fraction in the landfill gas | m3 CH4 / m3LFG |  | 6
| T | Temperature of the landfill gas | °C | N/A | 7
| P | Pressure of the landfill gas | Pa | N/A | 8
| 9 | Total amount of electricity and/or other energy carriers used in the project for gas pumping and heat transport (not derived from the gas) | MWh |  | 9
| 10 | CO2 emission intensity of the electricity and/or other energy carriers in ID 9. | t CO2 / MWh | 0.531 | 10
| 11 | Regulatory requirements relating to landfill gas projects | Test | OK | 11
FIXED PARAMETERS
| ID | variable | unit | value | remarks
| AF | Adjustment factor | % | 0 | 12
| Dch4 | Density of methane | tCH4/m3 | 0.0007168 | 13
| GWP CH4 | Global Warming Potential methane | tCO2eq/tCH4 | 21 | 14
CALCULATIONS
| ID | variable | unit | value | remarks
| MDreg | methane that would have been combusted in absence of project | tCH4 | 25.8588 | 15
| MDproject | methane combusted/destroyed by project | tCH4 | 517.1765 | 16
| MDflared | methane destroyed by flaring | tCH4 | 517.1765 | 17
| MDthermal | methane destroyed by generation of thermal energy | tCH4 | 0 | 18
| MDelectricity | methane destroyed by generation of electricity | tCH4 | 0 | 19
| EGi | power import | MWh | 0 | 20
| EGe | power export | MWh | 0 | 21
| F | fuel consumption to operate project | t | 0 | 22
| LHV | lower heating value fuel | GJ/t fuel | N/A | 23
| EFf | emission factor fuel | tCO2/GJ | N/A | 24
| ER | emission reduction by project | tCO2eq | 10317.6718 | 25
REMARKS
1 | LFGtotal = LFGflare since LFGelectricity and LFGthermal are zero
2 | Measured in Nm3 with thermal mass flow meter
3 | There was no power plant operating on site during the monitoring period
4 | There was no boiler operating on site during the monitoring period
5 | No methane was detected in the exhaust gas of the flare during any of the quarterly flare tests [detection limit < 0.1% CH4], a conservative flare efficiency has been applied
6 | This is the average value for the monitoring period, the actual measured values were used in the calculation of MDflared
7 | No temperature needs to be measured since a thermal mass flow meter was used, see http://cdm.unfccc.int/UserManagement/FileStorage/AM_CLAR_XURFEX9N1DBCDWH8IFJ47F4GGRLNZD
8 | No pressure needs to be measured since a thermal mass flow meter was used, see http://cdm.unfccc.int/UserManagement/FileStorage/AM_CLAR_XURFEX9N1DBCDWH8IFJ47F4GGRLNZD
9 | No power was generated on site
10 | As per PDD, used for whole crediting period. See http://cdm.unfccc.int/UserManagement/FileStorage/AM_CLAR_4Q0FZJXVZX4M63GEBW4FP5AKSYZZUD
11 | The project complies with all relevant national legislation. No legislation relevant to landfills was introduced during the monitoring period
12 | As per PDD
13 | As per PDD
14 | As per PDD
15 | MDproject * AF
16 | MDproject = MDflared, since MDelectricity and MDthermal are zero
17 | MDflared = LFGflared * Dch4 * Wch4 * FE, calculated from the continuously monitored values of LFG flared and Wch4
18 | Not applicable
19 | Not applicable
20 | From invoices
21 | Not applicable
22 | No fossil fuel was combused on site during the monitoring period
23 | No fossil fuel was combused on site during the monitoring period
24 | No fossil fuel was combused on site during the monitoring period
25 | ER = (MDproject - MDreg) * GWP CH4 - power import * CO2 intensity imported power

## SN1 SUMMARY
| Site | Aquascalientes, San Nicolas 1 flare |  | from | 2006-10-18 00:22
| CMD ID | CDM0425 |  | to | 2007-09-07 23:52
| Methodology | ACM0001 v2 |  | days | 324.9789
MONITORED DATA
| ID | variable | unit | value | remarks
| LFGtotal | Total amount of landfill gas captured | m3 | 6389187.9756 | 1
| LFGflare | Amount of landfill gas flared | m3 | 6389187.9756 | 2
| LFGelectricity | Amount of landfill gas combusted in power plant | m3 | 0 | 3
| LFGthermal | Amount of methane combusted in boiler | m3 | 0 | 4
| FE | Flare/combustion efficiency, determined by the operation hours (1) and the methane content in the exhaust gas (2) | % | 99.8 | 5
| Wch4 | Methane fraction in the landfill gas | m3 CH4 / m3LFG |  | 6
| T | Temperature of the landfill gas | °C | N/A | 7
| P | Pressure of the landfill gas | Pa | N/A | 8
| 9 | Total amount of electricity and/or other energy carriers used in the project for gas pumping and heat transport (not derived from the gas) | MWh |  | 9
| 10 | CO2 emission intensity of the electricity and/or other energy carriers in ID 9. | t CO2 / MWh | 0.531 | 10
| 11 | Regulatory requirements relating to landfill gas projects | Test | OK | 11
FIXED PARAMETERS
| ID | variable | unit | value | remarks
| AF | Adjustment factor | % | 5 | 12
| Dch4 | Density of methane | tCH4/m3 | 0.0007168 | 13
| GWP CH4 | Global Warming Potential methane | tCO2eq/tCH4 | 21 | 14
CALCULATIONS
| ID | variable | unit | value | remarks
| MDreg | methane that would have been combusted in absence of project | tCH4 | 117.6551 | 15
| MDproject | methane combusted/destroyed by project | tCH4 | 2353.1019 | 16
| MDflared | methane destroyed by flaring | tCH4 | 2353.1019 | 17
| MDthermal | methane destroyed by generation of thermal energy | tCH4 | 0 | 18
| MDelectricity | methane destroyed by generation of electricity | tCH4 | 0 | 19
| EGi | power import | MWh | 0 | 20
| EGe | power export | MWh | 0 | 21
| F | fuel consumption to operate project | t | 0 | 22
| LHV | lower heating value fuel | GJ/t fuel | N/A | 23
| EFf | emission factor fuel | tCO2/GJ | N/A | 24
| ER | emission reduction by project | tCO2eq | 46944.3833 | 25
REMARKS
1 | LFGtotal = LFGflare since LFGelectricity and LFGthermal are zero
2 | Measured in Nm3 with thermal mass flow meter
3 | There was no power plant operating on site during the monitoring period
4 | There was no boiler operating on site during the monitoring period
5 | No methane was detected in the exhaust gas of the flare during any of the quarterly flare tests [detection limit < 0.1% CH4], a conservative flare efficiency has been applied
6 | This is the average value for the monitoring period, the actual measured values were used in the calculation of MDflared
7 | No temperature needs to be measured since a thermal mass flow meter was used, see http://cdm.unfccc.int/UserManagement/FileStorage/AM_CLAR_XURFEX9N1DBCDWH8IFJ47F4GGRLNZD
8 | No pressure needs to be measured since a thermal mass flow meter was used, see http://cdm.unfccc.int/UserManagement/FileStorage/AM_CLAR_XURFEX9N1DBCDWH8IFJ47F4GGRLNZD
9 | No power was generated on site
10 | As per PDD, used for whole crediting period. See http://cdm.unfccc.int/UserManagement/FileStorage/AM_CLAR_4Q0FZJXVZX4M63GEBW4FP5AKSYZZUD
11 | The project complies with all relevant national legislation. No legislation relevant to landfills was introduced during the monitoring period
12 | As per PDD
13 | As per PDD
14 | As per PDD
15 | MDproject * AF
16 | MDproject = MDflared, since MDelectricity and MDthermal are zero
17 | MDflared = LFGflared * Dch4 * Wch4 * FE, calculated from the continuously monitored values of LFG flared and Wch4
18 | Not applicable
19 | Not applicable
20 | From invoices
21 | Not applicable
22 | No fossil fuel was combused on site during the monitoring period
23 | No fossil fuel was combused on site during the monitoring period
24 | No fossil fuel was combused on site during the monitoring period
25 | ER = (MDproject - MDreg) * GWP CH4 - power import * CO2 intensity imported power

## SN2 SUMMARY
| Site | Aquascalientes, San Nicolas 2 flare |  | from | 2006-10-18 00:08
| CMD ID | CDM0425 |  | to | 2007-09-07 23:55
| Methodology | ACM0001 v2 |  | days | 324.991
MONITORED DATA
| ID | variable | unit | value | remarks
| LFGtotal | Total amount of landfill gas captured | m3 | 6296355.4029 | 1
| LFGflare | Amount of landfill gas flared | m3 | 6296355.4029 | 2
| LFGelectricity | Amount of landfill gas combusted in power plant | m3 | 0 | 3
| LFGthermal | Amount of methane combusted in boiler | m3 | 0 | 4
| FE | Flare/combustion efficiency, determined by the operation hours (1) and the methane content in the exhaust gas (2) | % | 99.8 | 5
| Wch4 | Methane fraction in the landfill gas | m3 CH4 / m3LFG |  | 6
| T | Temperature of the landfill gas | °C | N/A | 7
| P | Pressure of the landfill gas | Pa | N/A | 8
| 9 | Total amount of electricity and/or other energy carriers used in the project for gas pumping and heat transport (not derived from the gas) | MWh |  | 9
| 10 | CO2 emission intensity of the electricity and/or other energy carriers in ID 9. | t CO2 / MWh | 0.531 | 10
| 11 | Regulatory requirements relating to landfill gas projects | Test | OK | 11
FIXED PARAMETERS
| ID | variable | unit | value | remarks
| AF | Adjustment factor | % | 0 | 12
| Dch4 | Density of methane | tCH4/m3 | 0.0007168 | 13
| GWP CH4 | Global Warming Potential methane | tCO2eq/tCH4 | 21 | 14
CALCULATIONS
| ID | variable | unit | value | remarks
| MDreg | methane that would have been combusted in absence of project | tCH4 | 113.3717 | 15
| MDproject | methane combusted/destroyed by project | tCH4 | 2265.176 | 16
| MDflared | methane destroyed by flaring | tCH4 | 2265.176 | 17
| MDthermal | methane destroyed by generation of thermal energy | tCH4 | 0 | 18
| MDelectricity | methane destroyed by generation of electricity | tCH4 | 0 | 19
| EGi | power import | MWh | 0 | 20
| EGe | power export | MWh | 0 | 21
| F | fuel consumption to operate project | t | 0 | 22
| LHV | lower heating value fuel | GJ/t fuel | N/A | 23
| EFf | emission factor fuel | tCO2/GJ | N/A | 24
| ER | emission reduction by project | tCO2eq | 45187.8909 | 25
REMARKS
1 | LFGtotal = LFGflare since LFGelectricity and LFGthermal are zero
2 | Measured in Nm3 with thermal mass flow meter
3 | There was no power plant operating on site during the monitoring period
4 | There was no boiler operating on site during the monitoring period
5 | No methane was detected in the exhaust gas of the flare during any of the quarterly flare tests [detection limit < 0.1% CH4], a conservative flare efficiency has been applied
6 | This is the average value for the monitoring period, the actual measured values were used in the calculation of MDflared
7 | No temperature needs to be measured since a thermal mass flow meter was used, see http://cdm.unfccc.int/UserManagement/FileStorage/AM_CLAR_XURFEX9N1DBCDWH8IFJ47F4GGRLNZD
8 | No pressure needs to be measured since a thermal mass flow meter was used, see http://cdm.unfccc.int/UserManagement/FileStorage/AM_CLAR_XURFEX9N1DBCDWH8IFJ47F4GGRLNZD
9 | No power was generated on site
10 | As per PDD, used for whole crediting period. See http://cdm.unfccc.int/UserManagement/FileStorage/AM_CLAR_4Q0FZJXVZX4M63GEBW4FP5AKSYZZUD
11 | The project complies with all relevant national legislation. No legislation relevant to landfills was introduced during the monitoring period
12 | As per PDD
13 | As per PDD
14 | As per PDD
15 | MDproject * AF
16 | MDproject = MDflared, since MDelectricity and MDthermal are zero
17 | MDflared = LFGflared * Dch4 * Wch4 * FE, calculated from the continuously monitored values of LFG flared and Wch4
18 | Not applicable
19 | Not applicable
20 | From invoices
21 | Not applicable
22 | No fossil fuel was combused on site during the monitoring period
23 | No fossil fuel was combused on site during the monitoring period
24 | No fossil fuel was combused on site during the monitoring period
25 | ER = (MDproject - MDreg) * GWP CH4 - power import * CO2 intensity imported power

## AQUAS ALL
| Site | AQUASCALIENTES |  | from | 2006-10-18 00:11
| CMD ID | CDM0425 |  | to | 2007-09-07 23:59
| Methodology | ACM0001 v2 |  | days | 324.9917
MONITORED DATA
| ID | variable | unit | value | remarks
| LFGtotal | Total amount of landfill gas captured | m3 | 14399963.5104 | 1
| LFGflare | Amount of landfill gas flared | m3 | 14399963.5104 | 2
| LFGelectricity | Amount of landfill gas combusted in power plant | m3 | 0 | 3
| LFGthermal | Amount of methane combusted in boiler | m3 | 0 | 4
| FE | Flare efficiency | % | 99.8 | 5
| Wch4 | Methane fraction in the landfill gas | m3 CH4 / m3LFG | 0.47682 | 6
| T | Temperature of the landfill gas | °C | N/A | 7
| P | Pressure of the landfill gas | Pa | 110325 | 8 | mbarg | 75 | 105 | avg
| 9 | Total amount of electricity and/or other energy carriers used in the project for gas pumping and heat transport (not derived from the gas) | MWh | 154.0197 | 9 | Pa [g] | 7500 | 10500
| 10 | CO2 emission intensity of the electricity and/or other energy carriers in ID 9. | t CO2 / MWh | 0.531 | 10 | Pa [a] | 108825 | 111825 | 110325
| 11 | Regulatory requirements relating to landfill gas projects | Test | OK | 11
FIXED PARAMETERS
| ID | variable | unit | value | remarks
| AF | Adjustment factor | % | 5 | 12
| Dch4 | Density of methane | tCH4/m3 | 0.0007168 | 13
| GWP CH4 | Global Warming Potential methane | tCO2eq/tCH4 | 21 | 14
CALCULATIONS
| ID | variable | unit | value | remarks
| MDreg | methane that would have been combusted in absence of project | tCH4 | 256.8856 | 15
| MDproject | methane combusted/destroyed by project | tCH4 | 5135.4545 | 16
| MDflared | methane destroyed by flaring | tCH4 | 5135.4545 | 17
| MDthermal | methane destroyed by generation of thermal energy | tCH4 | 0 | 18
| MDelectricity | methane destroyed by generation of electricity | tCH4 | 0 | 19
| EGi | power import | MWh | 154.0197 | 20
| EGe | power export | MWh | 0 | 21
| F | fuel consumption to operate project | t | 0 | 22
| LHV | lower heating value fuel | GJ/t fuel | N/A | 23
| EFf | emission factor fuel | tCO2/GJ | N/A | 24
| ER | emission reduction by project | tCO2eq | 102368.1616 | 25
REMARKS
1 | LFGtotal = LFGflare since LFGelectricity and LFGthermal are zero
2 | Measured in Nm3 with thermal mass flow meter
3 | There was no power plant operating on site during the monitoring period
4 | There was no boiler operating on site during the monitoring period
5 | No methane was detected in the exhaust gas of the flare during any of the quarterly flare tests [detection limit < 0.1% CH4], a conservative flare efficiency has been applied
6 | This is the average value for the monitoring period, the actual continously measured values were used in the calculation of MDflared
7 | No temperature needs to be measured since a thermal mass flow meter was used, see http://cdm.unfccc.int/UserManagement/FileStorage/AM_CLAR_XURFEX9N1DBCDWH8IFJ47F4GGRLNZD
8 | A thermal mass flow meter was used, LFG pressure reading is not used for emission reduction calculation purposes; see
http://cdm.unfccc.int/UserManagement/FileStorage/AM_CLAR_XURFEX9N1DBCDWH8IFJ47F4GGRLNZD
9 | No power was generated on site
10 | As per PDD, used for whole crediting period. See http://cdm.unfccc.int/UserManagement/FileStorage/AM_CLAR_4Q0FZJXVZX4M63GEBW4FP5AKSYZZUD
11 | The project complies with all relevant national legislation. No legislation relevant to landfills was introduced during the monitoring period
12 | As per PDD
13 | As per PDD
14 | As per PDD
15 | MDproject * AF
16 | MDproject = MDflared, since MDelectricity and MDthermal are zero
17 | MDflared = LFGflared * Dch4 * Wch4 * FE, calculated from the continuously monitored values of LFG flared and Wch4
18 | Not applicable
19 | Not applicable
20 | From invoices
21 | Not applicable
22 | No fossil fuel was combused on site during the monitoring period
23 | No fossil fuel was combused on site during the monitoring period
24 | No fossil fuel was combused on site during the monitoring period
25 | ER = (MDproject - MDreg) * GWP CH4 - power import * CO2 intensity imported power

## CH4
Nm3 CH4 / Nm3 LFG
47.1 | CU
47.5 | CU | average | 47.6819
46.8 | CU
47.8 | CU
45.6 | CU
45.4 | CU
46.3 | CU
45.3 | CU
45 | CU
45 | CU
44.7 | CU
44.7 | CU
42.7 | CU
42.4 | CU
38.9 | CU
38.9 | CU
38.2 | CU
38.1 | CU
37.8 | CU
39.6 | CU
40 | CU
41.1 | CU
41.5 | CU
41.8 | CU
41.8 | CU
42.1 | CU
42.1 | CU
42.4 | CU
42 | CU
42 | CU
42.2 | CU
42.4 | CU
42.2 | CU
42.2 | CU
42.4 | CU
42.2 | CU
41.6 | CU
41.7 | CU
42.2 | CU
42.7 | CU
42.9 | CU
43.4 | CU
44 | CU
44.8 | CU
46.3 | CU
44.4 | CU
43.8 | CU
43.2 | CU
42.4 | CU
43.1 | CU
43.3 | CU
43.3 | CU
43.6 | CU
44.6 | CU
45.6 | CU
42.6 | CU
43.6 | CU
43.5 | CU
41.9 | CU
40.8 | CU
40.2 | CU
39.5 | CU
40.3 | CU
41.1 | CU
41.7 | CU
42 | CU
41.9 | CU
42 | CU
42 | CU
42.6 | CU
43 | CU
43.1 | CU
43 | CU
42.9 | CU
43 | CU
43.1 | CU
43.3 | CU
42.7 | CU
42.7 | CU
43.2 | CU
42.8 | CU
42.5 | CU
42.2 | CU
42.3 | CU
42.4 | CU
43.7 | CU
43.3 | CU
43.9 | CU
45.9 | CU
46 | CU
46.1 | CU
43.8 | CU
44.7 | CU
44.5 | CU
43.1 | CU
42.6 | CU
44.5 | CU
42.7 | CU
44.1 | CU
43.1 | CU
43 | CU
43.8 | CU
40.8 | CU
40.4 | CU
40 | CU
40.2 | CU
38.8 | CU
39.9 | CU
40.3 | CU
39.5 | CU
40.1 | CU
39.9 | CU
41.4 | CU
42.8 | CU
43 | CU
43.2 | CU
43.4 | CU
43.4 | CU
43.8 | CU
44.2 | CU
44.5 | CU
44.5 | CU
44.6 | CU
44.2 | CU
44.3 | CU
44.3 | CU
44.1 | CU
43.4 | CU
43.3 | CU
43.1 | CU
43.1 | CU
43.5 | CU
43.4 | CU
43.4 | CU
43.8 | CU
44.2 | CU
44.5 | CU
44.8 | CU
45 | CU
45.6 | CU
45.2 | CU
45.8 | CU
45.7 | CU
45.8 | CU
43 | CU
42 | CU
43.7 | CU
43.8 | CU
42 | CU
39.8 | CU
40.5 | CU
39.8 | CU
39.2 | CU
38.6 | CU
38.6 | CU
39.1 | CU
38.8 | CU
40.9 | CU
40.6 | CU
40.5 | CU
40.5 | CU
41.1 | CU
41.5 | CU
41.8 | CU
42.1 | CU
41.9 | CU
42.2 | CU
42.3 | CU
42.5 | CU
42.3 | CU
42.4 | CU
42 | CU
41.8 | CU
41.4 | CU
40.9 | CU
40.9 | CU
41.1 | CU
41.2 | CU
41.2 | CU
41.2 | CU
41.2 | CU
41.9 | CU
42.5 | CU
44.2 | CU
42.8 | CU
42.5 | CU
43.1 | CU
45.7 | CU
46.5 | CU
48.2 | CU
47.4 | CU
47.3 | CU
47.3 | CU
48.3 | CU
47.5 | CU
47.6 | CU
46.8 | CU
45.3 | CU
44.5 | CU
43.4 | CU
43 | CU
43.7 | CU
44.1 | CU
43.7 | CU
45.3 | CU
46.1 | CU
46.5 | CU
46.8 | CU
46.9 | CU
46.8 | CU
47.2 | CU
47.4 | CU
47.5 | CU
47.5 | CU
47.6 | CU
47.6 | CU
47.5 | CU
47.1 | CU
47.1 | CU
46.9 | CU
46.5 | CU
46.5 | CU
46.1 | CU
46.6 | CU
46.2 | CU
46.3 | CU
46.6 | CU
46.6 | CU
47.1 | CU
47.4 | CU
47.6 | CU
47.3 | CU
48.4 | CU
49.8 | CU
49.3 | CU
47.8 | CU
47.8 | CU
47.9 | CU
49.2 | CU
49.1 | CU
46.2 | CU
47.2 | CU
48.1 | CU
47.1 | CU
46.1 | CU
46.7 | CU
46.2 | CU
46.5 | CU
46.9 | CU
47 | CU
46.8 | CU
47 | CU
47.6 | CU
47.5 | CU
48.3 | CU
48.4 | CU
48.6 | CU
48.6 | CU
48.6 | CU
48.9 | CU
48.6 | CU
48.4 | CU
48.5 | CU
48.5 | CU
48.5 | CU
48.4 | CU
47.9 | CU
48.1 | CU
47.7 | CU
48.1 | CU
48.1 | CU
48.1 | CU
48.4 | CU
49.1 | CU
50 | CU
50.9 | CU
50.8 | CU
51.1 | CU
51.1 | CU
50.9 | CU
50.5 | CU
49.9 | CU
50.8 | CU
50.6 | CU
50.7 | CU
52.2 | CU
52.6 | CU
51.7 | CU
50.9 | CU
51.3 | CU
50.3 | CU
50.3 | CU
52.1 | CU
52.5 | CU
53.2 | CU
53.8 | CU
55.6 | CU
55.1 | CU
55.2 | CU
55.1 | CU
55.1 | CU
55.2 | CU
55 | CU
55 | CU
55.2 | CU
54.9 | CU
55 | CU
55 | CU
54.9 | CU
55.1 | CU
55.3 | CU
55 | CU
55.1 | CU
55.1 | CU
55.2 | CU
54.8 | CU
55.1 | CU
55 | CU
54.8 | CU
54.9 | CU
55.2 | CU
55 | CU
55 | CU
55.1 | CU
55.1 | CU
55 | CU
55 | CU
54.8 | CU
54.8 | CU
54.7 | CU
54.8 | CU
55.1 | CU
55.2 | CU
55.2 | CU
55.3 | CU
55.5 | CU
56 | CU
55.7 | CU
55.3 | CU
55.3 | CU
55.3 | CU
55.1 | CU
55.4 | CU
55.3 | CU
55.1 | CU
55.1 | CU
55.2 | CU
55 | CU
55 | CU
55.1 | CU
55.2 | CU
55.1 | CU
54.9 | CU
55.4 | CU
55.2 | CU
55.2 | CU
55 | CU
55.4 | CU
55.2 | CU
55.4 | CU
55.2 | CU
55.2 | CU
55.2 | CU
55.1 | CU
55.1 | CU
55.1 | CU
55.2 | CU
55 | CU
55.1 | CU
55.2 | CU
55 | CU
55 | CU
54.9 | CU
55 | CU
55.1 | CU
55 | CU
55.1 | CU
55.1 | CU
55.3 | CU
55.5 | CU
55.8 | CU
55.5 | CU
55.6 | CU
55.5 | CU
55.6 | CU
55.3 | CU
55.6 | CU
55.4 | CU
55.2 | CU
55.4 | CU
55.2 | CU
55.3 | CU
55.4 | CU
55.3 | CU
55.3 | CU
55.3 | CU
55.1 | CU
55.2 | CU
55.2 | CU
55.3 | CU
55.3 | CU
55.2 | CU
55.4 | CU
55.3 | CU
55.4 | CU
55.4 | CU
55.2 | CU
55.3 | CU
55 | CU
55.2 | CU
54.9 | CU
55.1 | CU
55.2 | CU
52.8 | CU
55.1 | CU
51.7 | CU
51.6 | CU
52.4 | CU
52.9 | CU
54.8 | CU
49.2 | CU
49.3 | CU
49.3 | CU
49.2 | CU
49.4 | CU
49.5 | CU
49.3 | CU
50 | CU
50.1 | CU
49.7 | CU
49.5 | CU
49.8 | CU
51.9 | CU
57.3 | CU
47.8 | CU
48 | CU
48 | CU
47.8 | CU
47.8 | CU
47.7 | CU
47.8 | CU
47.5 | CU
47.7 | CU
47.8 | CU
47.7 | CU
47.9 | CU
47.9 | CU
47.7 | CU
47.4 | CU
47.7 | CU
47.8 | CU
47.9 | CU
47.7 | CU
47.7 | CU
47.8 | CU
47.6 | CU
47.5 | CU
47.5 | CU
47.5 | CU
47.5 | CU
47.5 | CU
47.3 | CU
47.5 | CU
47.5 | CU
47.6 | CU
47.5 | CU
47 | CU
47.6 | CU
46.6 | CU
45.8 | CU
45.3 | CU
45.7 | CU
44.6 | CU
43.6 | CU
42.6 | CU
42 | CU
43.4 | CU
42.5 | CU
42.9 | CU
42.8 | CU
43.3 | CU
44 | CU
43.5 | CU
44 | CU
43.7 | CU
44.2 | CU
44.3 | CU
45.1 | CU
44.7 | CU
44.9 | CU
44.5 | CU
44.5 | CU
44.4 | CU
44.4 | CU
43.8 | CU
44.2 | CU
43.8 | CU
43.7 | CU
43 | CU
43.3 | CU
44 | CU
43.5 | CU
44 | CU
44.1 | CU
44.6 | CU
45.5 | CU
46.3 | CU
46.4 | CU
46.9 | CU
46.5 | CU
45.5 | CU
44.9 | CU
43.4 | CU
45.8 | CU
47.1 | CU
46.8 | CU
47.6 | CU
47.5 | CU
46.2 | CU
45.5 | CU
44.8 | CU
42.4 | CU
44.3 | CU
44 | CU
42.2 | CU
42 | CU
41.1 | CU
43.3 | CU
44.3 | CU
43.9 | CU
44 | CU
44.1 | CU
44.2 | CU
44.5 | CU
44.8 | CU
44.5 | CU
44.1 | CU
43.9 | CU
43.7 | CU
44 | CU
44 | CU
43.3 | CU
44 | CU
43.1 | CU
43.7 | CU
43.3 | CU
43.5 | CU
44.1 | CU
44.7 | CU
45.2 | CU
45.6 | CU
46.1 | CU
46.5 | CU
46.7 | CU
46.7 | CU
46.7 | CU
46.2 | CU
47.1 | CU
45.8 | CU
46.5 | CU
46.4 | CU
47 | CU
45 | CU
44.9 | CU
44.4 | CU
43.5 | CU
43.7 | CU
42.2 | CU
42.3 | CU
41.4 | CU
40.4 | CU
39.4 | CU
39.2 | CU
39.6 | CU
40.6 | CU
43.2 | CU
43.7 | CU
43.9 | CU
44.4 | CU
44.6 | CU
44.7 | CU
44.8 | CU
44.5 | CU
44 | CU
44.3 | CU
44.3 | CU
43.5 | CU
43.7 | CU
44 | CU
43.7 | CU
44 | CU
43.5 | CU
44 | CU
44.6 | CU
44.7 | CU
44.9 | CU
46.4 | CU
46.3 | CU
46.2 | CU
46 | CU
47.9 | CU
46.8 | CU
45.2 | CU
46.3 | CU
46.4 | CU
46.3 | CU
45.7 | CU
47 | CU
47.1 | CU
46.9 | CU
45.1 | CU
44 | CU
43.2 | CU
42.5 | CU
40.7 | CU
39.5 | CU
37.7 | CU
35.8 | CU
34.4 | CU
34.9 | CU
35.7 | CU
37.4 | CU
38.4 | CU
38.2 | CU
38.7 | CU
39.2 | CU
39.3 | CU
39.7 | CU
39.5 | CU
39.5 | CU
39.7 | CU
39.4 | CU
39.7 | CU
39.5 | CU
39.6 | CU
39.7 | CU
40.2 | CU
40.2 | CU
39.5 | CU
40.3 | CU
40.7 | CU
41.1 | CU
41.6 | CU
42.4 | CU
43.1 | CU
42.8 | CU
42.4 | CU
44 | CU
42.9 | CU
43.2 | CU
43.4 | CU
44.1 | CU
43.1 | CU
42.7 | CU
41.7 | CU
42 | CU
40.4 | CU
41.1 | CU
38.3 | CU
37.2 | CU
36.3 | CU
35.6 | CU
37 | CU
36.9 | CU
34.6 | CU
34.9 | CU
35.9 | CU
37.3 | CU
38.5 | CU
39.1 | CU
39.3 | CU
39 | CU
39.3 | CU
39 | CU
39.1 | CU
39.6 | CU
39.6 | CU
39.1 | CU
39.5 | CU
39.4 | CU
39.1 | CU
38.2 | CU
38.5 | CU
38.5 | CU
38.2 | CU
38.4 | CU
38.7 | CU
39.4 | CU
39.4 | CU
41 | CU
42 | CU
41.8 | CU
41.9 | CU
43.8 | CU
46.2 | CU
43.7 | CU
44.3 | CU
43.5 | CU
44.7 | CU
42.6 | CU
43.2 | CU
41.8 | CU
39.2 | CU
38.5 | CU
38.3 | CU
39.3 | CU
38.7 | CU
38.6 | CU
38.7 | CU
39.6 | CU
39.8 | CU
39.6 | CU
39.9 | CU
39.8 | CU
40.3 | CU
40.7 | CU
40.9 | CU
40.7 | CU
40.6 | CU
42.1 | CU
41.6 | CU
40.8 | CU
41.2 | CU
41.1 | CU
41.5 | CU
40.9 | CU
41.4 | CU
41 | CU
40.7 | CU
40.7 | CU
40.8 | CU
41.6 | CU
40.7 | CU
41.2 | CU
41.3 | CU
41.8 | CU
42.1 | CU
42.7 | CU
43.2 | CU
45 | CU
43.3 | CU
47.3 | CU
41.3 | CU
42.3 | CU
42.9 | CU
41 | CU
40.3 | CU
41.7 | CU
40.6 | CU
39.2 | CU
39.1 | CU
38.7 | CU
38 | CU
36.6 | CU
36.7 | CU
36.8 | CU
37 | CU
35.7 | CU
36.7 | CU
38.5 | CU
38.6 | CU
39 | CU
39.2 | CU
38.8 | CU
39.5 | CU
39.7 | CU
40.1 | CU
40.4 | CU
40.4 | CU
40.5 | CU
40.3 | CU
39.9 | CU
39.7 | CU
39.5 | CU
38.7 | CU
39.5 | CU
39.7 | CU
40.1 | CU
40.1 | CU
40.4 | CU
41.2 | CU
42.2 | CU
42.8 | CU
43.2 | CU
43.6 | CU
43.7 | CU
41.6 | CU
47.2 | CU
49.1 | CU
47 | CU
48.1 | CU
48.8 | CU
46.4 | CU
45.8 | CU
46.4 | CU
46.4 | CU
45 | CU
44.1 | CU
40.8 | CU
41.5 | CU
42.9 | CU
41.8 | CU
41 | CU
41.4 | CU
43.1 | CU
43.6 | CU
44.6 | CU
44.7 | CU
45.3 | CU
45.5 | CU
45.3 | CU
45.9 | CU
46.7 | CU
46 | CU
46.2 | CU
46.1 | CU
45.5 | CU
45.7 | CU
45.1 | CU
44.8 | CU
44.9 | CU
45 | CU
44.6 | CU
45.8 | CU
46.6 | CU
46.5 | CU
46.8 | CU
47.8 | CU
47.5 | CU
48.6 | CU
53.9 | CU
50.3 | CU
49.6 | CU
49.7 | CU
48.4 | CU
48.4 | CU
48.5 | CU
48.1 | CU
48.2 | CU
47.2 | CU
46.1 | CU
44.9 | CU
44.5 | CU
42.4 | CU
42.8 | CU
42.7 | CU
42.9 | CU
43.7 | CU
44.2 | CU
44.5 | CU
44.5 | CU
44.7 | CU
44.9 | CU
45.5 | CU
45.2 | CU
45.3 | CU
45.7 | CU
45.8 | CU
46 | CU
45.5 | CU
45.3 | CU
45.5 | CU
45.6 | CU
45.6 | CU
45.2 | CU
44.8 | CU
45 | CU
44.9 | CU
44.8 | CU
45.8 | CU
46.4 | CU
46.5 | CU
47.1 | CU
47.9 | CU
47.5 | CU
48.3 | CU
49 | CU
49.1 | CU
47 | CU
47.8 | CU
47.9 | CU
46.7 | CU
46.1 | CU
46.2 | CU
46.5 | CU
46.4 | CU
45.2 | CU
44 | CU
43.1 | CU
42.1 | CU
43.5 | CU
42.8 | CU
43.8 | CU
40.8 | CU
43.4 | CU
43.4 | CU
44.1 | CU
44.4 | CU
45.4 | CU
45.3 | CU
45.3 | CU
45.1 | CU
45.8 | CU
45.8 | CU
45.2 | CU
45.2 | CU
45.2 | CU
45.1 | CU
45.5 | CU
45.3 | CU
45.3 | CU
45.1 | CU
44.7 | CU
44.6 | CU
44.7 | CU
44.6 | CU
44.9 | CU
45 | CU
46.8 | CU
47.5 | CU
48.1 | CU
46.8 | CU
45.7 | CU
47.8 | CU
47.4 | CU
47.2 | CU
47 | CU
47.6 | CU
46.9 | CU
44.4 | CU
45.2 | CU
46.6 | CU
45.8 | CU
45.3 | CU
43.6 | CU
44.1 | CU
43.2 | CU
43.3 | CU
43.7 | CU
43.8 | CU
43.2 | CU
42.5 | CU
44 | CU
43.7 | CU
44.3 | CU
45.6 | CU
45.3 | CU
45.1 | CU
45.3 | CU
45 | CU
45 | CU
45.1 | CU
45.1 | CU
45.3 | CU
45.3 | CU
45.1 | CU
45.3 | CU
45.2 | CU
44.9 | CU
44.9 | CU
44.9 | CU
44.5 | CU
44.3 | CU
45.1 | CU
45.9 | CU
46.5 | CU
47.4 | CU
48.5 | CU
47.3 | CU
47.2 | CU
47.4 | CU
48.1 | CU
47.7 | CU
47.2 | CU
47.8 | CU
46.7 | CU
45.5 | CU
45.9 | CU
46.9 | CU
46.2 | CU
45.3 | CU
44.9 | CU
44.9 | CU
42.5 | CU
43.1 | CU
42.6 | CU
43.7 | CU
44.4 | CU
43.8 | CU
45.2 | CU
45.6 | CU
45.7 | CU
45.9 | CU
46 | CU
46.6 | CU
46.7 | CU
46.8 | CU
47.5 | CU
46.7 | CU
46.9 | CU
46.8 | CU
46.5 | CU
46.6 | CU
46.5 | CU
46.7 | CU
46.4 | CU
46.1 | CU
46.3 | CU
46.9 | CU
47.6 | CU
47.8 | CU
48.7 | CU
48.8 | CU
49.1 | CU
48.9 | CU
48.8 | CU
48.9 | CU
47.8 | CU
48.5 | CU
48.7 | CU
48.5 | CU
47.8 | CU
48 | CU
48.2 | CU
47.8 | CU
47.5 | CU
46.1 | CU
45.5 | CU
44 | CU
43.3 | CU
43.9 | CU
42.3 | CU
41.9 | CU
42.5 | CU
43.4 | CU
44.3 | CU
45.2 | CU
45.9 | CU
46.3 | CU
46.9 | CU
46.6 | CU
46.8 | CU
47.3 | CU
47.1 | CU
47.3 | CU
47.3 | CU
46.9 | CU
47 | CU
46.8 | CU
46.9 | CU
46.8 | CU
46.8 | CU
47 | CU
46.9 | CU
47.1 | CU
47 | CU
47.9 | CU
48.4 | CU
48.8 | CU
49.1 | CU
49.4 | CU
49.4 | CU
49.4 | CU
48.2 | CU
49.3 | CU
48.6 | CU
49.7 | CU
49.4 | CU
48.4 | CU
48.7 | CU
48.2 | CU
46.7 | CU
46.8 | CU
46 | CU
45.2 | CU
45 | CU
44.3 | CU
43.6 | CU
43 | CU
44 | CU
44.6 | CU
45.4 | CU
46.3 | CU
46.6 | CU
46.9 | CU
46.9 | CU
47.1 | CU
47.1 | CU
47.6 | CU
47.6 | CU
47.8 | CU
47.5 | CU
47.5 | CU
47 | CU
47.4 | CU
47 | CU
46.9 | CU
46.6 | CU
46 | CU
46.7 | CU
46.9 | CU
47.3 | CU
47.7 | CU
48.1 | CU
49.1 | CU
49.3 | CU
49.5 | CU
49.8 | CU
49.8 | CU
48.3 | CU
49.2 | CU
48.5 | CU
49.9 | CU
49.1 | CU
49.6 | CU
48.6 | CU
48.5 | CU
47.7 | CU
47.3 | CU
46.7 | CU
45.4 | CU
44.5 | CU
44.2 | CU
43.4 | CU
45.4 | CU
44.1 | CU
44 | CU
45.5 | CU
46.2 | CU
46.6 | CU
46.5 | CU
46.9 | CU
46.9 | CU
46.9 | CU
47.2 | CU
48 | CU
48.1 | CU
47.3 | CU
47.1 | CU
46.6 | CU
46.8 | CU
46.4 | CU
46.5 | CU
46.8 | CU
46.9 | CU
46.8 | CU
46.8 | CU
47.4 | CU
47.8 | CU
48 | CU
48.5 | CU
49 | CU
49.3 | CU
49.4 | CU
48.6 | CU
48.4 | CU
47.8 | CU
48.8 | CU
48.9 | CU
48.7 | CU
48.7 | CU
48 | CU
47.8 | CU
47 | CU
45.1 | CU
30 | CU
28.9 | CU
28.8 | CU
29.2 | CU
29 | CU
28.2 | CU
29.2 | CU
28.8 | CU
28.8 | CU
28.7 | CU
29 | CU
29.2 | CU
28.8 | CU
28.9 | CU
28.9 | CU
28.8 | CU
29 | CU
28.7 | CU
28.4 | CU
28.5 | CU
28.5 | CU
28.2 | CU
27.9 | CU
27.7 | CU
27.8 | CU
27.8 | CU
28.1 | CU
28.6 | CU
29.1 | CU
29.3 | CU
29.6 | CU
29.7 | CU
30.6 | CU
30.8 | CU
31 | CU
32.1 | CU
32 | CU
32.2 | CU
31.1 | CU
31.3 | CU
31 | CU
31.2 | CU
30.6 | CU
29.6 | CU
29.9 | CU
29.7 | CU
29.1 | CU
28.3 | CU
29 | CU
29.1 | CU
29.2 | CU
28.9 | CU
29.1 | CU
29.3 | CU
29 | CU
28.7 | CU
28.8 | CU
29.4 | CU
29.9 | CU
29.9 | CU
29.8 | CU
30.3 | CU
30 | CU
29.6 | CU
30.1 | CU
30.3 | CU
30 | CU
29.5 | CU
29.4 | CU
28.8 | CU
28.5 | CU
28 | CU
28.1 | CU
28.9 | CU
29.4 | CU
29.7 | CU
30.1 | CU
30.6 | CU
31.3 | CU
31.9 | CU
33.1 | CU
33.3 | CU
33.6 | CU
34.4 | CU
33.8 | CU
33.2 | CU
33.5 | CU
32.6 | CU
32.7 | CU
32.9 | CU
32.6 | CU
32.2 | CU
31.2 | CU
31.2 | CU
30.4 | CU
30.7 | CU
31 | CU
30.8 | CU
30.9 | CU
31 | CU
31.2 | CU
31.2 | CU
31.2 | CU
31.3 | CU
31.4 | CU
31.3 | CU
31.7 | CU
31.4 | CU
31.1 | CU
31.5 | CU
31.5 | CU
31.3 | CU
31 | CU
30.5 | CU
31 | CU
31.1 | CU
30.8 | CU
30.6 | CU
31 | CU
31.6 | CU
32.1 | CU
32.5 | CU
32.9 | CU
33.3 | CU
34.1 | CU
34.7 | CU
35.6 | CU
36.5 | CU
37.2 | CU
36.6 | CU
37.9 | CU
37.2 | CU
37.5 | CU
37.5 | CU
37.4 | CU
37.4 | CU
38.1 | CU
38.4 | CU
24.2 | CU
19.7 | CU
44.2 | CU
43.1 | CU
42.4 | CU
42.1 | CU
41.2 | CU
41 | CU
43.6 | CU
44.4 | CU
44.6 | CU
45.5 | CU
45.3 | CU
45.3 | CU
45.5 | CU
44.9 | CU
45.3 | CU
45.1 | CU
45.4 | CU
45.1 | CU
44.9 | CU
44.7 | CU
44.3 | CU
44.1 | CU
44.4 | CU
44 | CU
44.6 | CU
45.3 | CU
45.7 | CU
45.9 | CU
46.8 | CU
47.2 | CU
47.6 | CU
47.4 | CU
46.9 | CU
46.4 | CU
46.6 | CU
46.4 | CU
46.1 | CU
46.5 | CU
45.7 | CU
45.7 | CU
46.6 | CU
46.1 | CU
44.9 | CU
43 | CU
44.6 | CU
42.8 | CU
42 | CU
41.1 | CU
41.8 | CU
40.7 | CU
39.6 | CU
39.5 | CU
40.8 | CU
41.2 | CU
44.1 | CU
45 | CU
45.7 | CU
45.8 | CU
45.5 | CU
45.5 | CU
44.3 | CU
43.4 | CU
43 | CU
43.4 | CU
42.9 | CU
42.7 | CU
42.2 | CU
42.2 | CU
42.1 | CU
42.5 | CU
43.8 | CU
43.5 | CU
44.7 | CU
45.1 | CU
45.6 | CU
46.7 | CU
47.7 | CU
48.1 | CU
47.6 | CU
48.4 | CU
50.1 | CU
49 | CU
48.3 | CU
48.2 | CU
26.7 | CU
48.7 | CU
46.5 | CU
47.2 | CU
46.8 | CU
45.4 | CU
45.7 | CU
44.6 | CU
42.8 | CU
41.4 | CU
41.5 | CU
40.6 | CU
40.4 | CU
40 | CU
40.1 | CU
42.1 | CU
42.4 | CU
44 | CU
44.2 | CU
45.3 | CU
45.8 | CU
45.7 | CU
45.6 | CU
44.8 | CU
44.4 | CU
43.7 | CU
43.3 | CU
43 | CU
42.8 | CU
42.3 | CU
42.9 | CU
43.5 | CU
42.9 | CU
43.6 | CU
45.3 | CU
45.5 | CU
46.7 | CU
47.1 | CU
47.8 | CU
48.8 | CU
49.2 | CU
48.2 | CU
49.4 | CU
46.9 | CU
46.3 | CU
47 | CU
46.3 | CU
47.5 | CU
47.7 | CU
45.3 | CU
46.7 | CU
43.7 | CU
43.9 | CU
43.1 | CU
43.3 | CU
42.6 | CU
43.1 | CU
41.7 | CU
40.8 | CU
42.1 | CU
42.2 | CU
42.4 | CU
42.3 | CU
42.7 | CU
43.6 | CU
44 | CU
44 | CU
44.5 | CU
45.2 | CU
44.8 | CU
44.5 | CU
44.1 | CU
43.4 | CU
43.2 | CU
43.2 | CU
43 | CU
43.1 | CU
43.4 | CU
43.8 | CU
44.8 | CU
44.6 | CU
45.2 | CU
46.5 | CU
47.2 | CU
47.7 | CU
47.8 | CU
47.3 | CU
47.5 | CU
46.2 | CU
46.8 | CU
46.2 | CU
46.8 | CU
47 | CU
47.3 | CU
47 | CU
46.6 | CU
45.3 | CU
44.3 | CU
43.4 | CU
43.6 | CU
41.9 | CU
41 | CU
39.9 | CU
39.6 | CU
39.2 | CU
38.9 | CU
39.1 | CU
39.9 | CU
41 | CU
41.7 | CU
41.9 | CU
42.2 | CU
42.1 | CU
42.8 | CU
42.8 | CU
42.7 | CU
43.1 | CU
43.7 | CU
43.2 | CU
42.8 | CU
42.4 | CU
42.4 | CU
42.2 | CU
42.4 | CU
42.7 | CU
43 | CU
43.7 | CU
44.8 | CU
45.4 | CU
46.2 | CU
47.2 | CU
46.2 | CU
46.3 | CU
47.5 | CU
46.4 | CU
44.7 | CU
45.2 | CU
44.4 | CU
44.7 | CU
47.3 | CU
46.2 | CU
44.9 | CU
45.3 | CU
44 | CU
42.2 | CU
41.2 | CU
41.4 | CU
40 | CU
42.5 | CU
39.8 | CU
39.4 | CU
38.5 | CU
38.6 | CU
39.6 | CU
40.7 | CU
41.7 | CU
42.4 | CU
42.4 | CU
43.2 | CU
42.8 | CU
43.2 | CU
42.7 | CU
42.8 | CU
42.4 | CU
42.6 | CU
42.2 | CU
42.1 | CU
42 | CU
41.6 | CU
41.5 | CU
41.6 | CU
42.4 | CU
43.2 | CU
43.1 | CU
43.6 | CU
44 | CU
45.1 | CU
45.3 | CU
47.3 | CU
48.1 | CU
48 | CU
44.8 | CU
46.5 | CU
45.8 | CU
46.1 | CU
46.2 | CU
44.3 | CU
43.6 | CU
43.8 | CU
42.5 | CU
43.4 | CU
42.1 | CU
41.1 | CU
40.1 | CU
39.9 | CU
40.6 | CU
39.2 | CU
38.6 | CU
39.2 | CU
40 | CU
40.3 | CU
41.6 | CU
42 | CU
42.4 | CU
42.4 | CU
42.4 | CU
43.4 | CU
42.8 | CU
42.7 | CU
42.5 | CU
42.3 | CU
42.6 | CU
42.7 | CU
42.4 | CU
41.9 | CU
42.3 | CU
42.5 | CU
42.7 | CU
43.4 | CU
44.1 | CU
44.5 | CU
45.7 | CU
46.8 | CU
46.4 | CU
46.3 | CU
45.9 | CU
44.6 | CU
44.9 | CU
45.7 | CU
46.6 | CU
45.2 | CU
45 | CU
45 | CU
45.1 | CU
44.3 | CU
43.7 | CU
42.8 | CU
42.3 | CU
41.1 | CU
40.6 | CU
39.9 | CU
40 | CU
39.1 | CU
39.2 | CU
39.2 | CU
40.3 | CU
41.1 | CU
42.1 | CU
42.5 | CU
43.1 | CU
43.2 | CU
43.4 | CU
43.8 | CU
43.7 | CU
43.7 | CU
42.9 | CU
43 | CU
42.7 | CU
43.1 | CU
42.9 | CU
43 | CU
43.3 | CU
43.2 | CU
43.9 | CU
44.4 | CU
45.6 | CU
46.1 | CU
46.3 | CU
46.4 | CU
45.7 | CU
45.6 | CU
46.2 | CU
45.3 | CU
45.9 | CU
45.9 | CU
46 | CU
46.2 | CU
45.6 | CU
45.1 | CU
44.9 | CU
44.3 | CU
44 | CU
42.9 | CU
42.8 | CU
41.9 | CU
41.3 | CU
40.7 | CU
40.5 | CU
39.8 | CU
39.8 | CU
39.9 | CU
40.8 | CU
41.6 | CU
42.4 | CU
42.9 | CU
43.3 | CU
43.4 | CU
43.3 | CU
43.4 | CU
43.3 | CU
43.7 | CU
43.5 | CU
43.1 | CU
43 | CU
42.7 | CU
43.1 | CU
42.4 | CU
41 | CU
42.6 | CU
42.8 | CU
42.8 | CU
41.6 | CU
43.6 | CU
43.9 | CU
45.2 | CU
43.6 | CU
44.1 | CU
44.8 | CU
45.4 | CU
45.4 | CU
44.1 | CU
44.2 | CU
43.7 | CU
44.8 | CU
43.8 | CU
44.4 | CU
45.3 | CU
44.2 | CU
43.6 | CU
42.2 | CU
41.5 | CU
41.2 | CU
41.9 | CU
41.4 | CU
40.7 | CU
41.8 | CU
41.3 | CU
41.6 | CU
42.9 | CU
43.3 | CU
43.9 | CU
44.6 | CU
45.2 | CU
45.9 | CU
46 | CU
45.8 | CU
45.6 | CU
45 | CU
44.4 | CU
44.4 | CU
44 | CU
43.2 | CU
43.3 | CU
43.5 | CU
42.4 | CU
42.9 | CU
43.4 | CU
43.9 | CU
46.4 | CU
44 | CU
45.8 | CU
46.2 | CU
48.1 | CU
44.4 | CU
45 | CU
46.3 | CU
46.4 | CU
46 | CU
47.5 | CU
45.8 | CU
45.8 | CU
45.6 | CU
45.7 | CU
43.9 | CU
43.9 | CU
43.7 | CU
43.2 | CU
41.9 | CU
42 | CU
41.7 | CU
41.8 | CU
41.4 | CU
42.1 | CU
42.9 | CU
42.9 | CU
43.3 | CU
43.8 | CU
44.4 | CU
44.8 | CU
45.3 | CU
45.3 | CU
44.9 | CU
44.9 | CU
44.7 | CU
43.9 | CU
44.2 | CU
44.5 | CU
44.4 | CU
43 | CU
44.7 | CU
44.8 | CU
44.1 | CU
44 | CU
45.4 | CU
45.8 | CU
45.7 | CU
45.9 | CU
46.7 | CU
47.5 | CU
47.9 | CU
47.1 | CU
44.6 | CU
46.4 | CU
46.9 | CU
48.3 | CU
47.6 | CU
46.9 | CU
46.2 | CU
46.4 | CU
46.6 | CU
47.3 | CU
46 | CU
46.8 | CU
47.4 | CU
48.1 | CU
49.5 | CU
54.1 | CU
47.7 | CU
47.8 | CU
47.5 | CU
47.6 | CU
47.7 | CU
47.6 | CU
47.3 | CU
47.5 | CU
47.3 | CU
47.5 | CU
47.4 | CU
47.2 | CU
47.2 | CU
47.2 | CU
47.4 | CU
47.3 | CU
47.3 | CU
47.3 | CU
47.4 | CU
47.2 | CU
47.4 | CU
47.2 | CU
47.3 | CU
47 | CU
47.2 | CU
47.2 | CU
47.4 | CU
47.3 | CU
46.8 | CU
45.7 | CU
45.6 | CU
46.2 | CU
44.2 | CU
47.5 | CU
46.5 | CU
46.9 | CU
46.5 | CU
44.2 | CU
44.5 | CU
43.5 | CU
43.6 | CU
42.7 | CU
43.3 | CU
43.9 | CU
43.3 | CU
43.1 | CU
43.9 | CU
44.3 | CU
44.4 | CU
44.6 | CU
45 | CU
45.3 | CU
45.2 | CU
45.4 | CU
45.4 | CU
46 | CU
45.5 | CU
46.2 | CU
45.7 | CU
45.4 | CU
45.8 | CU
45.4 | CU
45.4 | CU
45.5 | CU
45.1 | CU
45.4 | CU
44.7 | CU
44.4 | CU
44.9 | CU
45.2 | CU
45.2 | CU
45.5 | CU
44.7 | CU
45.2 | CU
46 | CU
47.2 | CU
47.3 | CU
45 | CU
45.2 | CU
46.4 | CU
46.9 | CU
47.3 | CU
45.7 | CU
44.8 | CU
44.1 | CU
42.7 | CU
42.8 | CU
44 | CU
42.4 | CU
42.4 | CU
42.8 | CU
43.1 | CU
42.7 | CU
42.9 | CU
43.4 | CU
43.3 | CU
44.4 | CU
45.5 | CU
45 | CU
43.9 | CU
44.6 | CU
44.8 | CU
45.4 | CU
44.4 | CU
44.3 | CU
44.3 | CU
44.2 | CU
43.9 | CU
44 | CU
43.2 | CU
43.7 | CU
44.1 | CU
43.9 | CU
43.7 | CU
43.5 | CU
44.2 | CU
45.1 | CU
44.8 | CU
44.7 | CU
44.9 | CU
46.2 | CU
46.4 | CU
46.1 | CU
44.4 | CU
44.1 | CU
44.4 | CU
46.7 | CU
45.8 | CU
45 | CU
45.2 | CU
45.4 | CU
42.8 | CU
43.2 | CU
43.9 | CU
42 | CU
41.2 | CU
40.7 | CU
40.2 | CU
40.3 | CU
40.3 | CU
41.5 | CU
41.7 | CU
42.3 | CU
42.8 | CU
42.9 | CU
43.4 | CU
43.5 | CU
43.5 | CU
43.9 | CU
43.9 | CU
43.8 | CU
43.4 | CU
43.4 | CU
43.9 | CU
43.2 | CU
42.7 | CU
42.5 | CU
42.3 | CU
42.4 | CU
42.4 | CU
42.9 | CU
43.1 | CU
43.5 | CU
43.3 | CU
44.9 | CU
44.8 | CU
45.3 | CU
46.9 | CU
48.2 | CU
47.2 | CU
43.7 | CU
44 | CU
44.6 | CU
45.7 | CU
45.7 | CU
47 | CU
45.7 | CU
44.1 | CU
43.3 | CU
43.2 | CU
42.2 | CU
39.5 | CU
41.2 | CU
38.9 | CU
40.5 | CU
41.4 | CU
41.4 | CU
41.5 | CU
42.1 | CU
42.3 | CU
43.1 | CU
43.2 | CU
43.4 | CU
43.8 | CU
44.1 | CU
44.1 | CU
43.5 | CU
43.6 | CU
43.6 | CU
43.3 | CU
43.1 | CU
42.8 | CU
42.5 | CU
42.1 | CU
42.3 | CU
42.5 | CU
43.6 | CU
43.4 | CU
43.1 | CU
43.6 | CU
43.9 | CU
44.6 | CU
44.5 | CU
45.6 | CU
45.5 | CU
45.4 | CU
46.2 | CU
46 | CU
46.4 | CU
47.6 | CU
47.7 | CU
47.3 | CU
45.6 | CU
45.2 | CU
44.1 | CU
44.4 | CU
43.6 | CU
42.4 | CU
41.7 | CU
40.6 | CU
39.3 | CU
39.5 | CU
40.2 | CU
42.1 | CU
43.2 | CU
43.3 | CU
43.7 | CU
44.2 | CU
43.9 | CU
44 | CU
44.1 | CU
44.3 | CU
43.6 | CU
44.2 | CU
43.9 | CU
43 | CU
42.6 | CU
42.4 | CU
42.3 | CU
41.6 | CU
40.9 | CU
40.9 | CU
42.3 | CU
42.3 | CU
42.6 | CU
43.5 | CU
44.4 | CU
44.6 | CU
45.8 | CU
47.4 | CU
49.2 | CU
48.6 | CU
45.7 | CU
47.1 | CU
46.9 | CU
46.5 | CU
47 | CU
46.1 | CU
46.1 | CU
46.7 | CU
45.5 | CU
45.4 | CU
43.7 | CU
43.3 | CU
42.6 | CU
41.2 | CU
41.2 | CU
41.4 | CU
42.9 | CU
43 | CU
43.2 | CU
43.5 | CU
44 | CU
44.1 | CU
44.3 | CU
44.1 | CU
44 | CU
44.5 | CU
44.2 | CU
43.5 | CU
43.7 | CU
43.7 | CU
43.9 | CU
43.3 | CU
43.2 | CU
43.4 | CU
42.7 | CU
43.2 | CU
43.1 | CU
43.2 | CU
43.2 | CU
43.6 | CU
44.2 | CU
44.2 | CU
44.2 | CU
44.2 | CU
44.2 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
44.3 | CU
47.6 | CU
47 | CU
46.3 | CU
46.6 | CU
46.9 | CU
46.8 | CU
46.9 | CU
46.2 | CU
45.8 | CU
46.5 | CU
46.6 | CU
45.7 | CU
47.4 | CU
44.8 | CU
43.3 | CU
42.2 | CU
42.7 | CU
43.6 | CU
42.1 | CU
39.9 | CU
39.4 | CU
40 | CU
40.2 | CU
40.4 | CU
42.6 | CU
43.3 | CU
43 | CU
43 | CU
44 | CU
43.7 | CU
44.3 | CU
43.9 | CU
43.7 | CU
43.4 | CU
43.2 | CU
42.8 | CU
43.7 | CU
43 | CU
43.4 | CU
43.4 | CU
43.8 | CU
43.8 | CU
43.6 | CU
44.7 | CU
45 | CU
46 | CU
46 | CU
46.7 | CU
45.8 | CU
45.7 | CU
45.9 | CU
46.6 | CU
45.9 | CU
46.4 | CU
47.2 | CU
46 | CU
46.6 | CU
46.7 | CU
45.7 | CU
45.5 | CU
44.6 | CU
44.9 | CU
43.8 | CU
43.9 | CU
42.6 | CU
42.3 | CU
42.1 | CU
40.2 | CU
41.1 | CU
42 | CU
42.5 | CU
43.1 | CU
43 | CU
43.9 | CU
44.4 | CU
44.4 | CU
44.3 | CU
43.9 | CU
43.9 | CU
43.4 | CU
43.7 | CU
43.7 | CU
43.3 | CU
43.3 | CU
42.7 | CU
42.5 | CU
42.5 | CU
43.1 | CU
43.2 | CU
43.1 | CU
43.5 | CU
44.3 | CU
44.2 | CU
44.7 | CU
45.1 | CU
45.6 | CU
46.1 | CU
46.3 | CU
43.8 | CU
46 | CU
46.2 | CU
46.4 | CU
47.3 | CU
46.4 | CU
44.1 | CU
43.7 | CU
45.3 | CU
43.8 | CU
43.5 | CU
43.9 | CU
37.3 | CU
37.4 | CU
37.2 | CU
36.6 | CU
37.4 | CU
38 | CU
37.8 | CU
38.1 | CU
37.9 | CU
38.2 | CU
38.3 | CU
38.3 | CU
38.2 | CU
38.3 | CU
38.8 | CU
38.3 | CU
38.4 | CU
38.5 | CU
38 | CU
37.4 | CU
37.3 | CU
37.6 | CU
38 | CU
37.9 | CU
38 | CU
38.9 | CU
39.2 | CU
40 | CU
40.4 | CU
40.3 | CU
41 | CU
40.9 | CU
41.2 | CU
41.7 | CU
42.1 | CU
41.8 | CU
41.9 | CU
41.9 | CU
42.6 | CU
43.1 | CU
43.1 | CU
42.7 | CU
42.7 | CU
44.9 | CU
44.6 | CU
33.5 | CU
33.4 | CU
33.7 | CU
33.1 | CU
32.8 | CU
32.6 | CU
33.4 | CU
32.5 | CU
32.8 | CU
33.5 | CU
33.2 | CU
33.7 | CU
33.5 | CU
33.8 | CU
33.9 | CU
34.1 | CU
33.8 | CU
33.7 | CU
33.4 | CU
33.5 | CU
32.9 | CU
32.6 | CU
32.9 | CU
33 | CU
33.6 | CU
33.6 | CU
34.6 | CU
34.8 | CU
34.9 | CU
35.1 | CU
35.3 | CU
35.6 | CU
35.9 | CU
36.2 | CU
37 | CU
37.3 | CU
37.5 | CU
37.4 | CU
37.1 | CU
37.6 | CU
38.2 | CU
37.8 | CU
37.6 | CU
37.9 | CU
38.2 | CU
38.3 | CU
38.9 | CU
39.3 | CU
44.1 | CU
44.6 | CU
45.5 | CU
9.8 | CU
44 | CU
44.1 | CU
45.8 | CU
46 | CU
45.9 | CU
45.4 | CU
45.7 | CU
46.2 | CU
45.9 | CU
46 | CU
45.8 | CU
45.9 | CU
46 | CU
46.8 | CU
46.4 | CU
45.9 | CU
45.7 | CU
45.8 | CU
46.6 | CU
45.9 | CU
46.3 | CU
46.9 | CU
47.9 | CU
49 | CU
48.6 | CU
49.6 | CU
49 | CU
48.7 | CU
50.1 | CU
49 | CU
48.5 | CU
48.2 | CU
47.5 | CU
46.9 | CU
46.5 | CU
45.9 | CU
45.1 | CU
44.9 | CU
44.2 | CU
43.7 | CU
42.8 | CU
43.7 | CU
42.9 | CU
42.1 | CU
43.6 | CU
44.2 | CU
44.4 | CU
44.5 | CU
45.1 | CU
44.9 | CU
45 | CU
45.2 | CU
45.1 | CU
45.1 | CU
45 | CU
45.5 | CU
45.4 | CU
44.9 | CU
45.1 | CU
45.6 | CU
45.7 | CU
46.5 | CU
46.7 | CU
47.1 | CU
47.6 | CU
48 | CU
47.6 | CU
47.9 | CU
48 | CU
47.6 | CU
48.7 | CU
48.8 | CU
48.6 | CU
48.4 | CU
48.6 | CU
48.8 | CU
48.5 | CU
48.1 | CU
47.3 | CU
47 | CU
46.7 | CU
45.7 | CU
44.4 | CU
44.2 | CU
43.7 | CU
43 | CU
42.2 | CU
42.6 | CU
42 | CU
41.5 | CU
42.5 | CU
43.3 | CU
43.4 | CU
43.3 | CU
43.5 | CU
43.2 | CU
43.8 | CU
44 | CU
44.2 | CU
43.8 | CU
43.7 | CU
43.3 | CU
43.5 | CU
44 | CU
43.8 | CU
43.6 | CU
43.5 | CU
44.5 | CU
45.2 | CU
45.8 | CU
46.3 | CU
46.8 | CU
46.1 | CU
46.1 | CU
46 | CU
46.1 | CU
46.3 | CU
47 | CU
46.8 | CU
46.3 | CU
47.3 | CU
47.1 | CU
46.7 | CU
46.6 | CU
46.1 | CU
44.9 | CU
45.4 | CU
45.5 | CU
44.2 | CU
43.9 | CU
43.3 | CU
41.9 | CU
42 | CU
41.7 | CU
41.3 | CU
41.9 | CU
42.4 | CU
42.7 | CU
43.1 | CU
43.1 | CU
44.3 | CU
43.7 | CU
43.4 | CU
43.7 | CU
44.1 | CU
44.2 | CU
44.3 | CU
44.2 | CU
44.3 | CU
44.2 | CU
43.7 | CU
43.4 | CU
43.6 | CU
43.6 | CU
43.8 | CU
44 | CU
45.8 | CU
45.3 | CU
46.3 | CU
46.3 | CU
46.7 | CU
45.8 | CU
45.1 | CU
44.4 | CU
45.9 | CU
46.4 | CU
46.6 | CU
46.6 | CU
45.5 | CU
46.6 | CU
45.7 | CU
45.1 | CU
44.9 | CU
44.5 | CU
44.3 | CU
44 | CU
42.3 | CU
41.8 | CU
41.5 | CU
41.6 | CU
41.5 | CU
42 | CU
42.7 | CU
42.6 | CU
43.6 | CU
43.4 | CU
43.6 | CU
45.1 | CU
44.8 | CU
44.8 | CU
44.1 | CU
43.9 | CU
43.2 | CU
43.1 | CU
43 | CU
43.3 | CU
43 | CU
43.4 | CU
43.8 | CU
43.9 | CU
43.6 | CU
44.1 | CU
44.3 | CU
44.6 | CU
45.2 | CU
46.4 | CU
46.3 | CU
46.3 | CU
46.9 | CU
46.8 | CU
45.4 | CU
45.4 | CU
45.6 | CU
47 | CU
45.2 | CU
44.8 | CU
46.2 | CU
44.4 | CU
43.8 | CU
43.8 | CU
44.4 | CU
44.1 | CU
43.5 | CU
42.4 | CU
43.4 | CU
43.3 | CU
43.4 | CU
44 | CU
43.6 | CU
44.2 | CU
44.6 | CU
45.2 | CU
45.3 | CU
45.2 | CU
45.3 | CU
45.4 | CU
45.6 | CU
45.6 | CU
45.6 | CU
45.6 | CU
45.8 | CU
45.3 | CU
45.4 | CU
45.3 | CU
45.1 | CU
45.1 | CU
44.9 | CU
45.1 | CU
45.9 | CU
46.8 | CU
47.1 | CU
47.7 | CU
48.2 | CU
48.4 | CU
49.5 | CU
47.8 | CU
47.5 | CU
48.7 | CU
47 | CU
48.9 | CU
48.5 | CU
47.8 | CU
46.2 | CU
46.4 | CU
45.4 | CU
46.5 | CU
45.6 | CU
44.9 | CU
45.3 | CU
44.4 | CU
44.1 | CU
43.7 | CU
43.6 | CU
44.5 | CU
45.3 | CU
46.2 | CU
46.5 | CU
46.6 | CU
46.6 | CU
46.7 | CU
46.9 | CU
47 | CU
46.7 | CU
46.7 | CU
46.6 | CU
46.3 | CU
46.7 | CU
46.7 | CU
46.7 | CU
46.4 | CU
46.3 | CU
46.6 | CU
46.7 | CU
46.5 | CU
47.5 | CU
47.9 | CU
48.1 | CU
48.6 | CU
49.3 | CU
49.8 | CU
50.3 | CU
51.1 | CU
52 | CU
0 | CU
49.3 | CU
50.5 | CU
49.7 | CU
49.7 | CU
49.4 | CU
48.8 | CU
49.1 | CU
48.5 | CU
48 | CU
47.3 | CU
46.5 | CU
46.3 | CU
46.4 | CU
46 | CU
45.7 | CU
45.5 | CU
46.2 | CU
47.1 | CU
47.3 | CU
47.6 | CU
47.8 | CU
47.9 | CU
48.3 | CU
48.2 | CU
48.3 | CU
48.4 | CU
48.3 | CU
47.9 | CU
48 | CU
47.9 | CU
48.2 | CU
48.1 | CU
47.8 | CU
47.6 | CU
47.4 | CU
48 | CU
48.2 | CU
48.7 | CU
49.5 | CU
50.1 | CU
48.8 | CU
48.9 | CU
48.6 | CU
48.9 | CU
48.7 | CU
48.9 | CU
49.8 | CU
49.7 | CU
49.4 | CU
49.4 | CU
49.7 | CU
48.6 | CU
48.8 | CU
48 | CU
48.3 | CU
48.2 | CU
47.4 | CU
46.8 | CU
46.3 | CU
45.7 | CU
45.2 | CU
44.4 | CU
45.4 | CU
45.4 | CU
46.7 | CU
46.9 | CU
47 | CU
47.2 | CU
47.4 | CU
47.8 | CU
47.3 | CU
47.7 | CU
47.5 | CU
46.9 | CU
46.4 | CU
46 | CU
45.6 | CU
45.4 | CU
45.2 | CU
45.2 | CU
45.7 | CU
46.4 | CU
47.1 | CU
47.5 | CU
48.8 | CU
49.6 | CU
49.5 | CU
48.6 | CU
48.7 | CU
48.9 | CU
49.4 | CU
48.8 | CU
49.2 | CU
49.6 | CU
48.9 | CU
48.3 | CU
48.3 | CU
48.1 | CU
48.2 | CU
47.6 | CU
47.2 | CU
47.2 | CU
46.7 | CU
46.7 | CU
46.2 | CU
44.7 | CU
44.4 | CU
44.9 | CU
44.5 | CU
45.6 | CU
46 | CU
46.4 | CU
46.7 | CU
47.2 | CU
47.3 | CU
47.5 | CU
47.4 | CU
47 | CU
46.6 | CU
46.4 | CU
46 | CU
46.7 | CU
44.9 | CU
44.9 | CU
45.2 | CU
45.5 | CU
45.4 | CU
45.7 | CU
45.9 | CU
47 | CU
47.8 | CU
48.1 | CU
48.1 | CU
48.3 | CU
47.8 | CU
48.1 | CU
47.3 | CU
48.4 | CU
48.1 | CU
48.5 | CU
47.6 | CU
48 | CU
46.7 | CU
46.9 | CU
46.6 | CU
0 | CU
45 | CU
44.8 | CU
45.7 | CU
45.2 | CU
44.6 | CU
45 | CU
45.3 | CU
45.4 | CU
45.1 | CU
45.3 | CU
45.2 | CU
45.8 | CU
45.9 | CU
45.5 | CU
46 | CU
46.1 | CU
46.8 | CU
47 | CU
46.7 | CU
46.3 | CU
46.1 | CU
45.9 | CU
45.1 | CU
44.8 | CU
44.8 | CU
44.5 | CU
44.5 | CU
44.2 | CU
44.9 | CU
44.4 | CU
45.2 | CU
45.8 | CU
46 | CU
46.2 | CU
46.4 | CU
46.9 | CU
48.5 | CU
49.2 | CU
46.9 | CU
48 | CU
48.2 | CU
47.6 | CU
47.4 | CU
47.4 | CU
47.6 | CU
46.5 | CU
44.9 | CU
44.9 | CU
44.2 | CU
43.1 | CU
42.9 | CU
41.8 | CU
41.1 | CU
41 | CU
40.9 | CU
41.8 | CU
42.7 | CU
43.3 | CU
44.1 | CU
43.9 | CU
43.8 | CU
43.7 | CU
44 | CU
44.2 | CU
44.4 | CU
44.8 | CU
44.6 | CU
44 | CU
43.5 | CU
43.9 | CU
43.5 | CU
43.5 | CU
43.5 | CU
43.4 | CU
43.9 | CU
44.6 | CU
45.3 | CU
45.1 | CU
45 | CU
45.7 | CU
46.6 | CU
46.9 | CU
47 | CU
46.6 | CU
47.4 | CU
46.6 | CU
47.1 | CU
48.1 | CU
48 | CU
46.2 | CU
46.2 | CU
46.1 | CU
45.2 | CU
45.5 | CU
44.3 | CU
44 | CU
43.6 | CU
42 | CU
41.2 | CU
41.7 | CU
41.6 | CU
41.2 | CU
42.2 | CU
42.8 | CU
43.4 | CU
43.6 | CU
43.5 | CU
44.1 | CU
44.3 | CU
43.8 | CU
43 | CU
43.9 | CU
43.7 | CU
43.5 | CU
43.4 | CU
42.9 | CU
43.1 | CU
42.8 | CU
43.5 | CU
44.2 | CU
44.6 | CU
45.2 | CU
45.3 | CU
44.8 | CU
44.2 | CU
44.4 | CU
44.1 | CU
44.8 | CU
46.6 | CU
47.4 | CU
45.9 | CU
42.9 | CU
43.8 | CU
45.7 | CU
46.2 | CU
46.3 | CU
45.2 | CU
43.4 | CU
44.4 | CU
43 | CU
42.6 | CU
40.9 | CU
40.3 | CU
39.9 | CU
31.3 | CU
38.9 | CU
38.9 | CU
39.9 | CU
39.9 | CU
40.3 | CU
40.7 | CU
40.6 | CU
41 | CU
41.3 | CU
41.2 | CU
41 | CU
40.8 | CU
40.5 | CU
40.6 | CU
40.4 | CU
40.5 | CU
40.6 | CU
40.3 | CU
40.3 | CU
39.8 | CU
39.9 | CU
40.4 | CU
40.9 | CU
41.3 | CU
41.9 | CU
41.6 | CU
41.6 | CU
41.2 | CU
41.7 | CU
41.6 | CU
42.7 | CU
42.9 | CU
43.1 | CU
43.1 | CU
41.6 | CU
41.9 | CU
41.7 | CU
41.4 | CU
41.6 | CU
41 | CU
42.5 | CU
43.7 | CU
30.8 | CU
40.5 | CU
41.3 | CU
41.5 | CU
41.1 | CU
40.8 | CU
41.2 | CU
40.7 | CU
40.7 | CU
41.4 | CU
41.7 | CU
42 | CU
42 | CU
42.4 | CU
42.1 | CU
42.1 | CU
42 | CU
41.6 | CU
42.4 | CU
42.3 | CU
42.1 | CU
41.7 | CU
41.7 | CU
42.1 | CU
42.5 | CU
42.3 | CU
42.8 | CU
43.1 | CU
43.8 | CU
44 | CU
43.8 | CU
44.5 | CU
44.1 | CU
45.2 | CU
44.5 | CU
45 | CU
44.8 | CU
44.7 | CU
43.9 | CU
43.5 | CU
43.7 | CU
44 | CU
44 | CU
43.2 | CU
43.2 | CU
42.6 | CU
42.2 | CU
42.7 | CU
42 | CU
42.1 | CU
41.9 | CU
42.1 | CU
41.5 | CU
41.5 | CU
41.5 | CU
42.1 | CU
42.4 | CU
42.6 | CU
42.9 | CU
43 | CU
43 | CU
43.2 | CU
43.3 | CU
43 | CU
43.1 | CU
43.1 | CU
43 | CU
43.2 | CU
43.1 | CU
42.8 | CU
42.6 | CU
42.5 | CU
42.9 | CU
43.3 | CU
43.6 | CU
44.5 | CU
45.8 | CU
45.7 | CU
46.4 | CU
47.3 | CU
47.5 | CU
47.1 | CU
46.1 | CU
45.8 | CU
46.4 | CU
45.8 | CU
46.3 | CU
46.9 | CU
46.2 | CU
45.9 | CU
45 | CU
44.8 | CU
46 | CU
46.4 | CU
48.7 | CU
51.3 | CU
0.5 | CU
0.1 | CU
44.3 | CU
43.2 | CU
43.9 | CU
44.8 | CU
45.3 | CU
45.3 | CU
45.4 | CU
45.6 | CU
46.1 | CU
45.9 | CU
46 | CU
45.8 | CU
45.7 | CU
45.9 | CU
45.7 | CU
45.7 | CU
45.4 | CU
45.4 | CU
44.8 | CU
44.6 | CU
44.3 | CU
44 | CU
44.3 | CU
44.3 | CU
44.9 | CU
45.9 | CU
47.5 | CU
46.4 | CU
47.8 | CU
46.7 | CU
46.8 | CU
47.5 | CU
46.2 | CU
46.4 | CU
46.3 | CU
46.3 | CU
46.2 | CU
45.8 | CU
45.3 | CU
45.5 | CU
45.5 | CU
45.2 | CU
45.1 | CU
0.4 | CU
42.2 | CU
42.3 | CU
43.6 | CU
29.5 | CU
44.5 | CU
44.7 | CU
45.1 | CU
45.6 | CU
45.8 | CU
46.3 | CU
46.4 | CU
46.6 | CU
46.4 | CU
45.9 | CU
46 | CU
45.9 | CU
45.8 | CU
44.9 | CU
43.5 | CU
44 | CU
42.9 | CU
43 | CU
43.6 | CU
43 | CU
44.4 | CU
44 | CU
43.8 | CU
45.2 | CU
45.9 | CU
45.6 | CU
46.8 | CU
48.8 | CU
46.8 | CU
46.1 | CU
45.5 | CU
46.3 | CU
47.5 | CU
47.9 | CU
46.4 | CU
45.6 | CU
45.2 | CU
44.4 | CU
43.2 | CU
43.2 | CU
44.3 | CU
42.9 | CU
42.5 | CU
42.1 | CU
42.6 | CU
42.4 | CU
42.3 | CU
43 | CU
43 | CU
42.8 | CU
43.1 | CU
43.1 | CU
43.3 | CU
43.6 | CU
43.3 | CU
42.9 | CU
42.5 | CU
42.5 | CU
42.2 | CU
42.1 | CU
41.7 | CU
42.2 | CU
44.1 | CU
42.4 | CU
42 | CU
41.5 | CU
41.5 | CU
42 | CU
42.1 | CU
42.6 | CU
42.1 | CU
43.2 | CU
44.1 | CU
46.1 | CU
48.4 | CU
49.6 | CU
45.3 | CU
46.5 | CU
47.2 | CU
44 | CU
44.4 | CU
43.6 | CU
43.8 | CU
0.3 | CU
41.7 | CU
41.8 | CU
41.5 | CU
41.7 | CU
40.1 | CU
40 | CU
39 | CU
39.4 | CU
40.8 | CU
41.8 | CU
42.3 | CU
42.9 | CU
43.3 | CU
43.6 | CU
43.3 | CU
43 | CU
42.5 | CU
42.1 | CU
42.1 | CU
41.6 | CU
41.3 | CU
40.9 | CU
41.9 | CU
41.4 | CU
39.6 | CU
40.5 | CU
40.4 | CU
40.9 | CU
41.3 | CU
42.3 | CU
42.2 | CU
42.6 | CU
43.6 | CU
44.1 | CU
44.2 | CU
45.2 | CU
46.4 | CU
47.5 | CU
47.2 | CU
46 | CU
46.5 | CU
43.4 | CU
44.4 | CU
43.7 | CU
41.9 | CU
41.5 | CU
42.3 | CU
41 | CU
41.3 | CU
40.5 | CU
40.1 | CU
39.9 | CU
39.8 | CU
40.5 | CU
40.6 | CU
41 | CU
41.3 | CU
41.6 | CU
41.7 | CU
41.9 | CU
42.1 | CU
42.2 | CU
42.3 | CU
42 | CU
41.8 | CU
42 | CU
42 | CU
42.2 | CU
42.2 | CU
41.9 | CU
41.5 | CU
41.6 | CU
41.9 | CU
42.1 | CU
42.4 | CU
43.1 | CU
43.4 | CU
44.1 | CU
45.4 | CU
45 | CU
45.7 | CU
46.2 | CU
47.5 | CU
47.5 | CU
47 | CU
46.3 | CU
46 | CU
46.3 | CU
46 | CU
45.1 | CU
44.7 | CU
43 | CU
41.8 | CU
42.1 | CU
41.9 | CU
41.5 | CU
40.7 | CU
39.9 | CU
40.2 | CU
39.8 | CU
40.2 | CU
41.7 | CU
42.9 | CU
43.2 | CU
43 | CU
43.4 | CU
43.4 | CU
43.3 | CU
43.4 | CU
43.6 | CU
43.6 | CU
43.6 | CU
43.9 | CU
43.8 | CU
42.7 | CU
43.4 | CU
42.9 | CU
42.2 | CU
42.3 | CU
42.8 | CU
43.6 | CU
43.6 | CU
43.9 | CU
44.3 | CU
45.1 | CU
47.1 | CU
46.8 | CU
46.5 | CU
46.7 | CU
48.3 | CU
45.6 | CU
47.4 | CU
46.8 | CU
46.1 | CU
46.2 | CU
46 | CU
47.1 | CU
46.7 | CU
45.5 | CU
44 | CU
42.9 | CU
43.2 | CU
42.1 | CU
42.3 | CU
41.8 | CU
41.2 | CU
42.4 | CU
42.7 | CU
43.1 | CU
43.7 | CU
43.7 | CU
44.3 | CU
44.3 | CU
44.3 | CU
45.5 | CU
45.2 | CU
45.2 | CU
45 | CU
45 | CU
44 | CU
44.1 | CU
44.5 | CU
44.8 | CU
44.6 | CU
44.4 | CU
44.6 | CU
45.2 | CU
45.6 | CU
46.4 | CU
46.8 | CU
46.6 | CU
47 | CU
47.7 | CU
47.9 | CU
47.5 | CU
48.7 | CU
47.9 | CU
46.7 | CU
47 | CU
47.5 | CU
47.2 | CU
47.3 | CU
46.3 | CU
46.7 | CU
45.9 | CU
45.7 | CU
44.9 | CU
44.6 | CU
44.1 | CU
42.6 | CU
41.9 | CU
42.1 | CU
41.9 | CU
42.7 | CU
44.1 | CU
44.3 | CU
44.6 | CU
45.2 | CU
44.5 | CU
44.7 | CU
44.9 | CU
44.5 | CU
44.7 | CU
44.9 | CU
44.6 | CU
44.6 | CU
44.2 | CU
44.7 | CU
44.5 | CU
43.8 | CU
44.4 | CU
44.6 | CU
44.5 | CU
44.2 | CU
44.7 | CU
45.6 | CU
45.8 | CU
45.9 | CU
46.6 | CU
47.5 | CU
47.3 | CU
47.3 | CU
47.8 | CU
47.7 | CU
48 | CU
46.7 | CU
47.5 | CU
46.9 | CU
47.2 | CU
46.9 | CU
44.8 | CU
44.1 | CU
45.5 | CU
44.7 | CU
43.4 | CU
42.7 | CU
43.6 | CU
42.9 | CU
42.7 | CU
43.6 | CU
43.8 | CU
44 | CU
44.3 | CU
44.6 | CU
44.5 | CU
44.2 | CU
44.5 | CU
44.7 | CU
44.2 | CU
44.2 | CU
43.6 | CU
43.6 | CU
43.1 | CU
42.9 | CU
43.1 | CU
42.8 | CU
42.6 | CU
43.1 | CU
43.6 | CU
44.1 | CU
44.2 | CU
44.4 | CU
45 | CU
45 | CU
46.4 | CU
46.7 | CU
46.7 | CU
47.4 | CU
47.5 | CU
47.9 | CU
46.6 | CU
45.8 | CU
47.1 | CU
46.8 | CU
45.9 | CU
45.3 | CU
44.3 | CU
43.5 | CU
43.5 | CU
43.5 | CU
43.6 | CU
43.8 | CU
43.8 | CU
43.5 | CU
43 | CU
42.8 | CU
43.7 | CU
43.6 | CU
43.9 | CU
43.8 | CU
44.3 | CU
44.1 | CU
44.4 | CU
44.2 | CU
43.8 | CU
43.8 | CU
43.3 | CU
42.9 | CU
42.6 | CU
42.2 | CU
41.9 | CU
42 | CU
41.5 | CU
42.2 | CU
42.3 | CU
42.5 | CU
42.1 | CU
42.8 | CU
43.2 | CU
44.1 | CU
45 | CU
45.3 | CU
46.2 | CU
45.4 | CU
43.3 | CU
43.2 | CU
43.3 | CU
43.6 | CU
43.7 | CU
43.4 | CU
43.4 | CU
42.4 | CU
42.2 | CU
42.9 | CU
42.7 | CU
41.6 | CU
41.5 | CU
41.9 | CU
42 | CU
41.7 | CU
41.7 | CU
41.8 | CU
41.9 | CU
42.4 | CU
42.2 | CU
42.4 | CU
42 | CU
42 | CU
41.6 | CU
41.4 | CU
41.5 | CU
40.9 | CU
40.4 | CU
39.9 | CU
40.7 | CU
40.2 | CU
39.4 | CU
40.4 | CU
40.4 | CU
40.6 | CU
40.9 | CU
40.8 | CU
41.4 | CU
41.7 | CU
42.5 | CU
43 | CU
43.1 | CU
43.2 | CU
43.9 | CU
44.6 | CU
45.9 | CU
45.9 | CU
44.4 | CU
45.9 | CU
45.3 | CU
42.6 | CU
43.1 | CU
41.5 | CU
39.8 | CU
40.2 | CU
38.6 | CU
39.6 | CU
38.9 | CU
37.6 | CU
37.1 | CU
37.5 | CU
38.2 | CU
38.6 | CU
38.2 | CU
38.4 | CU
38.5 | CU
39 | CU
39.4 | CU
39 | CU
39.7 | CU
40.6 | CU
39.3 | CU
38.6 | CU
39.4 | CU
39.3 | CU
38.7 | CU
39.3 | CU
39.2 | CU
38.8 | CU
40 | CU
40.9 | CU
39.8 | CU
40.7 | CU
40.4 | CU
42.4 | CU
42.5 | CU
42.8 | CU
45.1 | CU
45.8 | CU
46.3 | CU
45.5 | CU
45.4 | CU
44.4 | CU
44.8 | CU
43.4 | CU
43 | CU
43.6 | CU
41.9 | CU
41.5 | CU
41.7 | CU
39.8 | CU
38.6 | CU
38.6 | CU
38.6 | CU
37.2 | CU
36.5 | CU
38.1 | CU
37.9 | CU
38.5 | CU
38.9 | CU
39.3 | CU
39.4 | CU
39.8 | CU
41.1 | CU
41 | CU
40.9 | CU
41.1 | CU
41.2 | CU
39.9 | CU
39.7 | CU
39.3 | CU
39.1 | CU
39.2 | CU
39.6 | CU
39.3 | CU
40.8 | CU
39.8 | CU
40.3 | CU
40.5 | CU
40.8 | CU
41.3 | CU
42.1 | CU
43.5 | CU
44.1 | CU
44.9 | CU
45.5 | CU
44.8 | CU
43.8 | CU
47.7 | CU
46.1 | CU
44.2 | CU
44.1 | CU
43.6 | CU
42.3 | CU
41.1 | CU
39.9 | CU
38.5 | CU
38.8 | CU
37.6 | CU
36.2 | CU
37.8 | CU
37.9 | CU
38.1 | CU
38.6 | CU
39.2 | CU
39.3 | CU
38.8 | CU
38.1 | CU
38.4 | CU
38.6 | CU
39.2 | CU
39.4 | CU
39.6 | CU
40.1 | CU
39.6 | CU
39.8 | CU
40.1 | CU
40.1 | CU
39.3 | CU
40.3 | CU
40.5 | CU
40 | CU
40.4 | CU
41 | CU
41.9 | CU
42.6 | CU
43 | CU
43.2 | CU
43.8 | CU
44.8 | CU
43.5 | CU
45.4 | CU
44.7 | CU
46.1 | CU
46.6 | CU
44.9 | CU
44.6 | CU
43.2 | CU
42.9 | CU
42 | CU
41.4 | CU
40.9 | CU
39.8 | CU
39.5 | CU
38.5 | CU
38 | CU
38.2 | CU
35.8 | CU
37.3 | CU
38.3 | CU
37.1 | CU
37 | CU
38.7 | CU
39.8 | CU
40.8 | CU
39.3 | CU
39.7 | CU
39.8 | CU
39.8 | CU
39.6 | CU
40.5 | CU
40.1 | CU
40.1 | CU
39.7 | CU
39.5 | CU
39.3 | CU
39.7 | CU
39.9 | CU
41.3 | CU
42.1 | CU
42.4 | CU
42.9 | CU
43.4 | CU
44.3 | CU
43.3 | CU
44.3 | CU
44.8 | CU
43.9 | CU
45.1 | CU
44.8 | CU
44.9 | CU
43.9 | CU
43.7 | CU
43 | CU
42.3 | CU
41.1 | CU
39.8 | CU
40.6 | CU
39.8 | CU
36.6 | CU
37 | CU
39 | CU
38.8 | CU
38.6 | CU
38.4 | CU
38.9 | CU
38.4 | CU
38.3 | CU
38.3 | CU
39.1 | CU
39.3 | CU
39.1 | CU
38.4 | CU
39.2 | CU
39.1 | CU
39.3 | CU
39.5 | CU
39.5 | CU
39.6 | CU
39.6 | CU
39.4 | CU
39.7 | CU
39.8 | CU
39.4 | CU
39.6 | CU
40.7 | CU
41 | CU
41.1 | CU
42.5 | CU
42.9 | CU
44.8 | CU
46 | CU
47.1 | CU
48 | CU
47.5 | CU
48.2 | CU
47.8 | CU
48.2 | CU
46.2 | CU
45.4 | CU
44.4 | CU
46.3 | CU
44.3 | CU
44.4 | CU
43.5 | CU
42.9 | CU
41.1 | CU
38.1 | CU
36.1 | CU
35.1 | CU
34.3 | CU
36.5 | CU
37 | CU
36.6 | CU
36 | CU
37.1 | CU
37.4 | CU
37.3 | CU
37 | CU
37.2 | CU
37.3 | CU
37.3 | CU
37 | CU
37.1 | CU
37.6 | CU
37.3 | CU
36.7 | CU
37.3 | CU
37.1 | CU
37.4 | CU
38.3 | CU
38.3 | CU
39.1 | CU
38.1 | CU
41.4 | CU
43.9 | CU
45.1 | CU
45.1 | CU
44.2 | CU
44.2 | CU
49 | CU
49.7 | CU
47.7 | CU
45 | CU
48.2 | CU
46.7 | CU
47.7 | CU
49.1 | CU
47.4 | CU
48.3 | CU
49.6 | CU
50.2 | CU
52.4 | CU
47.8 | CU
48 | CU
47.6 | CU
47.6 | CU
47.5 | CU
47.6 | CU
47.8 | CU
47.7 | CU
47.5 | CU
47.3 | CU
47.5 | CU
47.6 | CU
47.5 | CU
47.3 | CU
47.1 | CU
47.6 | CU
47.4 | CU
47.4 | CU
47.3 | CU
47.2 | CU
47.5 | CU
47.5 | CU
47.4 | CU
47.3 | CU
47.2 | CU
47.1 | CU
47.4 | CU
47.4 | CU
47.2 | CU
47.1 | CU
46.6 | CU
46.3 | CU
46.7 | CU
46.8 | CU
46.7 | CU
47.8 | CU
45.6 | CU
46.8 | CU
44.4 | CU
44.2 | CU
43.8 | CU
44.9 | CU
42.8 | CU
41.8 | CU
40.5 | CU
39.9 | CU
38.1 | CU
37.4 | CU
36.3 | CU
34.4 | CU
34 | CU
34 | CU
32.9 | CU
34 | CU
35.3 | CU
37.1 | CU
37.8 | CU
38 | CU
37.9 | CU
37.9 | CU
38.6 | CU
38.7 | CU
38.7 | CU
39 | CU
39.2 | CU
38.8 | CU
39 | CU
38.8 | CU
39 | CU
38.2 | CU
37.9 | CU
39.7 | CU
40.8 | CU
40.7 | CU
41.9 | CU
44.1 | CU
45.7 | CU
46 | CU
46 | CU
46.4 | CU
47.3 | CU
46.9 | CU
47.5 | CU
46.2 | CU
46.1 | CU
44.9 | CU
46 | CU
44.4 | CU
43.8 | CU
43.4 | CU
41.7 | CU
41.7 | CU
40.4 | CU
39.1 | CU
38.2 | CU
36.9 | CU
36.2 | CU
36 | CU
36.2 | CU
36 | CU
39.1 | CU
39.2 | CU
39.5 | CU
39.8 | CU
40.3 | CU
40.9 | CU
40.7 | CU
40.8 | CU
40.7 | CU
40.5 | CU
40.4 | CU
40 | CU
39.8 | CU
39.9 | CU
39.8 | CU
40.2 | CU
40.2 | CU
40.8 | CU
40.8 | CU
40.4 | CU
43 | CU
44.1 | CU
45.4 | CU
45.8 | CU
45.4 | CU
44.5 | CU
46.4 | CU
46.5 | CU
45.1 | CU
45.8 | CU
45.8 | CU
47.1 | CU
46.7 | CU
43.8 | CU
44.7 | CU
41.6 | CU
40.3 | CU
39.4 | CU
39.5 | CU
38.9 | CU
37.8 | CU
36.3 | CU
36.5 | CU
37.5 | CU
35.8 | CU
36.5 | CU
38.8 | CU
39.4 | CU
39.8 | CU
39.8 | CU
39.6 | CU
39.5 | CU
39.7 | CU
40.2 | CU
39.4 | CU
40 | CU
39.6 | CU
39 | CU
39.5 | CU
39.7 | CU
39.7 | CU
38.7 | CU
38.9 | CU
38.8 | CU
39.3 | CU
39.3 | CU
40.5 | CU
40.8 | CU
41.3 | CU
42.3 | CU
43.5 | CU
44.6 | CU
44.6 | CU
45.3 | CU
46.5 | CU
46.9 | CU
47.5 | CU
44.5 | CU
42.9 | CU
42.6 | CU
42.3 | CU
41.3 | CU
41.7 | CU
39.3 | CU
38.3 | CU
38.4 | CU
37.6 | CU
35.7 | CU
35.7 | CU
34.8 | CU
34.8 | CU
35.6 | CU
36.6 | CU
37.1 | CU
37.5 | CU
38.6 | CU
39.4 | CU
38.7 | CU
39 | CU
39.7 | CU
39.6 | CU
39.7 | CU
39.9 | CU
40.2 | CU
39.7 | CU
39.5 | CU
39.5 | CU
39.9 | CU
40.4 | CU
40.8 | CU
41.1 | CU
41.7 | CU
42.9 | CU
44.5 | CU
45.5 | CU
46.4 | CU
47.5 | CU
47.5 | CU
47.1 | CU
47 | CU
47.9 | CU
48.5 | CU
48.9 | CU
49.3 | CU
48.9 | CU
49.3 | CU
48.3 | CU
48.5 | CU
47.9 | CU
49.2 | CU
53.1 | CU
47.9 | CU
47.8 | CU
47.8 | CU
47.8 | CU
47.5 | CU
47.4 | CU
47.4 | CU
47.5 | CU
47.4 | CU
47.2 | CU
47.4 | CU
47.3 | CU
47.2 | CU
47 | CU
47.1 | CU
47.3 | CU
47.2 | CU
47.2 | CU
47.3 | CU
47.3 | CU
47.4 | CU
47.5 | CU
47.5 | CU
47.4 | CU
47 | CU
47.2 | CU
46.6 | CU
46.4 | CU
46.3 | CU
46.3 | CU
46 | CU
46.2 | CU
46.3 | CU
46.8 | CU
46.8 | CU
46.9 | CU
46.6 | CU
46.3 | CU
46.1 | CU
46 | CU
45.3 | CU
44.9 | CU
44.7 | CU
44.2 | CU
41.5 | CU
40.3 | CU
39.4 | CU
37.7 | CU
37 | CU
36.5 | CU
36.4 | CU
35.8 | CU
36.5 | CU
38 | CU
38.6 | CU
38.7 | CU
38.9 | CU
39.4 | CU
39.6 | CU
39.7 | CU
40.1 | CU
39.9 | CU
40.6 | CU
40.4 | CU
40.2 | CU
41.1 | CU
40.1 | CU
39.2 | CU
39.3 | CU
39.1 | CU
40.1 | CU
41 | CU
41.8 | CU
42.4 | CU
43.3 | CU
44.1 | CU
46 | CU
47 | CU
46.8 | CU
47 | CU
46.9 | CU
47.3 | CU
46.4 | CU
46.8 | CU
46.3 | CU
46.1 | CU
46.2 | CU
44.6 | CU
44.1 | CU
43.4 | CU
42.7 | CU
41.5 | CU
40.5 | CU
38.9 | CU
36.5 | CU
35.3 | CU
34.6 | CU
34.8 | CU
35.2 | CU
37.8 | CU
38.4 | CU
38.3 | CU
38 | CU
38.6 | CU
39.6 | CU
39.3 | CU
39 | CU
39.2 | CU
39.1 | CU
40 | CU
39.3 | CU
38.6 | CU
39.8 | CU
38.5 | CU
38.2 | CU
39.3 | CU
39.2 | CU
40.1 | CU
40.6 | CU
40 | CU
43.1 | CU
43.9 | CU
45.1 | CU
46.1 | CU
45 | CU
45.9 | CU
44.4 | CU
45.4 | CU
48.9 | CU
49.6 | CU
45.9 | CU
46.8 | CU
46.6 | CU
44.8 | CU
43.5 | CU
41.9 | CU
40.7 | CU
41.8 | CU
38.6 | CU
38 | CU
37.3 | CU
35.6 | CU
34.9 | CU
34.7 | CU
35.2 | CU
36.8 | CU
37.8 | CU
37.7 | CU
37.3 | CU
37.3 | CU
38.5 | CU
38.6 | CU
38.5 | CU
38.1 | CU
38.5 | CU
38.9 | CU
38.9 | CU
38.2 | CU
38.7 | CU
38.8 | CU
38.7 | CU
39.7 | CU
45.2 | CU
40.3 | CU
43.4 | CU
41 | CU
43.4 | CU
44.9 | CU
47.8 | CU
49.4 | CU
48.5 | CU
53 | CU
50.3 | CU
50.2 | CU
49.8 | CU
51.3 | CU
23.8 | CU
24.6 | CU
45.8 | CU
44.3 | CU
43.1 | CU
41.9 | CU
40.6 | CU
38.7 | CU
37.4 | CU
37.3 | CU
36.8 | CU
34.7 | CU
34.2 | CU
34.5 | CU
34 | CU
35.5 | CU
37.6 | CU
37.7 | CU
38.1 | CU
38.5 | CU
39.2 | CU
39.5 | CU
39.9 | CU
39.5 | CU
39.3 | CU
39.7 | CU
38.8 | CU
39.8 | CU
37.9 | CU
37.7 | CU
38 | CU
39.1 | CU
40.7 | CU
39.1 | CU
38.8 | CU
38.6 | CU
36.5 | CU
41.3 | CU
43.8 | CU
42.6 | CU
44.3 | CU
45.1 | CU
45.5 | CU
45.5 | CU
48.8 | CU
48.2 | CU
46.1 | CU
45.7 | CU
45.3 | CU
44.7 | CU
43.5 | CU
42.8 | CU
41.2 | CU
40.6 | CU
38.8 | CU
38.1 | CU
37.1 | CU
35.7 | CU
35.6 | CU
34.7 | CU
34.7 | CU
34.3 | CU
35.6 | CU
36.8 | CU
37.9 | CU
38.8 | CU
38.8 | CU
39.4 | CU
39.3 | CU
39.5 | CU
40.4 | CU
40 | CU
39.7 | CU
39 | CU
37.5 | CU
37.2 | CU
37.5 | CU
38.5 | CU
40.5 | CU
40.8 | CU
41.5 | CU
42.1 | CU
43.1 | CU
44.4 | CU
45.5 | CU
45.3 | CU
46.4 | CU
48.4 | CU
45.8 | CU
45.7 | CU
45.7 | CU
48.1 | CU
46 | CU
46 | CU
43.4 | CU
43.6 | CU
42.5 | CU
42.1 | CU
41.1 | CU
39.6 | CU
38.4 | CU
37.7 | CU
37.6 | CU
36.1 | CU
34.7 | CU
34.1 | CU
34.4 | CU
34.4 | CU
34.8 | CU
36.6 | CU
37.1 | CU
37.3 | CU
37.3 | CU
38.2 | CU
38 | CU
38.1 | CU
37.9 | CU
38.3 | CU
38.3 | CU
38.2 | CU
38.9 | CU
39.1 | CU
38.4 | CU
38.3 | CU
40.8 | CU
41 | CU
41.7 | CU
42.6 | CU
44 | CU
45.8 | CU
46.6 | CU
46.1 | CU
45.6 | CU
46 | CU
45.5 | CU
45.2 | CU
45.3 | CU
45.8 | CU
44.9 | CU
44.4 | CU
43.6 | CU
42.8 | CU
0 | CU
42.2 | CU
41.2 | CU
40.1 | CU
0 | CU
37.8 | CU
36.9 | CU
35 | CU
33.7 | CU
33.5 | CU
32.2 | CU
31.9 | CU
32.6 | CU
34.9 | CU
35.6 | CU
35.9 | CU
36 | CU
36.8 | CU
36.7 | CU
36.5 | CU
36.8 | CU
37.5 | CU
37.1 | CU
37.4 | CU
37.4 | CU
37.9 | CU
37.6 | CU
37.4 | CU
37.9 | CU
38.4 | CU
39.3 | CU
40.4 | CU
42.2 | CU
43.4 | CU
43.7 | CU
44.7 | CU
45 | CU
45.4 | CU
45.2 | CU
45.2 | CU
45.3 | CU
45.4 | CU
45.4 | CU
45.6 | CU
44.9 | CU
44 | CU
42.3 | CU
41.9 | CU
40.3 | CU
39.4 | CU
37.7 | CU
36.7 | CU
36.7 | CU
34.1 | CU
33.5 | CU
33.3 | CU
32.9 | CU
32.4 | CU
33 | CU
34.8 | CU
35.6 | CU
36.1 | CU
36.3 | CU
36.3 | CU
36.7 | CU
36.7 | CU
36.7 | CU
36.7 | CU
36.9 | CU
36.5 | CU
35.7 | CU
36 | CU
36.6 | CU
36.9 | CU
37.2 | CU
37.6 | CU
37.6 | CU
38.4 | CU
38.8 | CU
39.6 | CU
41.5 | CU
41.9 | CU
44.8 | CU
43.8 | CU
42.5 | CU
42 | CU
41.5 | CU
41.1 | CU
40 | CU
41.1 | CU
45.2 | CU
45.4 | CU
45.1 | CU
44.9 | CU
1.1 | CU
40.9 | CU
38.9 | CU
37.3 | CU
35 | CU
34.9 | CU
34.2 | CU
33.7 | CU
34.3 | CU
33.4 | CU
33.9 | CU
35.2 | CU
35.5 | CU
35.1 | CU
36.6 | CU
37.1 | CU
37.7 | CU
38 | CU
38.7 | CU
38.2 | CU
37.3 | CU
38.4 | CU
38 | CU
37 | CU
39.1 | CU
38.6 | CU
38.9 | CU
39.7 | CU
41.1 | CU
41.8 | CU
43.2 | CU
45.6 | CU
45.6 | CU
44.7 | CU
45.2 | CU
45.6 | CU
45.9 | CU
46.2 | CU
45.8 | CU
45.9 | CU
45.4 | CU
45.8 | CU
45.1 | CU
43.5 | CU
43.3 | CU
41.4 | CU
41.5 | CU
39.5 | CU
38.6 | CU
38 | CU
36.5 | CU
36.2 | CU
35.1 | CU
34.3 | CU
33.9 | CU
34 | CU
34.7 | CU
37.5 | CU
37.8 | CU
38.1 | CU
37.8 | CU
38.1 | CU
38.4 | CU
38.4 | CU
38.6 | CU
39.2 | CU
39 | CU
39.2 | CU
39 | CU
38.5 | CU
38.8 | CU
38.5 | CU
39.5 | CU
39.5 | CU
41.5 | CU
42.3 | CU
43 | CU
43.5 | CU
44.8 | CU
46.7 | CU
48 | CU
47.7 | CU
45.3 | CU
45.5 | CU
44.8 | CU
47.3 | CU
48.4 | CU
46.6 | CU
48 | CU
45.6 | CU
43.1 | CU
42.5 | CU
41.2 | CU
40.3 | CU
39.4 | CU
37.5 | CU
34.7 | CU
32.6 | CU
31.4 | CU
31.1 | CU
31.1 | CU
32.5 | CU
33.1 | CU
34 | CU
34.3 | CU
33.9 | CU
34.4 | CU
34.5 | CU
34.4 | CU
35 | CU
35.4 | CU
35.1 | CU
35.1 | CU
35.4 | CU
35.7 | CU
35.7 | CU
35.6 | CU
35.2 | CU
35.9 | CU
36.2 | CU
35.6 | CU
36.2 | CU
39.4 | CU
41.9 | CU
43.8 | CU
43.2 | CU
42.4 | CU
42.4 | CU
46.6 | CU
41.7 | CU
41.2 | CU
42 | CU
43.9 | CU
45.3 | CU
39.3 | CU
42.5 | CU
38 | CU
41.4 | CU
40.6 | CU
38.7 | CU
36.9 | CU
34.9 | CU
33.4 | CU
32.4 | CU
31.5 | CU
31.2 | CU
32.6 | CU
32 | CU
32.7 | CU
33.7 | CU
34.3 | CU
35.5 | CU
35.3 | CU
35.1 | CU
35.5 | CU
35.2 | CU
35.4 | CU
35.2 | CU
36.1 | CU
35.4 | CU
35.1 | CU
35.2 | CU
35 | CU
34.7 | CU
34.3 | CU
35 | CU
34.7 | CU
36.3 | CU
37.1 | CU
37.7 | CU
38.8 | CU
41.4 | CU
45 | CU
43.6 | CU
45.1 | CU
44.4 | CU
41.7 | CU
42.1 | CU
39.2 | CU
39 | CU
35.3 | CU
43.7 | CU
38.9 | CU
36.7 | CU
39.4 | CU
36.7 | CU
35.1 | CU
36.2 | CU
32.5 | CU
33.7 | CU
30.3 | CU
32 | CU
33.9 | CU
33.2 | CU
32.9 | CU
33.7 | CU
35 | CU
34.7 | CU
34.8 | CU
35.1 | CU
34.5 | CU
34.7 | CU
34.8 | CU
35.8 | CU
35.1 | CU
34.6 | CU
34.9 | CU
34.5 | CU
34.2 | CU
34.7 | CU
34.5 | CU
34.6 | CU
34.5 | CU
35.4 | CU
35.8 | CU
36 | CU
35.1 | CU
36 | CU
38.5 | CU
39.5 | CU
43.3 | CU
42.1 | CU
49.5 | CU
48.7 | CU
48.3 | CU
48.4 | CU
44.8 | CU
44 | CU
43.7 | CU
41.6 | CU
41.4 | CU
40.1 | CU
39.8 | CU
37.6 | CU
36.6 | CU
34.1 | CU
32.5 | CU
34.5 | CU
36.2 | CU
35.4 | CU
35.8 | CU
36.5 | CU
37.6 | CU
37.4 | CU
37.7 | CU
37.9 | CU
37.7 | CU
38.6 | CU
38.4 | CU
38.4 | CU
38.1 | CU
38 | CU
38.2 | CU
38.4 | CU
37.8 | CU
37.7 | CU
37 | CU
36.9 | CU
36.8 | CU
39 | CU
37.9 | CU
40.2 | CU
41.2 | CU
45.1 | CU
45.5 | CU
45.4 | CU
45.9 | CU
47.5 | CU
46.7 | CU
48.8 | CU
45.3 | CU
45.9 | CU
44.1 | CU
44.8 | CU
43.1 | CU
42.4 | CU
40.7 | CU
39.3 | CU
38.9 | CU
38.5 | CU
36.9 | CU
35.7 | CU
34.3 | CU
32.8 | CU
32.3 | CU
32.6 | CU
32.9 | CU
34.8 | CU
35.8 | CU
36 | CU
36.5 | CU
36.3 | CU
36.7 | CU
36.3 | CU
37 | CU
37 | CU
37.9 | CU
37.7 | CU
38.9 | CU
37.4 | CU
37.8 | CU
38.9 | CU
38.6 | CU
38.6 | CU
39.3 | CU
40.1 | CU
41.2 | CU
40.1 | CU
42.5 | CU
43.2 | CU
43.2 | CU
43.5 | CU
46.7 | CU
47.8 | CU
45.3 | CU
49 | CU
47.4 | CU
47 | CU
45.1 | CU
44.6 | CU
43.3 | CU
43.1 | CU
42.4 | CU
42.9 | CU
49.6 | CU
0.7 | CU
0.6 | CU
33.9 | CU
33.8 | CU
32.9 | CU
32.3 | CU
32.2 | CU
33.3 | CU
34.8 | CU
35.2 | CU
35.3 | CU
36.5 | CU
36.7 | CU
36.9 | CU
37.2 | CU
36.9 | CU
36.9 | CU
37.4 | CU
38.1 | CU
38.2 | CU
38.1 | CU
37.2 | CU
37.3 | CU
37.6 | CU
37.6 | CU
38.4 | CU
38.9 | CU
39.3 | CU
39.7 | CU
39.8 | CU
41.8 | CU
42.6 | CU
44.5 | CU
45.4 | CU
45.6 | CU
46.7 | CU
45.1 | CU
43 | CU
47.5 | CU
43.9 | CU
46 | CU
44 | CU
41.9 | CU
38.4 | CU
39.9 | CU
38.6 | CU
36.6 | CU
35.1 | CU
34.1 | CU
33.1 | CU
32.5 | CU
32.1 | CU
32.1 | CU
33 | CU
34.6 | CU
35.6 | CU
36.2 | CU
36.5 | CU
36.6 | CU
36.6 | CU
36.9 | CU
37.1 | CU
37.5 | CU
37.4 | CU
38.1 | CU
37.3 | CU
37.4 | CU
37.5 | CU
37.2 | CU
37.7 | CU
37.7 | CU
37.8 | CU
38.7 | CU
39.9 | CU
40.2 | CU
41.1 | CU
42.2 | CU
44.2 | CU
44.6 | CU
41.8 | CU
44.6 | CU
46.5 | CU
44.4 | CU
44.8 | CU
43.6 | CU
43.4 | CU
43.7 | CU
43 | CU
42.2 | CU
42.5 | CU
42 | CU
39.5 | CU
36.9 | CU
37 | CU
35.2 | CU
33.9 | CU
33.1 | CU
32.4 | CU
32.5 | CU
33.3 | CU
35.4 | CU
36.3 | CU
36.5 | CU
36.4 | CU
36.8 | CU
37.3 | CU
38.2 | CU
38.6 | CU
38.6 | CU
39 | CU
39.7 | CU
39.5 | CU
39.4 | CU
38.6 | CU
38.6 | CU
39.2 | CU
39.2 | CU
39.7 | CU
39.9 | CU
40.5 | CU
42.4 | CU
43.2 | CU
44.8 | CU
46.1 | CU
45.8 | CU
46.1 | CU
46.4 | CU
45.7 | CU
46.9 | CU
46.2 | CU
46.3 | CU
47.6 | CU
45.6 | CU
45.4 | CU
44.4 | CU
44.2 | CU
43.3 | CU
42.1 | CU
40.9 | CU
40.5 | CU
37.2 | CU
34.3 | CU
33.6 | CU
33.5 | CU
32.9 | CU
34.4 | CU
35.7 | CU
36.6 | CU
36.2 | CU
37.1 | CU
37 | CU
37.2 | CU
37.8 | CU
37.8 | CU
37.5 | CU
38.9 | CU
38.5 | CU
38.2 | CU
37.5 | CU
37.5 | CU
37.2 | CU
37.9 | CU
38 | CU
39.3 | CU
39.4 | CU
40.8 | CU
40.6 | CU
42 | CU
43.7 | CU
45.7 | CU
46.5 | CU
46.1 | CU
47 | CU
47 | CU
47 | CU
46.9 | CU
46.7 | CU
46.4 | CU
45.3 | CU
44.4 | CU
44.3 | CU
42.1 | CU
42 | CU
40.8 | CU
38.9 | CU
38.1 | CU
36.7 | CU
35.4 | CU
34.7 | CU
31.8 | CU
31.5 | CU
31.9 | CU
32.7 | CU
33.5 | CU
34.4 | CU
34.8 | CU
35.4 | CU
35.2 | CU
35.6 | CU
35.6 | CU
35.1 | CU
35.2 | CU
35 | CU
34.6 | CU
36.4 | CU
36.2 | CU
36.1 | CU
37 | CU
37.1 | CU
36.7 | CU
38.5 | CU
38.6 | CU
41.2 | CU
42.6 | CU
44.4 | CU
44.4 | CU
44.3 | CU
45 | CU
45.5 | CU
45.5 | CU
44 | CU
45.5 | CU
44.3 | CU
43.9 | CU
44.7 | CU
44 | CU
42.8 | CU
42.2 | CU
41.2 | CU
39.1 | CU
37.5 | CU
37.2 | CU
35.4 | CU
34.8 | CU
33.2 | CU
31.7 | CU
31.7 | CU
31.2 | CU
31.8 | CU
34.8 | CU
34.5 | CU
35.5 | CU
35.7 | CU
35.6 | CU
36.3 | CU
36.8 | CU
37.2 | CU
36.5 | CU
36.5 | CU
36.2 | CU
37 | CU
36.4 | CU
36.1 | CU
36.8 | CU
35.8 | CU
36.2 | CU
37.9 | CU
39.4 | CU
40.2 | CU
41 | CU
42.3 | CU
43.2 | CU
43.4 | CU
44.1 | CU
44.3 | CU
43.5 | CU
41 | CU
45.3 | CU
42.2 | CU
43.1 | CU
43 | CU
41.4 | CU
41.6 | CU
40.2 | CU
38.2 | CU
40.7 | CU
41.2 | CU
37.8 | CU
36.5 | CU
35.5 | CU
34.4 | CU
33 | CU
32.7 | CU
32.1 | CU
32.7 | CU
32.8 | CU
34.5 | CU
35.5 | CU
35.6 | CU
36.3 | CU
36.6 | CU
36.6 | CU
36.4 | CU
36.1 | CU
36.5 | CU
37.2 | CU
36.6 | CU
36.8 | CU
37 | CU
36.8 | CU
37.1 | CU
37.6 | CU
38.9 | CU
39.7 | CU
40.7 | CU
42.3 | CU
44.9 | CU
45.9 | CU
46 | CU
46.9 | CU
45.5 | CU
44.5 | CU
48.9 | CU
46.3 | CU
46.5 | CU
45.8 | CU
47.3 | CU
45.8 | CU
45.5 | CU
43.8 | CU
42 | CU
41.1 | CU
38.7 | CU
38 | CU
37 | CU
36 | CU
33.8 | CU
31.3 | CU
31.7 | CU
32.1 | CU
32.1 | CU
32.2 | CU
32.6 | CU
33.8 | CU
35.2 | CU
34.9 | CU
35.1 | CU
35.7 | CU
35.4 | CU
35.3 | CU
35.6 | CU
35.5 | CU
35.8 | CU
36.1 | CU
36.8 | CU
36.3 | CU
36.2 | CU
35.8 | CU
36.3 | CU
37.1 | CU
37.5 | CU
39.2 | CU
39.9 | CU
40.7 | CU
40.8 | CU
40.6 | CU
43.3 | CU
40.9 | CU
39.8 | CU
41.8 | CU
42.2 | CU
40.7 | CU
40.8 | CU
37.8 | CU
38.8 | CU
39.2 | CU
38.7 | CU
38.5 | CU
38.2 | CU
37 | CU
0 | CU
34.7 | CU
34.3 | CU
32.7 | CU
32.7 | CU
32.5 | CU
32.2 | CU
32.8 | CU
34.5 | CU
35.2 | CU
35.5 | CU
35.7 | CU
35.9 | CU
36.6 | CU
36.2 | CU
36.4 | CU
36.5 | CU
35.4 | CU
36.6 | CU
36.1 | CU
35.6 | CU
34.2 | CU
35.3 | CU
35.4 | CU
36.4 | CU
37.4 | CU
37.2 | CU
39.2 | CU
39.5 | CU
40.8 | CU
42.2 | CU
43.7 | CU
41 | CU
44.7 | CU
41.9 | CU
41.6 | CU
41.5 | CU
38.6 | CU
39.7 | CU
41.6 | CU
49.6 | CU
46.9 | CU
43.6 | CU
42.4 | CU
42.2 | CU
40.6 | CU
39.5 | CU
38.4 | CU
37.8 | CU
37.4 | CU
36.4 | CU
36.4 | CU
35.5 | CU
36.9 | CU
38.6 | CU
39.2 | CU
39.6 | CU
39.8 | CU
40.2 | CU
41 | CU
41.3 | CU
41.4 | CU
41.2 | CU
41 | CU
40.8 | CU
40.7 | CU
40.9 | CU
40.4 | CU
40 | CU
40.8 | CU
41 | CU
41.1 | CU
42.7 | CU
44.1 | CU
44.7 | CU
45.9 | CU
46.5 | CU
46.3 | CU
45 | CU
48.8 | CU
48.3 | CU
48.7 | CU
50.4 | CU
48.8 | CU
46.1 | CU
45.2 | CU
47.5 | CU
45.7 | CU
44.6 | CU
43.3 | CU
41.7 | CU
41 | CU
39.5 | CU
39 | CU
36.9 | CU
36.3 | CU
34.8 | CU
35.6 | CU
35.4 | CU
36.3 | CU
37.8 | CU
39 | CU
38.7 | CU
39.6 | CU
39.6 | CU
39.5 | CU
39.3 | CU
39.7 | CU
40.2 | CU
39.8 | CU
40.5 | CU
40.1 | CU
39.6 | CU
39.5 | CU
40.1 | CU
40.7 | CU
41.4 | CU
42.2 | CU
42.7 | CU
43.6 | CU
44.7 | CU
45.6 | CU
46.3 | CU
46.9 | CU
46 | CU
47.1 | CU
48.8 | CU
48.8 | CU
49.7 | CU
48.6 | CU
46.4 | CU
46.1 | CU
46.2 | CU
45.7 | CU
44.4 | CU
44.1 | CU
42.5 | CU
41.3 | CU
40 | CU
38.5 | CU
36.7 | CU
35.7 | CU
35.8 | CU
35 | CU
34.5 | CU
36.4 | CU
37.3 | CU
38.3 | CU
38.3 | CU
39 | CU
38.8 | CU
38.6 | CU
38.6 | CU
38.4 | CU
38.5 | CU
40 | CU
40 | CU
40.5 | CU
40.2 | CU
39.5 | CU
39.4 | CU
39.4 | CU
40.5 | CU
42.3 | CU
42.9 | CU
44.2 | CU
45.2 | CU
46.7 | CU
47 | CU
46.4 | CU
47.4 | CU
47.4 | CU
47.2 | CU
47.8 | CU
47.5 | CU
48.1 | CU
47.2 | CU
46.8 | CU
46 | CU
45 | CU
43.9 | CU
43.1 | CU
42.4 | CU
41.3 | CU
38.8 | CU
37.2 | CU
36.5 | CU
34 | CU
33.2 | CU
33.5 | CU
33.7 | CU
34.1 | CU
36.2 | CU
36.3 | CU
37 | CU
36.7 | CU
37.1 | CU
37.1 | CU
37.8 | CU
38.2 | CU
37.7 | CU
38.5 | CU
38.7 | CU
37.8 | CU
37.6 | CU
37.3 | CU
38 | CU
38.4 | CU
38.8 | CU
38.8 | CU
39.7 | CU
42.9 | CU
45.6 | CU
46 | CU
45.6 | CU
46 | CU
46.3 | CU
46.4 | CU
45.7 | CU
46.4 | CU
46.5 | CU
45.9 | CU
45.7 | CU
45.4 | CU
45.1 | CU
44.3 | CU
44.4 | CU
43 | CU
42.4 | CU
40.1 | CU
38.8 | CU
38.2 | CU
36.3 | CU
35.4 | CU
33.6 | CU
33.1 | CU
33.1 | CU
33.7 | CU
36.8 | CU
37.7 | CU
37.7 | CU
38.4 | CU
38.4 | CU
39 | CU
39.6 | CU
40.3 | CU
40.6 | CU
40.2 | CU
39.8 | CU
40.2 | CU
40 | CU
39.5 | CU
39.2 | CU
39.6 | CU
38.9 | CU
39.8 | CU
39.9 | CU
41.1 | CU
41 | CU
42.4 | CU
44.8 | CU
45.4 | CU
46.2 | CU
46.6 | CU
47.2 | CU
46.7 | CU
47 | CU
46.9 | CU
46 | CU
46.5 | CU
46.4 | CU
46.4 | CU
43.4 | CU
43 | CU
41.2 | CU
40.5 | CU
39.6 | CU
38.1 | CU
37.3 | CU
36.6 | CU
35.1 | CU
34.3 | CU
35.2 | CU
36.5 | CU
37.1 | CU
37.3 | CU
36.9 | CU
37.6 | CU
38.8 | CU
39 | CU
39.5 | CU
40.1 | CU
40.6 | CU
40.5 | CU
40.5 | CU
40.4 | CU
39.5 | CU
40.5 | CU
40.3 | CU
39.9 | CU
40.1 | CU
40.9 | CU
41.1 | CU
42 | CU
42 | CU
43.9 | CU
44.9 | CU
45.5 | CU
44.2 | CU
45.7 | CU
46.8 | CU
44.3 | CU
47.8 | CU
47.3 | CU
47.1 | CU
46.4 | CU
44.3 | CU
45.5 | CU
43.5 | CU
41.5 | CU
40.7 | CU
41.1 | CU
38.3 | CU
37.6 | CU
37.7 | CU
35.4 | CU
34.5 | CU
35 | CU
34.2 | CU
36.2 | CU
36.7 | CU
38.6 | CU
38.5 | CU
39 | CU
39.2 | CU
39.1 | CU
38.9 | CU
38.4 | CU
39.1 | CU
39.4 | CU
39.1 | CU
38.9 | CU
39.3 | CU
39.4 | CU
39.1 | CU
39.8 | CU
39.7 | CU
41.1 | CU
41.9 | CU
42.8 | CU
42.7 | CU
43.8 | CU
45.8 | CU
46.5 | CU
46.2 | CU
46.4 | CU
46.7 | CU
46.3 | CU
46.6 | CU
45.8 | CU
46.1 | CU
45.2 | CU
45.1 | CU
44.4 | CU
43.7 | CU
43.6 | CU
41.4 | CU
39.2 | CU
38.5 | CU
37.3 | CU
36.2 | CU
35.4 | CU
33.9 | CU
32.7 | CU
33.3 | CU
34.4 | CU
37 | CU
37 | CU
36.9 | CU
37.6 | CU
37.3 | CU
37.8 | CU
37.5 | CU
37.7 | CU
38.1 | CU
38.5 | CU
38.9 | CU
39.3 | CU
39.7 | CU
39.4 | CU
39.5 | CU
39.7 | CU
39.5 | CU
39.7 | CU
40.3 | CU
41.3 | CU
41.6 | CU
42.5 | CU
44.3 | CU
45.4 | CU
45.8 | CU
45.9 | CU
46.8 | CU
45.2 | CU
46 | CU
45.5 | CU
45.7 | CU
44.9 | CU
44 | CU
43.6 | CU
42.5 | CU
42 | CU
38.8 | CU
38.1 | CU
37.1 | CU
35.8 | CU
35.2 | CU
35.3 | CU
36.1 | CU
35.5 | CU
36.2 | CU
36.9 | CU
37.2 | CU
37.5 | CU
37.8 | CU
37.7 | CU
38.8 | CU
39.1 | CU
39.4 | CU
39.9 | CU
39.7 | CU
39.6 | CU
39.4 | CU
39.3 | CU
39.3 | CU
39.6 | CU
39.6 | CU
39.8 | CU
40.2 | CU
40.4 | CU
41 | CU
41 | CU
41.9 | CU
42.3 | CU
43.4 | CU
44.3 | CU
45.1 | CU
44.9 | CU
45.7 | CU
46 | CU
48 | CU
46.5 | CU
46.8 | CU
45.8 | CU
46.8 | CU
46.6 | CU
45.8 | CU
44.3 | CU
42.9 | CU
42 | CU
40.5 | CU
38.9 | CU
38.1 | CU
37.4 | CU
36.4 | CU
36.2 | CU
35.5 | CU
36.5 | CU
38.8 | CU
39.1 | CU
39.2 | CU
38.9 | CU
39.2 | CU
39.6 | CU
39.8 | CU
40.1 | CU
40.4 | CU
40.5 | CU
40.5 | CU
39.6 | CU
40.4 | CU
40.1 | CU
40.3 | CU
39.3 | CU
40.9 | CU
40.9 | CU
41.1 | CU
41.1 | CU
42.5 | CU
43.2 | CU
43.8 | CU
44.5 | CU
45.9 | CU
46 | CU
45.6 | CU
45.3 | CU
46.3 | CU
47.4 | CU
47.3 | CU
47.6 | CU
45 | CU
45.1 | CU
45 | CU
44.8 | CU
43.4 | CU
41.1 | CU
40.3 | CU
39.1 | CU
36.1 | CU
34.4 | CU
33.1 | CU
33.6 | CU
32.3 | CU
34.3 | CU
36.6 | CU
36.7 | CU
37.3 | CU
37.6 | CU
37.6 | CU
37.9 | CU
38.7 | CU
39.1 | CU
38.9 | CU
39.6 | CU
38.9 | CU
39.5 | CU
40.2 | CU
40.1 | CU
39.9 | CU
40.4 | CU
39.9 | CU
39.8 | CU
40 | CU
40.8 | CU
42.1 | CU
43.7 | CU
45.6 | CU
46 | CU
45.2 | CU
46.3 | CU
45.4 | CU
45.8 | CU
44.6 | CU
45.9 | CU
45.9 | CU
45.9 | CU
45.9 | CU
45.3 | CU
45.3 | CU
44.9 | CU
43.8 | CU
42.8 | CU
40.7 | CU
39.6 | CU
36.3 | CU
35.1 | CU
34.2 | CU
34.7 | CU
34.7 | CU
34.9 | CU
36.6 | CU
37 | CU
37.4 | CU
37.8 | CU
37.5 | CU
38.6 | CU
38.6 | CU
39.7 | CU
39.5 | CU
39.4 | CU
40.2 | CU
40.6 | CU
40.6 | CU
41.1 | CU
40.7 | CU
40.9 | CU
40.6 | CU
40.8 | CU
40.7 | CU
41.6 | CU
42.2 | CU
42.5 | CU
44.5 | CU
45.4 | CU
46.5 | CU
46.2 | CU
48 | CU
46.7 | CU
46.9 | CU
47.2 | CU
47.1 | CU
48.2 | CU
47.2 | CU
46.8 | CU
48.1 | CU
49 | CU
52.7 | CU
47.4 | CU
46 | CU
45.2 | CU
43.7 | CU
42.4 | CU
42 | CU
41.1 | CU
38.6 | CU
38.3 | CU
38.9 | CU
40.4 | CU
41.3 | CU
41.4 | CU
41.6 | CU
41.9 | CU
42 | CU
41.6 | CU
42 | CU
42.4 | CU
41.9 | CU
43 | CU
43.8 | CU
44.2 | CU
43.1 | CU
43.6 | CU
43.2 | CU
43.4 | CU
43.4 | CU
44.1 | CU
45.5 | CU
46.2 | CU
47.7 | CU
48.7 | CU
50 | CU
50.3 | CU
49.1 | CU
49.7 | CU
49.2 | CU
49.8 | CU
50.1 | CU
49.5 | CU
49.1 | CU
49.8 | CU
50 | CU
52.6 | CU
47.8 | CU
47.7 | CU
45.9 | CU
44.9 | CU
43.4 | CU
41.7 | CU
39.7 | CU
38.1 | CU
42.2 | CU
36.6 | CU
41.6 | CU
39.8 | CU
42.3 | CU
42.5 | CU
42.6 | CU
43 | CU
43.4 | CU
44 | CU
43.6 | CU
43.6 | CU
43.7 | CU
44.1 | CU
44.5 | CU
44.6 | CU
45.3 | CU
45.8 | CU
45.6 | CU
45.2 | CU
46.1 | CU
46.5 | CU
47.3 | CU
48.3 | CU
49.2 | CU
50.5 | CU
51.1 | CU
51.4 | CU
51.4 | CU
51.6 | CU
51.6 | CU
53.6 | CU
51.4 | CU
51.1 | CU
51.1 | CU
51 | CU
50.8 | CU
50.3 | CU
50.5 | CU
50 | CU
48.8 | CU
48.1 | CU
47.7 | CU
47.1 | CU
47 | CU
47 | CU
47.6 | CU
46.5 | CU
49.9 | CU
56.9 | CU
55.2 | CU
55.2 | CU
55.1 | CU
55.2 | CU
55 | CU
55.1 | CU
55.2 | CU
54.9 | CU
55 | CU
55.1 | CU
55 | CU
55.2 | CU
55 | CU
55.1 | CU
54.9 | CU
55.1 | CU
55.1 | CU
54.9 | CU
55 | CU
54.7 | CU
54.5 | CU
54.4 | CU
54.4 | CU
54 | CU
54.4 | CU
54.1 | CU
54.8 | CU
54.5 | CU
55.1 | CU
54.2 | CU
55 | CU
54.4 | CU
55.3 | CU
54.7 | CU
55.2 | CU
55 | CU
55.1 | CU
54.9 | CU
55 | CU
55.3 | CU
55.4 | CU
55.4 | CU
55.5 | CU
55.3 | CU
55.2 | CU
55.4 | CU
55.1 | CU
55.3 | CU
55.2 | CU
55.1 | CU
55.1 | CU
55.1 | CU
55.2 | CU
55 | CU
54.9 | CU
55 | CU
55 | CU
55 | CU
55 | CU
55 | CU
54.8 | CU
54.9 | CU
54.9 | CU
55 | CU
54.9 | CU
54.8 | CU
54.5 | CU
54.7 | CU
54.4 | CU
54.3 | CU
54.5 | CU
54.4 | CU
54.3 | CU
52.7 | CU
52.9 | CU
50.6 | CU
50.7 | CU
50.5 | CU
52.8 | CU
49.4 | CU
50.5 | CU
45.5 | CU
45.2 | CU
45.2 | CU
44.8 | CU
47.7 | CU
1.1 | CU
0.2 | CU
36.5 | CU
35.4 | CU
35.7 | CU
36.3 | CU
37.9 | CU
39.5 | CU
39.9 | CU
40.6 | CU
40.6 | CU
40.5 | CU
41.5 | CU
41.7 | CU
42.4 | CU
42.6 | CU
42.7 | CU
42.2 | CU
42.1 | CU
42.4 | CU
43.4 | CU
43.5 | CU
44.3 | CU
45.1 | CU
45.6 | CU
46.3 | CU
47.5 | CU
48.6 | CU
49.5 | CU
50.9 | CU
54.8 | CU
54.1 | CU
51.3 | CU
51.2 | CU
52.4 | CU
49.8 | CU
50.5 | CU
50.2 | CU
48.6 | CU
48.6 | CU
50.9 | CU
43.9 | CU
43.7 | CU
41.7 | CU
40.6 | CU
41.8 | CU
40 | CU
39.3 | CU
39 | CU
41.3 | CU
38.5 | CU
38.8 | CU
40 | CU
41.3 | CU
41.6 | CU
41.5 | CU
42.2 | CU
42.5 | CU
43 | CU
43 | CU
43.1 | CU
43.2 | CU
43.1 | CU
42.5 | CU
42.6 | CU
43.1 | CU
43.5 | CU
43.7 | CU
44 | CU
45.2 | CU
45 | CU
45.7 | CU
46.3 | CU
47 | CU
48 | CU
47.9 | CU
48.8 | CU
49.3 | CU
49.9 | CU
49.4 | CU
49.4 | CU
49.2 | CU
48.8 | CU
49.3 | CU
49 | CU
48.7 | CU
48.2 | CU
46.6 | CU
45.6 | CU
44.9 | CU
43.2 | CU
42.6 | CU
42.4 | CU
40.8 | CU
38.6 | CU
37.3 | CU
37.3 | CU
37.8 | CU
40.3 | CU
41.7 | CU
42.1 | CU
41.5 | CU
42.2 | CU
42.5 | CU
42.6 | CU
43.4 | CU
43.3 | CU
43.4 | CU
43 | CU
42.6 | CU
43.9 | CU
44.4 | CU
44.3 | CU
44.4 | CU
45.5 | CU
45.3 | CU
46.3 | CU
47.3 | CU
48.3 | CU
48.8 | CU
48.9 | CU
48.9 | CU
49.7 | CU
49 | CU
49.7 | CU
50.1 | CU
49.9 | CU
50.6 | CU
50.1 | CU
50.4 | CU
49.7 | CU
49.6 | CU
48.6 | CU
48.7 | CU
47.8 | CU
46.4 | CU
44.6 | CU
43 | CU
41.2 | CU
40.3 | CU
39.4 | CU
38.1 | CU
37.4 | CU
37.9 | CU
39.8 | CU
41.7 | CU
42.1 | CU
42.5 | CU
42.5 | CU
42.5 | CU
42.1 | CU
42.4 | CU
42.9 | CU
44.3 | CU
43.4 | CU
43.4 | CU
44 | CU
43.5 | CU
43.3 | CU
43.6 | CU
43.4 | CU
43.2 | CU
44.2 | CU
45 | CU
45.9 | CU
47.5 | CU
48.1 | CU
47.6 | CU
48.4 | CU
48 | CU
47.7 | CU
47 | CU
47.5 | CU
49.1 | CU
48.2 | CU
48 | CU
49.5 | CU
48.9 | CU
47.4 | CU
46.9 | CU
44 | CU
43.2 | CU
43.5 | CU
40.8 | CU
42.1 | CU
41 | CU
39 | CU
40.7 | CU
37 | CU
38 | CU
40.1 | CU
41.2 | CU
40.8 | CU
41.1 | CU
41.6 | CU
42.1 | CU
42.1 | CU
42.2 | CU
43.1 | CU
43.5 | CU
42.1 | CU
42.5 | CU
41.8 | CU
41.5 | CU
41 | CU
43.1 | CU
42.2 | CU
42 | CU
42.7 | CU
43.5 | CU
44.1 | CU
46.4 | CU
47.2 | CU
47.8 | CU
48.1 | CU
48.5 | CU
48.4 | CU
48.1 | CU
48.3 | CU
48.6 | CU
47.8 | CU
47.4 | CU
47 | CU
45.9 | CU
44.4 | CU
44.9 | CU
43.6 | CU
42.2 | CU
41.4 | CU
39.3 | CU
38.1 | CU
36.8 | CU
35.5 | CU
35.7 | CU
35.1 | CU
36.4 | CU
37 | CU
38 | CU
38.6 | CU
38.5 | CU
39.4 | CU
39.6 | CU
39.8 | CU
38.9 | CU
39.3 | CU
38.7 | CU
40.2 | CU
41.8 | CU
41.9 | CU
41.6 | CU
41.6 | CU
40.9 | CU
40.7 | CU
41.6 | CU
42.8 | CU
42.6 | CU
43.2 | CU
45.5 | CU
46.7 | CU
47.6 | CU
46.7 | CU
47.8 | CU
47.2 | CU
47.9 | CU
48.3 | CU
48.7 | CU
49 | CU
48.7 | CU
47.7 | CU
47 | CU
45.6 | CU
45.8 | CU
43.3 | CU
41.4 | CU
39.6 | CU
38.7 | CU
37.6 | CU
36.3 | CU
34.9 | CU
34.3 | CU
34.2 | CU
34.6 | CU
36.9 | CU
37.7 | CU
38.4 | CU
38.8 | CU
39.2 | CU
39.8 | CU
40.1 | CU
39.8 | CU
40.2 | CU
40.5 | CU
41.4 | CU
41.4 | CU
41.4 | CU
41.7 | CU
40.2 | CU
40.5 | CU
40.9 | CU
41.6 | CU
42 | CU
43 | CU
43.3 | CU
43.6 | CU
45.5 | CU
46.5 | CU
47.3 | CU
46.8 | CU
47.5 | CU
47.9 | CU
48.9 | CU
49.3 | CU
48.6 | CU
48.8 | CU
48.1 | CU
47.5 | CU
47.1 | CU
46.7 | CU
45.1 | CU
43.5 | CU
41.9 | CU
39.6 | CU
39.2 | CU
38.1 | CU
37.2 | CU
36.3 | CU
35.4 | CU
36.3 | CU
38.1 | CU
39.8 | CU
39.4 | CU
40 | CU
40.1 | CU
39.8 | CU
41.3 | CU
41.4 | CU
42.2 | CU
41.8 | CU
41.2 | CU
40.6 | CU
39.9 | CU
41.4 | CU
41.3 | CU
41.6 | CU
42.6 | CU
42.2 | CU
41.8 | CU
42.9 | CU
43.1 | CU
43.9 | CU
45.5 | CU
46.1 | CU
46.7 | CU
45.1 | CU
47.1 | CU
47.4 | CU
47.6 | CU
48.5 | CU
48.2 | CU
49.8 | CU
48.7 | CU
48.6 | CU
47.8 | CU
47.5 | CU
47.8 | CU
40.6 | CU
43 | CU
41.5 | CU
39.7 | CU
38.7 | CU
38.9 | CU
38 | CU
39.6 | CU
40.3 | CU
41.4 | CU
42.2 | CU
42.9 | CU
42.4 | CU
42.3 | CU
43.2 | CU
43.2 | CU
43.4 | CU
43.5 | CU
43.7 | CU
42.9 | CU
43.8 | CU
43.9 | CU
43.2 | CU
42.8 | CU
42.6 | CU
43.2 | CU
43 | CU
42.8 | CU
43 | CU
43.4 | CU
43.9 | CU
44 | CU
44.6 | CU
46.5 | CU
47.3 | CU
47.3 | CU
47.9 | CU
48.8 | CU
46.3 | CU
48.4 | CU
48.4 | CU
46.1 | CU
45.6 | CU
46.7 | CU
45.7 | CU
45.1 | CU
45.3 | CU
44.2 | CU
40.8 | CU
41 | CU
39.8 | CU
38.6 | CU
36.3 | CU
37.4 | CU
38.8 | CU
40.3 | CU
42.6 | CU
41.5 | CU
42.2 | CU
41.9 | CU
42.3 | CU
42.3 | CU
42.2 | CU
43.1 | CU
43.1 | CU
43.2 | CU
42.7 | CU
43.3 | CU
43.2 | CU
43.8 | CU
43.7 | CU
43.5 | CU
44 | CU
43.6 | CU
43.7 | CU
44.4 | CU
44.7 | CU
46.4 | CU
47.7 | CU
48 | CU
48.4 | CU
49.2 | CU
50.2 | CU
48.5 | CU
49.7 | CU
48.5 | CU
50.2 | CU
48.7 | CU
48.5 | CU
48 | CU
47.2 | CU
45.5 | CU
42.6 | CU
42 | CU
40.9 | CU
38.3 | CU
36.6 | CU
35.5 | CU
34.9 | CU
35.1 | CU
35.9 | CU
37.6 | CU
38.2 | CU
38.5 | CU
39.6 | CU
39.8 | CU
40.5 | CU
40.3 | CU
40.8 | CU
41.5 | CU
40.6 | CU
39.5 | CU
40.5 | CU
41 | CU
40.7 | CU
40.3 | CU
40.4 | CU
39.6 | CU
40.2 | CU
40.6 | CU
40.8 | CU
41.2 | CU
42 | CU
43.3 | CU
44.1 | CU
45.4 | CU
46.3 | CU
48.1 | CU
46 | CU
44.7 | CU
46.8 | CU
46.4 | CU
44.8 | CU
47.4 | CU
46.8 | CU
45.5 | CU
45.5 | CU
44.2 | CU
43.8 | CU
43.7 | CU
41.3 | CU
40.2 | CU
38 | CU
37.9 | CU
36.3 | CU
36.1 | CU
37.3 | CU
40 | CU
40.2 | CU
41 | CU
40.3 | CU
41.3 | CU
41 | CU
41.1 | CU
40.4 | CU
41.2 | CU
40.6 | CU
41 | CU
40.8 | CU
41.3 | CU
41 | CU
40.7 | CU
40.6 | CU
41.3 | CU
41 | CU
41.7 | CU
42 | CU
42.6 | CU
43.6 | CU
44.6 | CU
46 | CU
46.9 | CU
47.1 | CU
47.4 | CU
47.3 | CU
47.5 | CU
47.6 | CU
47.7 | CU
47.8 | CU
48.4 | CU
47.7 | CU
48.2 | CU
47.6 | CU
46.8 | CU
46.1 | CU
45.1 | CU
43.1 | CU
41.2 | CU
37.7 | CU
35.3 | CU
35.2 | CU
35.2 | CU
36.9 | CU
37.4 | CU
38.8 | CU
39.4 | CU
39.2 | CU
40.2 | CU
40 | CU
40.1 | CU
40.7 | CU
40.2 | CU
40.2 | CU
40.3 | CU
40.2 | CU
40.4 | CU
40 | CU
38.8 | CU
39.7 | CU
39.9 | CU
39.5 | CU
39.6 | CU
41.7 | CU
41.9 | CU
42.5 | CU
43.8 | CU
45.5 | CU
46.4 | CU
45.7 | CU
44.9 | CU
46.4 | CU
45.6 | CU
46.4 | CU
46.8 | CU
47.6 | CU
46.8 | CU
46.8 | CU
47.1 | CU
47.2 | CU
46.1 | CU
45.1 | CU
42.8 | CU
39.6 | CU
41.5 | CU
38.5 | CU
37 | CU
35.9 | CU
35.2 | CU
36.5 | CU
37.7 | CU
37.8 | CU
38.2 | CU
38.3 | CU
39 | CU
38.7 | CU
39.4 | CU
40.3 | CU
40.4 | CU
40.7 | CU
40.6 | CU
39.9 | CU
39.6 | CU
40.1 | CU
39.7 | CU
39.3 | CU
39.1 | CU
38.1 | CU
37.7 | CU
41.7 | CU
43.5 | CU
44.6 | CU
46.7 | CU
47.7 | CU
47.8 | CU
47 | CU
46.3 | CU
47.2 | CU
47.2 | CU
47.2 | CU
48 | CU
47.5 | CU
47.7 | CU
47.7 | CU
47.2 | CU
46.8 | CU
46.3 | CU
46.1 | CU
45.6 | CU
43.3 | CU
41.7 | CU
39.9 | CU
38.5 | CU
37.2 | CU
36.5 | CU
35.4 | CU
35.2 | CU
37 | CU
38.9 | CU
38.8 | CU
40.6 | CU
40.3 | CU
40.2 | CU
40.6 | CU
40.9 | CU
40.5 | CU
40.4 | CU
40.2 | CU
39.7 | CU
39.6 | CU
40.3 | CU
39.4 | CU
40.3 | CU
40.7 | CU
41.4 | CU
41.2 | CU
41.6 | CU
42.3 | CU
43.1 | CU
45.4 | CU
46.2 | CU
45.8 | CU
46.2 | CU
46.4 | CU
46.6 | CU
47.8 | CU
47.2 | CU
47.9 | CU
47.5 | CU
48.1 | CU
47.5 | CU
47.7 | CU
46.8 | CU
45.7 | CU
44.6 | CU
43.5 | CU
42.6 | CU
41.8 | CU
40.5 | CU
37.8 | CU
37 | CU
36.3 | CU
35.8 | CU
36.9 | CU
38.5 | CU
39.1 | CU
40 | CU
40.9 | CU
41.1 | CU
40.5 | CU
40.4 | CU
40.1 | CU
40.5 | CU
41 | CU
40.8 | CU
40.4 | CU
40.8 | CU
40.3 | CU
40.9 | CU
41.1 | CU
41 | CU
41.4 | CU
42.3 | CU
43.1 | CU
44.9 | CU
46.7 | CU
47.6 | CU
47.9 | CU
47.6 | CU
48 | CU
48.4 | CU
48.7 | CU
48.2 | CU
48.7 | CU
49 | CU
49.3 | CU
48.6 | CU
48.1 | CU
47.6 | CU
46.8 | CU
46 | CU
43.9 | CU
42 | CU
40.2 | CU
38.6 | CU
36.7 | CU
35.4 | CU
34.4 | CU
34.8 | CU
35.1 | CU
36.8 | CU
37.7 | CU
37.6 | CU
37.7 | CU
38.1 | CU
39.1 | CU
39.4 | CU
40.2 | CU
40.3 | CU
39.9 | CU
39.5 | CU
40.6 | CU
40.6 | CU
40.9 | CU
41.1 | CU
40.9 | CU
40.9 | CU
41.2 | CU
41.6 | CU
42.6 | CU
45.4 | CU
47.4 | CU
47.5 | CU
47.2 | CU
47.1 | CU
46.9 | CU
47 | CU
47.7 | CU
47.8 | CU
48 | CU
48 | CU
47.9 | CU
47.8 | CU
47.5 | CU
47.4 | CU
45.7 | CU
44.8 | CU
43.7 | CU
42.6 | CU
41 | CU
39.9 | CU
37.8 | CU
35.8 | CU
35.5 | CU
36 | CU
36.8 | CU
38 | CU
37.9 | CU
38.7 | CU
39.4 | CU
39.9 | CU
40.1 | CU
40.8 | CU
41.8 | CU
41.2 | CU
41.2 | CU
41.9 | CU
42 | CU
41.2 | CU
41.4 | CU
41.8 | CU
41.2 | CU
41.5 | CU
41.6 | CU
42.3 | CU
43.1 | CU
44.7 | CU
46.3 | CU
47.7 | CU
47.7 | CU
47.4 | CU
47.8 | CU
48.2 | CU
48.1 | CU
48.3 | CU
49.4 | CU
48.5 | CU
48.7 | CU
48.4 | CU
48.1 | CU
48 | CU
47.2 | CU
46.6 | CU
44.2 | CU
41.7 | CU
39.8 | CU
38.7 | CU
37.4 | CU
36.3 | CU
35 | CU
35.2 | CU
35.6 | CU
37.2 | CU
37.2 | CU
38 | CU
37.8 | CU
38.4 | CU
39 | CU
38.7 | CU
40 | CU
40.3 | CU
40.4 | CU
40 | CU
39.8 | CU
39.8 | CU
39.9 | CU
40.3 | CU
39.9 | CU
39.9 | CU
40.5 | CU
40.5 | CU
41.7 | CU
42.6 | CU
44.6 | CU
45.6 | CU
46.3 | CU
46.3 | CU
46.8 | CU
46.9 | CU
46.8 | CU
47.1 | CU
47 | CU
47.6 | CU
48.3 | CU
47.6 | CU
47.3 | CU
46.5 | CU
46 | CU
45.7 | CU
44.8 | CU
41.7 | CU
39.2 | CU
37.5 | CU
35.3 | CU
34.5 | CU
34.6 | CU
34.4 | CU
35.3 | CU
36.7 | CU
36.3 | CU
37.2 | CU
38.1 | CU
38.6 | CU
38.8 | CU
40.2 | CU
39.3 | CU
39.1 | CU
39 | CU
39.5 | CU
40 | CU
39.8 | CU
38.9 | CU
38.2 | CU
39.4 | CU
39.7 | CU
39.7 | CU
40.2 | CU
40.9 | CU
42.3 | CU
43.3 | CU
44.8 | CU
45.1 | CU
45.2 | CU
45.3 | CU
45.8 | CU
46.1 | CU
46.5 | CU
47.4 | CU
46.7 | CU
47 | CU
46.6 | CU
46.2 | CU
45.6 | CU
45.2 | CU
43.6 | CU
42.9 | CU
40.5 | CU
39.7 | CU
38.3 | CU
37.1 | CU
34.7 | CU
35 | CU
35.6 | CU
37.4 | CU
38.3 | CU
39.3 | CU
39.3 | CU
39 | CU
39.4 | CU
40.1 | CU
40.3 | CU
40.3 | CU
40.7 | CU
40.3 | CU
40 | CU
40.4 | CU
40.4 | CU
40.2 | CU
40 | CU
40.3 | CU
40.8 | CU
40.8 | CU
42 | CU
42.7 | CU
44.1 | CU
44.4 | CU
45.7 | CU
46 | CU
46.1 | CU
46.6 | CU
47.4 | CU
47.4 | CU
47.8 | CU
47.8 | CU
48.4 | CU
48 | CU
48.9 | CU
48.6 | CU
48.6 | CU
47.7 | CU
46.5 | CU
46.4 | CU
45.7 | CU
46.1 | CU
45.6 | CU
45.9 | CU
53.5 | CU
43.5 | CU
43.4 | CU
43.2 | CU
43.3 | CU
43.3 | CU
43 | CU
43.2 | CU
43.2 | CU
43.2 | CU
43.1 | CU
43.1 | CU
43.1 | CU
43.2 | CU
43.1 | CU
43.2 | CU
43.1 | CU
43.1 | CU
43 | CU
43 | CU
42.9 | CU
42.8 | CU
43 | CU
43 | CU
43.2 | CU
43 | CU
42.9 | CU
42.8 | CU
42.5 | CU
42.5 | CU
42.8 | CU
42.5 | CU
42.8 | CU
43.5 | CU
43.3 | CU
43.2 | CU
42.9 | CU
43.2 | CU
43.7 | CU
43.1 | CU
43.7 | CU
43.3 | CU
43.3 | CU
43.4 | CU
44.1 | CU
43.8 | CU
43.9 | CU
43.5 | CU
43.4 | CU
43.5 | CU
43.4 | CU
43.3 | CU
43.3 | CU
43.3 | CU
43.1 | CU
43.1 | CU
43.2 | CU
43.3 | CU
43.2 | CU
43.2 | CU
43.3 | CU
43.2 | CU
43.3 | CU
43.1 | CU
43.3 | CU
43.3 | CU
43.3 | CU
43 | CU
43.1 | CU
43.1 | CU
43.2 | CU
43.3 | CU
43.2 | CU
42.8 | CU
42.7 | CU
42.7 | CU
42.9 | CU
43 | CU
43.2 | CU
43.5 | CU
43.9 | CU
42.7 | CU
43.4 | CU
43 | CU
43.4 | CU
41.4 | CU
39.4 | CU
39 | CU
36.8 | CU
34.4 | CU
33.7 | CU
33.1 | CU
32.4 | CU
32.1 | CU
32.2 | CU
33.3 | CU
34.3 | CU
34.7 | CU
34.7 | CU
35.2 | CU
35 | CU
36.4 | CU
37.2 | CU
36.9 | CU
36.8 | CU
36.9 | CU
36.1 | CU
36 | CU
36.7 | CU
36.2 | CU
36.2 | CU
36 | CU
37 | CU
37.4 | CU
37.7 | CU
38.5 | CU
38.6 | CU
39 | CU
40.4 | CU
41.7 | CU
42.4 | CU
41.7 | CU
45 | CU
42.4 | CU
43.8 | CU
46.4 | CU
43.6 | CU
46.4 | CU
45.7 | CU
45.3 | CU
44.9 | CU
45.9 | CU
50.2 | CU
43.6 | CU
42.3 | CU
39.7 | CU
30.4 | CU
35.7 | CU
34.8 | CU
34.4 | CU
34.7 | CU
35.9 | CU
37.6 | CU
37.8 | CU
38.2 | CU
38.7 | CU
38.5 | CU
39.2 | CU
39.4 | CU
39.6 | CU
39.6 | CU
40 | CU
39.6 | CU
39 | CU
38.9 | CU
39 | CU
38.7 | CU
38.4 | CU
38.7 | CU
38 | CU
38.4 | CU
38.4 | CU
39.8 | CU
41 | CU
42.5 | CU
41.5 | CU
41.7 | CU
43.5 | CU
45.8 | CU
46.9 | CU
46.9 | CU
42.9 | CU
48.3 | CU
46.3 | CU
46.6 | CU
47.3 | CU
43.8 | CU
42.9 | CU
41.2 | CU
39.8 | CU
37.6 | CU
38.3 | CU
37.2 | CU
37 | CU
35.6 | CU
33.8 | CU
34.9 | CU
35.2 | CU
36.9 | CU
37 | CU
37.9 | CU
37.7 | CU
38.5 | CU
38.1 | CU
39.2 | CU
38.8 | CU
39.3 | CU
39 | CU
38.4 | CU
38.3 | CU
38.4 | CU
38.4 | CU
37.9 | CU
38.5 | CU
38.4 | CU
39.2 | CU
39.1 | CU
39.3 | CU
39.7 | CU
40.6 | CU
41.2 | CU
42.5 | CU
43.3 | CU
42.3 | CU
42.8 | CU
43.9 | CU
42.5 | CU
43.5 | CU
45 | CU
45.2 | CU
44.2 | CU
42.5 | CU
42.5 | CU
42.2 | CU
40.6 | CU
38.8 | CU
36.4 | CU
36 | CU
35.6 | CU
36.2 | CU
36.6 | CU
36.1 | CU
35.8 | CU
36.4 | CU
37 | CU
37 | CU
38 | CU
38.1 | CU
39 | CU
38.8 | CU
38.6 | CU
38.9 | CU
38.6 | CU
38.8 | CU
38.7 | CU
39.2 | CU
38.6 | CU
38.7 | CU
38.2 | CU
38.5 | CU
38.3 | CU
38.5 | CU
38.7 | CU
38.6 | CU
38.6 | CU
40 | CU
40.3 | CU
41.2 | CU
42.9 | CU
43.4 | CU
43.8 | CU
43.6 | CU
43.9 | CU
43.9 | CU
44 | CU
44.5 | CU
43.6 | CU
43.5 | CU
43.5 | CU
41 | CU
38.9 | CU
36.7 | CU
38.2 | CU
38.3 | CU
38 | CU
37.3 | CU
38 | CU
36.8 | CU
36.9 | CU
37.3 | CU
38 | CU
38.3 | CU
38.7 | CU
39.4 | CU
39.9 | CU
39.8 | CU
39.4 | CU
40.2 | CU
39.8 | CU
40.2 | CU
40.1 | CU
40 | CU
39.2 | CU
39.2 | CU
39.6 | CU
39.8 | CU
39.8 | CU
40.3 | CU
40.3 | CU
40.8 | CU
42 | CU
43 | CU
43.2 | CU
43.9 | CU
44.9 | CU
44.4 | CU
44 | CU
45 | CU
46.7 | CU
46.4 | CU
45.6 | CU
45.4 | CU
45.5 | CU
45 | CU
44.2 | CU
44.8 | CU
44.8 | CU
43.6 | CU
41.3 | CU
37.4 | CU
38.9 | CU
39.3 | CU
36.6 | CU
35 | CU
37.8 | CU
37.3 | CU
38.5 | CU
39.5 | CU
39.4 | CU
39.5 | CU
39.4 | CU
39.8 | CU
40.6 | CU
40.9 | CU
41 | CU
41.2 | CU
40.9 | CU
40.2 | CU
40.1 | CU
40.2 | CU
40.7 | CU
41.1 | CU
40.7 | CU
40.8 | CU
40.8 | CU
41.5 | CU
42 | CU
42.6 | CU
43 | CU
44.1 | CU
45.6 | CU
46.2 | CU
46.7 | CU
46.6 | CU
46.9 | CU
46.7 | CU
46.9 | CU
47.3 | CU
46 | CU
47.4 | CU
46.9 | CU
46.2 | CU
46.3 | CU
45.8 | CU
44.1 | CU
41.7 | CU
40 | CU
34 | CU
32.6 | CU
32.5 | CU
33.2 | CU
33.8 | CU
35.2 | CU
35.8 | CU
36.1 | CU
36.2 | CU
36.2 | CU
36.6 | CU
37.1 | CU
37.4 | CU
38.1 | CU
37.7 | CU
38.1 | CU
38.2 | CU
37.5 | CU
37 | CU
38.1 | CU
38.8 | CU
38.6 | CU
39 | CU
38.2 | CU
38.4 | CU
38.8 | CU
39.4 | CU
39.8 | CU
40.9 | CU
41.9 | CU
42.8 | CU
43.4 | CU
43.2 | CU
42.6 | CU
44.1 | CU
43.1 | CU
44.3 | CU
44.5 | CU
43.8 | CU
46.5 | CU
46.4 | CU
46.7 | CU
44.9 | CU
44.4 | CU
43.1 | CU
41.2 | CU
39.3 | CU
38 | CU
37.3 | CU
35.9 | CU
37.9 | CU
39 | CU
39.8 | CU
40.3 | CU
40.3 | CU
40.9 | CU
41.4 | CU
41.9 | CU
42.2 | CU
41.7 | CU
41.6 | CU
42.1 | CU
42.2 | CU
41.7 | CU
41.8 | CU
42.1 | CU
42.1 | CU
42.3 | CU
42.5 | CU
42.4 | CU
42.6 | CU
43.5 | CU
43.8 | CU
44.2 | CU
45.4 | CU
46.4 | CU
47.2 | CU
46.5 | CU
46.5 | CU
48.4 | CU
49 | CU
50 | CU
52.4 | CU
42.6 | CU
48.2 | CU
48 | CU
46.6 | CU
45.6 | CU
44.5 | CU
42.9 | CU
41.7 | CU
40.2 | CU
38.5 | CU
37 | CU
35.9 | CU
34.5 | CU
34.1 | CU
35.7 | CU
37.6 | CU
38.8 | CU
39.7 | CU
39.6 | CU
40.2 | CU
40.2 | CU
40.5 | CU
40.2 | CU
40.8 | CU
41.4 | CU
41.2 | CU
40.8 | CU
41.9 | CU
41.3 | CU
41.5 | CU
41.9 | CU
42 | CU
41.4 | CU
42 | CU
42.6 | CU
43.3 | CU
44.2 | CU
45.5 | CU
46.6 | CU
46.2 | CU
46.6 | CU
46.9 | CU
47 | CU
46.7 | CU
47.2 | CU
46.5 | CU
46.9 | CU
46.5 | CU
46.5 | CU
46.4 | CU
45.3 | CU
43.8 | CU
42.5 | CU
39.8 | CU
39.1 | CU
36.5 | CU
36.8 | CU
36.7 | CU
36.7 | CU
34.2 | CU
36.4 | CU
37.3 | CU
38.2 | CU
37.7 | CU
38.4 | CU
39.2 | CU
39.2 | CU
39.9 | CU
39.5 | CU
40 | CU
40 | CU
40 | CU
39.6 | CU
39.4 | CU
40.1 | CU
40.6 | CU
40.5 | CU
41 | CU
40.2 | CU
40.9 | CU
40.9 | CU
41.9 | CU
43.1 | CU
44 | CU
45.9 | CU
46 | CU
46.2 | CU
46.1 | CU
45.6 | CU
46.7 | CU
46.4 | CU
45.6 | CU
46.9 | CU
46.9 | CU
46.7 | CU
46.7 | CU
46.8 | CU
44.8 | CU
43.1 | CU
40.9 | CU
39.3 | CU
38.1 | CU
37.6 | CU
35.9 | CU
37.8 | CU
36.1 | CU
37.7 | CU
39 | CU
39.6 | CU
39.6 | CU
39.9 | CU
40.7 | CU
41.1 | CU
40.6 | CU
41.2 | CU
41.9 | CU
41.3 | CU
41.7 | CU
40.8 | CU
40.2 | CU
41.3 | CU
41.2 | CU
41.5 | CU
40.4 | CU
41.4 | CU
40.8 | CU
41.1 | CU
41.6 | CU
42.1 | CU
43.5 | CU
44.3 | CU
44.9 | CU
45.1 | CU
43.7 | CU
43.9 | CU
46.5 | CU
46.2 | CU
45.3 | CU
45.1 | CU
46.6 | CU
45.8 | CU
45.4 | CU
45.2 | CU
43.2 | CU
41.9 | CU
41.9 | CU
40.3 | CU
39.9 | CU
38.1 | CU
38.6 | CU
37.5 | CU
38 | CU
37.8 | CU
37.9 | CU
38.9 | CU
39.2 | CU
40.3 | CU
40.9 | CU
41 | CU
41.5 | CU
41.4 | CU
41.9 | CU
41.1 | CU
42 | CU
41.8 | CU
42.1 | CU
41.8 | CU
41 | CU
41.3 | CU
42.2 | CU
40.6 | CU
41.1 | CU
42 | CU
42.5 | CU
42.3 | CU
44.2 | CU
44.6 | CU
45.5 | CU
44.8 | CU
44.9 | CU
44.8 | CU
44.8 | CU
44.2 | CU
44.2 | CU
44.3 | CU
43.9 | CU
43.3 | CU
43.1 | CU
42.3 | CU
40.9 | CU
39.5 | CU
38.9 | CU
38 | CU
37.6 | CU
36.4 | CU
37.6 | CU
36.8 | CU
35.9 | CU
38 | CU
38.9 | CU
39.3 | CU
39.9 | CU
40 | CU
40.1 | CU
40.7 | CU
41.4 | CU
42.1 | CU
42 | CU
41.5 | CU
41.7 | CU
41.2 | CU
40.9 | CU
41.8 | CU
41.3 | CU
41.1 | CU
41.2 | CU
41.1 | CU
42 | CU
42.9 | CU
43.4 | CU
44.7 | CU
45.5 | CU
45.7 | CU
44.4 | CU
45.1 | CU
45.5 | CU
45.6 | CU
45.2 | CU
45.7 | CU
45.4 | CU
45.7 | CU
45.4 | CU
44.6 | CU
43.9 | CU
42.9 | CU
43.4 | CU
42.6 | CU
41.5 | CU
39.9 | CU
38.1 | CU
37.3 | CU
36.1 | CU
37.5 | CU
38.4 | CU
38.9 | CU
39.4 | CU
40.1 | CU
40.4 | CU
40.9 | CU
41.4 | CU
41.4 | CU
42 | CU
42.1 | CU
42.3 | CU
42.5 | CU
41.7 | CU
42.1 | CU
42.4 | CU
42 | CU
41.9 | CU
40.5 | CU
41.9 | CU
42 | CU
42.2 | CU
43.5 | CU
44.1 | CU
44.7 | CU
44.8 | CU
45.6 | CU
45.3 | CU
45.8 | CU
45.2 | CU
45.9 | CU
46.4 | CU
45.2 | CU
45.2 | CU
45.9 | CU
45.1 | CU
45.7 | CU
44.7 | CU
43.4 | CU
42.4 | CU
41.6 | CU
41.3 | CU
38.3 | CU
36.9 | CU
35.4 | CU
37.1 | CU
37.4 | CU
37.7 | CU
37.8 | CU
39.2 | CU
39.7 | CU
39.8 | CU
41.2 | CU
41.8 | CU
42.4 | CU
42.1 | CU
40.8 | CU
40.7 | CU
41.7 | CU
41.6 | CU
41.5 | CU
41.1 | CU
41.2 | CU
40.5 | CU
39.8 | CU
40.9 | CU
42.3 | CU
43.3 | CU
45.5 | CU
46.5 | CU
47.3 | CU
47.8 | CU
47 | CU
47.9 | CU
46.7 | CU
47.7 | CU
46.4 | CU
47.3 | CU
47.9 | CU
47.2 | CU
47.2 | CU
47 | CU
46.8 | CU
44.8 | CU
43.5 | CU
41.7 | CU
39.7 | CU
38.3 | CU
37.6 | CU
36.7 | CU
35.5 | CU
35.2 | CU
36 | CU
37.7 | CU
39.4 | CU
39.4 | CU
39.7 | CU
40.6 | CU
40.7 | CU
40.6 | CU
41 | CU
41.2 | CU
40.8 | CU
41.6 | CU
41 | CU
39 | CU
40.3 | CU
40.5 | CU
41.2 | CU
41.2 | CU
42.2 | CU
42.1 | CU
44.2 | CU
45.6 | CU
46.7 | CU
46.7 | CU
46.4 | CU
45.8 | CU
46.5 | CU
46.9 | CU
47.5 | CU
46.8 | CU
47.1 | CU
46.6 | CU
47.2 | CU
46.8 | CU
46.1 | CU
44.5 | CU
42.7 | CU
40.6 | CU
39.4 | CU
37 | CU
35.8 | CU
35.4 | CU
34.7 | CU
33.3 | CU
34.4 | CU
36.6 | CU
37.5 | CU
37.9 | CU
38.4 | CU
39.3 | CU
40.1 | CU
40.2 | CU
40.7 | CU
40 | CU
39.7 | CU
39.5 | CU
39.8 | CU
40.3 | CU
40.8 | CU
40.8 | CU
41.1 | CU
40.9 | CU
40.5 | CU
40.2 | CU
40.6 | CU
43.3 | CU
46.3 | CU
45.9 | CU
46.3 | CU
45.8 | CU
46.9 | CU
46.3 | CU
46.2 | CU
46.9 | CU
46.8 | CU
46.9 | CU
45.9 | CU
45.9 | CU
44.7 | CU
43 | CU
41 | CU
38.3 | CU
38 | CU
35.9 | CU
35.2 | CU
34.4 | CU
34.7 | CU
35 | CU
37.1 | CU
38.1 | CU
38.8 | CU
38.9 | CU
39.5 | CU
39.6 | CU
40.3 | CU
41 | CU
41.1 | CU
41.1 | CU
41.4 | CU
41.2 | CU
40.7 | CU
40.3 | CU
40.2 | CU
40.6 | CU
40.8 | CU
40.9 | CU
41.3 | CU
41.2 | CU
42 | CU
42.5 | CU
42.8 | CU
45 | CU
45.1 | CU
46.8 | CU
46.5 | CU
46.4 | CU
46.2 | CU
46.4 | CU
47.7 | CU
47.2 | CU
47 | CU
47.1 | CU
47 | CU
45 | CU
44.8 | CU
42.9 | CU
41.2 | CU
38.9 | CU
37.9 | CU
37.2 | CU
36.7 | CU
35.6 | CU
34.6 | CU
35.8 | CU
37.3 | CU
38.7 | CU
39.8 | CU
39.2 | CU
40.3 | CU
40.5 | CU
39.8 | CU
40.9 | CU
40.1 | CU
40.1 | CU
40.4 | CU
40.5 | CU
40.1 | CU
39.7 | CU
39.4 | CU
40.2 | CU
39.7 | CU
40.6 | CU
40.1 | CU
39.9 | CU
40.3 | CU
40.7 | CU
42.3 | CU
43.7 | CU
45.1 | CU
46.1 | CU
45.2 | CU
45.2 | CU
45.9 | CU
46.4 | CU
46 | CU
45.6 | CU
45.6 | CU
44.6 | CU
44.6 | CU
43.1 | CU
41.4 | CU
40 | CU
39.2 | CU
37.8 | CU
36.6 | CU
35 | CU
33.9 | CU
33.3 | CU
33.1 | CU
33.5 | CU
35 | CU
35.9 | CU
36.5 | CU
36.6 | CU
37.4 | CU
38.1 | CU
38.2 | CU
38.7 | CU
38.8 | CU
38.7 | CU
38.2 | CU
38.3 | CU
38.1 | CU
38.1 | CU
38.1 | CU
37.9 | CU
39.1 | CU
38.7 | CU
38.8 | CU
38.9 | CU
39.7 | CU
40.9 | CU
42.7 | CU
44.9 | CU
46.5 | CU
44.9 | CU
45.1 | CU
45.5 | CU
45.5 | CU
46.3 | CU
46.2 | CU
44 | CU
43.7 | CU
43.1 | CU
41.7 | CU
40.3 | CU
38.8 | CU
38 | CU
36.3 | CU
36.3 | CU
35.4 | CU
34.7 | CU
34.3 | CU
34 | CU
35 | CU
36.8 | CU
37.3 | CU
37.1 | CU
37.3 | CU
38.1 | CU
38.9 | CU
39.1 | CU
39 | CU
39.4 | CU
39.7 | CU
39.7 | CU
38.5 | CU
39.5 | CU
39.8 | CU
39.6 | CU
39.5 | CU
39.7 | CU
40.2 | CU
39.9 | CU
40.6 | CU
41.6 | CU
42.2 | CU
43.8 | CU
45.8 | CU
46.8 | CU
46.8 | CU
46.5 | CU
46.8 | CU
47.2 | CU
47.2 | CU
47 | CU
47.1 | CU
46.9 | CU
48 | CU
48.1 | CU
47.5 | CU
43.4 | CU
42.2 | CU
40.6 | CU
39.3 | CU
38.4 | CU
37.3 | CU
35.5 | CU
35.1 | CU
35.3 | CU
37.8 | CU
38.2 | CU
38.3 | CU
38.8 | CU
39.5 | CU
40.5 | CU
40.7 | CU
40.8 | CU
41.6 | CU
41.3 | CU
40.5 | CU
41.1 | CU
41.9 | CU
41.2 | CU
41.3 | CU
41.3 | CU
41 | CU
41.2 | CU
42.3 | CU
42.7 | CU
42.7 | CU
43.8 | CU
44.8 | CU
46.4 | CU
47.6 | CU
48.8 | CU
48.6 | CU
48.2 | CU
48.9 | CU
49.5 | CU
49.3 | CU
49.4 | CU
49.6 | CU
49.9 | CU
49.7 | CU
49.8 | CU
49.1 | CU
47.9 | CU
47.1 | CU
42.5 | CU
39.8 | CU
38.2 | CU
37.3 | CU
36 | CU
35.1 | CU
35.9 | CU
37.9 | CU
39.3 | CU
39.6 | CU
40 | CU
40.6 | CU
40.5 | CU
40.4 | CU
41 | CU
41.1 | CU
41.1 | CU
41.7 | CU
41.7 | CU
41.1 | CU
40.5 | CU
41.5 | CU
41.6 | CU
41.2 | CU
41.3 | CU
41.3 | CU
43.1 | CU
44.8 | CU
46.1 | CU
47.3 | CU
47.7 | CU
48 | CU
48.5 | CU
47.9 | CU
48 | CU
47.2 | CU
46.8 | CU
49.6 | CU
48.5 | CU
48.2 | CU
48 | CU
47.1 | CU
45.6 | CU
43.6 | CU
42.3 | CU
40.3 | CU
34.6 | CU
32.1 | CU
33.1 | CU
32.5 | CU
34.8 | CU
36.4 | CU
37 | CU
37 | CU
37.5 | CU
37.4 | CU
37.3 | CU
37.7 | CU
37.3 | CU
37.5 | CU
37.7 | CU
37.6 | CU
37.7 | CU
38 | CU
38.2 | CU
38.3 | CU
38.2 | CU
38.2 | CU
38.2 | CU
37.2 | CU
37.9 | CU
38.4 | CU
39.2 | CU
40.1 | CU
41.5 | CU
42.5 | CU
42.9 | CU
43.4 | CU
44.4 | CU
45.5 | CU
47.3 | CU
45.2 | CU
44.8 | CU
45.1 | CU
45.3 | CU
45.5 | CU
44.6 | CU
43.4 | CU
42.3 | CU
39.7 | CU
38.7 | CU
38.3 | CU
35.6 | CU
35.9 | CU
35.6 | CU
33.1 | CU
34.6 | CU
35.6 | CU
36.3 | CU
37.1 | CU
37.4 | CU
38.4 | CU
38.6 | CU
38.7 | CU
38.5 | CU
39.5 | CU
39.2 | CU
39.1 | CU
38.6 | CU
38.3 | CU
38.4 | CU
38.2 | CU
38.1 | CU
37.9 | CU
38.2 | CU
39 | CU
38.9 | CU
39.5 | CU
39.3 | CU
40.2 | CU
41.5 | CU
42.5 | CU
42.2 | CU
43.1 | CU
42.6 | CU
42.7 | CU
40.2 | CU
42.5 | CU
41.2 | CU
42 | CU
41.3 | CU
38.1 | CU
39.6 | CU
38.5 | CU
38.7 | CU
38.6 | CU
36.7 | CU
36.4 | CU
35.5 | CU
35.7 | CU
35.4 | CU
35.5 | CU
35.2 | CU
35.6 | CU
37.8 | CU
38.2 | CU
38.1 | CU
38.7 | CU
39.1 | CU
39.6 | CU
39.7 | CU
38.9 | CU
38.7 | CU
38.4 | CU
38.5 | CU
38.6 | CU
38.3 | CU
38.4 | CU
38.5 | CU
38.8 | CU
38.9 | CU
38.8 | CU
39.2 | CU
39.1 | CU
40 | CU
39.9 | CU
41.6 | CU
42.8 | CU
43.1 | CU
43.4 | CU
43.3 | CU
44.2 | CU
41.9 | CU
43.2 | CU
43.3 | CU
42.5 | CU
42.4 | CU
43.1 | CU
42.9 | CU
42.6 | CU
39.7 | CU
38.3 | CU
37 | CU
36.9 | CU
33.8 | CU
32.9 | CU
35 | CU
33.8 | CU
35.5 | CU
35.5 | CU
35.9 | CU
36.1 | CU
36 | CU
37.9 | CU
37.7 | CU
38 | CU
38.6 | CU
38.7 | CU
38.2 | CU
38.2 | CU
37.6 | CU
37.4 | CU
37.1 | CU
38.5 | CU
38 | CU
37.8 | CU
38 | CU
38.3 | CU
37.7 | CU
38.3 | CU
39.9 | CU
41.3 | CU
41.9 | CU
43.1 | CU
42.7 | CU
42.3 | CU
42.8 | CU
42.9 | CU
43.4 | CU
43.5 | CU
43.8 | CU
43.9 | CU
43.1 | CU
41.9 | CU
43 | CU
44.4 | CU
41.2 | CU
39.5 | CU
38.4 | CU
36.7 | CU
35.2 | CU
34.9 | CU
33.4 | CU
35.3 | CU
32.2 | CU
32.7 | CU
34.7 | CU
35.7 | CU
36.6 | CU
36.9 | CU
36.9 | CU
37.5 | CU
37.8 | CU
38.6 | CU
38.7 | CU
38.7 | CU
38.9 | CU
39 | CU
38.6 | CU
38.5 | CU
39.2 | CU
38.5 | CU
39.3 | CU
39.7 | CU
39.3 | CU
41.8 | CU
42.8 | CU
43 | CU
43.7 | CU
44 | CU
44.2 | CU
44.4 | CU
44.5 | CU
43.8 | CU
45.5 | CU
45.3 | CU
44.6 | CU
46.7 | CU
49.4 | CU
43.4 | CU
48.9 | CU
40.6 | CU
36.5 | CU
35.6 | CU
34.8 | CU
32.6 | CU
31.8 | CU
31.8 | CU
33 | CU
34.8 | CU
35.1 | CU
35.4 | CU
35.5 | CU
35.6 | CU
36.2 | CU
37.1 | CU
36.9 | CU
36.7 | CU
37.5 | CU
37.6 | CU
37.5 | CU
38 | CU
37.7 | CU
37.7 | CU
37.9 | CU
37.9 | CU
37.7 | CU
37.7 | CU
38.5 | CU
38.5 | CU
39.8 | CU
41.4 | CU
42.7 | CU
43.6 | CU
43.1 | CU
43 | CU
43.7 | CU
43.1 | CU
42.8 | CU
42.4 | CU
42.8 | CU
42.7 | CU
43.3 | CU
42.7 | CU
41 | CU
39.2 | CU
39.3 | CU
36.7 | CU
36.6 | CU
37.6 | CU
49.2 | CU
32 | CU
31.7 | CU
31.9 | CU
31.5 | CU
32.7 | CU
33.4 | CU
33.5 | CU
33.5 | CU
34.5 | CU
35.5 | CU
34.3 | CU
35.8 | CU
36.2 | CU
35.1 | CU
35.4 | CU
35.6 | CU
36.2 | CU
36.2 | CU
35.6 | CU
35.2 | CU
35 | CU
36.3 | CU
37.2 | CU
37.4 | CU
38.7 | CU
40.3 | CU
41.1 | CU
42.5 | CU
41.1 | CU
40.2 | CU
41.2 | CU
43.8 | CU
42.4 | CU
41.9 | CU
40.7 | CU
42.3 | CU
44.3 | CU
42.9 | CU
46.3 | CU
47.7 | CU
37.1 | CU
37.3 | CU
35.1 | CU
34.8 | CU
34.8 | CU
32.5 | CU
31.9 | CU
31.3 | CU
31.2 | CU
31.1 | CU
33.5 | CU
32.8 | CU
33.6 | CU
34.3 | CU
34.3 | CU
34.6 | CU
34.7 | CU
35.3 | CU
35.3 | CU
35.6 | CU
35.6 | CU
35.5 | CU
35.2 | CU
35.2 | CU
35.2 | CU
35.1 | CU
35.3 | CU
35.7 | CU
36 | CU
36.4 | CU
37.8 | CU
39.4 | CU
40.9 | CU
42.6 | CU
42.5 | CU
42.1 | CU
42 | CU
41.9 | CU
42.1 | CU
41.5 | CU
41.7 | CU
41.4 | CU
40.9 | CU
40.6 | CU
40.6 | CU
39.1 | CU
37.9 | CU
36.7 | CU
36 | CU
34.6 | CU
33.5 | CU
33 | CU
32.4 | CU
31.9 | CU
31.4 | CU
31.1 | CU
31.6 | CU
32.3 | CU
32.4 | CU
32.6 | CU
32.7 | CU
32.6 | CU
33.1 | CU
33 | CU
33.2 | CU
32.9 | CU
32.4 | CU
32.9 | CU
33.1 | CU
33.2 | CU
33.3 | CU
33.1 | CU
33.2 | CU
33.2 | CU
33.9 | CU
35 | CU
35.2 | CU
36.4 | CU
38.9 | CU
40.8 | CU
42.2 | CU
42.1 | CU
42.4 | CU
41.7 | CU
41.1 | CU
41.6 | CU
41.9 | CU
41.7 | CU
41.5 | CU
41 | CU
40.4 | CU
39.6 | CU
38.1 | CU
37.2 | CU
35.8 | CU
34.2 | CU
33.4 | CU
32.4 | CU
31.9 | CU
31.7 | CU
31.4 | CU
31.9 | CU
32.7 | CU
33.4 | CU
33.9 | CU
34.1 | CU
33.9 | CU
34.7 | CU
34.7 | CU
34.8 | CU
35.4 | CU
35.6 | CU
35.3 | CU
35.2 | CU
35 | CU
35.3 | CU
34.9 | CU
34.8 | CU
35.4 | CU
36.1 | CU
36.5 | CU
37.2 | CU
38 | CU
39.6 | CU
41.2 | CU
42.2 | CU
42.7 | CU
42.3 | CU
43.2 | CU
42.5 | CU
43.4 | CU
43.1 | CU
43.7 | CU
42.9 | CU
43.4 | CU
42.5 | CU
42.6 | CU
41.3 | CU
40.2 | CU
38.5 | CU
37.3 | CU
35.7 | CU
34.9 | CU
34 | CU
33.3 | CU
32.3 | CU
32 | CU
32.4 | CU
34 | CU
34.7 | CU
35.4 | CU
35.5 | CU
36.1 | CU
36.7 | CU
36.7 | CU
37 | CU
37.1 | CU
37.1 | CU
37.4 | CU
37.1 | CU
36.5 | CU
36.9 | CU
37.5 | CU
37.3 | CU
37.1 | CU
36.5 | CU
36.9 | CU
37.2 | CU
37.1 | CU
37.7 | CU
38.2 | CU
39.3 | CU
41.2 | CU
42.4 | CU
42.2 | CU
42.3 | CU
42.6 | CU
42.7 | CU
42.5 | CU
42.5 | CU
43.3 | CU
43.3 | CU
42.8 | CU
42 | CU
40.3 | CU
38.9 | CU
37.2 | CU
36.6 | CU
35.4 | CU
34.9 | CU
33.7 | CU
35 | CU
34.4 | CU
34.5 | CU
35.2 | CU
37.2 | CU
37.8 | CU
37.9 | CU
38.1 | CU
38.2 | CU
38.6 | CU
38.8 | CU
39.5 | CU
39.3 | CU
39.4 | CU
39.4 | CU
39.7 | CU
39.9 | CU
39.6 | CU
39.5 | CU
39.2 | CU
39.4 | CU
39.3 | CU
39 | CU
38.9 | CU
39.9 | CU
40.6 | CU
41.1 | CU
41.6 | CU
43.9 | CU
43.7 | CU
44.7 | CU
44.8 | CU
43.7 | CU
43.1 | CU
45.4 | CU
45.4 | CU
45.7 | CU
44.8 | CU
44.2 | CU
44.5 | CU
42.9 | CU
40.6 | CU
39.8 | CU
38.3 | CU
38 | CU
35.9 | CU
35.5 | CU
34 | CU
34.2 | CU
34.8 | CU
36.9 | CU
37.4 | CU
37.6 | CU
37.9 | CU
38.3 | CU
38.5 | CU
38.8 | CU
38.9 | CU
39 | CU
39.1 | CU
39.2 | CU
39.8 | CU
39.1 | CU
39.4 | CU
39.5 | CU
39.7 | CU
39.3 | CU
39.3 | CU
39.2 | CU
39.2 | CU
39.3 | CU
40 | CU
40.6 | CU
41.2 | CU
42.5 | CU
43.2 | CU
42.9 | CU
45 | CU
44.5 | CU
44.4 | CU
44.5 | CU
45.3 | CU
45.8 | CU
45.2 | CU
44.5 | CU
43.3 | CU
42.3 | CU
41.3 | CU
40.1 | CU
38.7 | CU
38.3 | CU
37 | CU
36.2 | CU
35.7 | CU
35.4 | CU
36.6 | CU
37.9 | CU
38.3 | CU
38.9 | CU
39 | CU
39.8 | CU
40.2 | CU
40.1 | CU
40 | CU
40.5 | CU
40.6 | CU
40.1 | CU
40.3 | CU
40.9 | CU
40.6 | CU
40.8 | CU
41 | CU
40.3 | CU
40.7 | CU
40.7 | CU
41.3 | CU
41.5 | CU
42.4 | CU
42.7 | CU
43.2 | CU
44.1 | CU
45.8 | CU
45.2 | CU
45 | CU
45.6 | CU
45.7 | CU
45.4 | CU
46.1 | CU
43.4 | CU
43.2 | CU
43.4 | CU
42.3 | CU
41.7 | CU
39.8 | CU
39.5 | CU
38.4 | CU
39 | CU
38.2 | CU
38.3 | CU
37 | CU
37.6 | CU
38.3 | CU
39 | CU
39.6 | CU
39.2 | CU
39.9 | CU
39.9 | CU
39.8 | CU
40.1 | CU
39.7 | CU
39.8 | CU
40 | CU
39.8 | CU
39.6 | CU
40.3 | CU
39.6 | CU
39.9 | CU
39.6 | CU
39.9 | CU
39.5 | CU
39.4 | CU
39.2 | CU
39.8 | CU
39.7 | CU
40.1 | CU
40.7 | CU
41.1 | CU
41.7 | CU
41.6 | CU
41.4 | CU
42.6 | CU
42.3 | CU
42.5 | CU
42.9 | CU
43.1 | CU
42.7 | CU
42.4 | CU
42.1 | CU
41.4 | CU
41 | CU
40.9 | CU
40.5 | CU
39 | CU
41.3 | CU
42.4 | CU
46.1 | CU
46.9 | CU
36.4 | CU
36.2 | CU
36.2 | CU
36.3 | CU
36.2 | CU
36 | CU
36.4 | CU
36.2 | CU
36.2 | CU
36.3 | CU
36.4 | CU
36.3 | CU
36.2 | CU
36.4 | CU
36.3 | CU
36.3 | CU
36.3 | CU
36.2 | CU
36.3 | CU
36.2 | CU
36.3 | CU
36.1 | CU
36.1 | CU
36.2 | CU
36.3 | CU
36.5 | CU
36.6 | CU
36.5 | CU
36.3 | CU
36.2 | CU
36.4 | CU
36.3 | CU
36.3 | CU
36.3 | CU
36.2 | CU
36.3 | CU
36.2 | CU
36.3 | CU
36.1 | CU
36.1 | CU
36.2 | CU
36.3 | CU
36.5 | CU
36.6 | CU
36.5 | CU
36.3 | CU
36.4 | CU
36.6 | CU
36.3 | CU
36.6 | CU
36.6 | CU
36.4 | CU
36.6 | CU
36.9 | CU
36.8 | CU
37.2 | CU
37.1 | CU
37.6 | CU
37.7 | CU
37.4 | CU
37.4 | CU
37.2 | CU
37.1 | CU
36.7 | CU
37.2 | CU
37.2 | CU
37.6 | CU
38.2 | CU
38.4 | CU
39.1 | CU
39.3 | CU
39.3 | CU
39 | CU
39.2 | CU
39 | CU
39.2 | CU
39.3 | CU
39.4 | CU
39.6 | CU
39.2 | CU
39.3 | CU
39.3 | CU
40.1 | CU
40.1 | CU
46.9 | CU
49.1 | CU
47.8 | CU
47.6 | CU
0 | CU
0 | CU
0 | CU
0 | CU
0 | CU
36.5 | CU
35.7 | CU
37.1 | CU
38.5 | CU
38.8 | CU
39.1 | CU
39.3 | CU
39.6 | CU
39.9 | CU
40.3 | CU
40 | CU
39.6 | CU
39.7 | CU
39.5 | CU
39.6 | CU
39.8 | CU
39.5 | CU
39.5 | CU
39.3 | CU
39.9 | CU
39.9 | CU
40 | CU
40.2 | CU
40.6 | CU
40.6 | CU
41.6 | CU
42 | CU
43.5 | CU
43.8 | CU
43.8 | CU
43.9 | CU
43.5 | CU
43.8 | CU
43.4 | CU
44 | CU
43.9 | CU
43.8 | CU
43.4 | CU
43.5 | CU
42.6 | CU
42.2 | CU
39.8 | CU
38.9 | CU
37.8 | CU
37.9 | CU
37.3 | CU
36.7 | CU
36.4 | CU
36.8 | CU
37.9 | CU
38.2 | CU
39 | CU
39.2 | CU
39.5 | CU
40 | CU
39.6 | CU
40 | CU
40.5 | CU
40.3 | CU
40.2 | CU
39.7 | CU
39.9 | CU
40.3 | CU
40.3 | CU
39.9 | CU
39.7 | CU
40.7 | CU
40.6 | CU
41 | CU
41.3 | CU
41.7 | CU
42.4 | CU
43.4 | CU
43.5 | CU
43.4 | CU
43.4 | CU
43.5 | CU
43.7 | CU
43.5 | CU
43.2 | CU
43.4 | CU
43 | CU
42.8 | CU
42.1 | CU
42 | CU
41.1 | CU
39.8 | CU
39.4 | CU
37.9 | CU
36.7 | CU
35.8 | CU
35.8 | CU
35.8 | CU
35.5 | CU
35.4 | CU
35.6 | CU
36.1 | CU
36.3 | CU
36.7 | CU
37.3 | CU
38.4 | CU
39.2 | CU
39.2 | CU
39 | CU
39.4 | CU
39.3 | CU
39.2 | CU
38.9 | CU
38.8 | CU
38.9 | CU
38.8 | CU
38.9 | CU
39.3 | CU
40 | CU
40.5 | CU
40.4 | CU
41.3 | CU
42.1 | CU
42.8 | CU
43.6 | CU
43.4 | CU
43.1 | CU
43.8 | CU
43.4 | CU
44.4 | CU
44 | CU
44.2 | CU
43.6 | CU
43.8 | CU
43 | CU
42.6 | CU
42.1 | CU
40.3 | CU
39.2 | CU
37.8 | CU
37.2 | CU
36.8 | CU
36.5 | CU
35.9 | CU
36 | CU
36.5 | CU
36.9 | CU
38 | CU
38 | CU
38.6 | CU
39.2 | CU
39.4 | CU
39.7 | CU
40.1 | CU
41.1 | CU
40.9 | CU
40.2 | CU
39.6 | CU
40.3 | CU
40 | CU
40.1 | CU
40.2 | CU
40.3 | CU
40.5 | CU
41 | CU
41.4 | CU
41 | CU
41.3 | CU
41.9 | CU
42.9 | CU
43.4 | CU
43.6 | CU
43.8 | CU
44.1 | CU
44.2 | CU
44.3 | CU
44 | CU
44.1 | CU
48.3 | CU
48.1 | CU
48.2 | CU
47.5 | CU
47.7 | CU
46.4 | CU
45.3 | CU
43.4 | CU
42.3 | CU
40.8 | CU
39.9 | CU
39 | CU
39 | CU
39.1 | CU
40.3 | CU
40.9 | CU
41.6 | CU
41.9 | CU
42.1 | CU
42.3 | CU
42.2 | CU
42.9 | CU
43 | CU
43.6 | CU
43.2 | CU
43 | CU
43 | CU
43.3 | CU
42.7 | CU
42.6 | CU
42.8 | CU
43 | CU
43.7 | CU
44 | CU
44.1 | CU
44.4 | CU
45.3 | CU
45.5 | CU
46.2 | CU
45.8 | CU
46.8 | CU
47.4 | CU
47.4 | CU
48 | CU
46.6 | CU
47.4 | CU
46.9 | CU
46.3 | CU
46 | CU
45.9 | CU
44.6 | CU
43.7 | CU
42.9 | CU
41.8 | CU
38.8 | CU
36.3 | CU
34 | CU
33.9 | CU
33.8 | CU
33.9 | CU
35.2 | CU
35.6 | CU
36 | CU
37.1 | CU
37.2 | CU
37.6 | CU
37.6 | CU
38 | CU
38.1 | CU
38 | CU
37.9 | CU
38 | CU
37.9 | CU
38.4 | CU
38.4 | CU
37.9 | CU
38.1 | CU
38.7 | CU
38.6 | CU
39.3 | CU
39.3 | CU
39.6 | CU
40.5 | CU
41.5 | CU
42.9 | CU
43.8 | CU
44.1 | CU
44.6 | CU
44.4 | CU
44.3 | CU
44.5 | CU
44.2 | CU
44 | CU
43.9 | CU
43.6 | CU
42.7 | CU
40.8 | CU
39.3 | CU
38.3 | CU
36.6 | CU
35.5 | CU
34.1 | CU
32.6 | CU
32.4 | CU
32.2 | CU
32 | CU
32.4 | CU
32.8 | CU
33.2 | CU
33 | CU
33.8 | CU
34.7 | CU
34.5 | CU
35.1 | CU
35.4 | CU
35.3 | CU
35.2 | CU
35.5 | CU
35.8 | CU
36.6 | CU
35.8 | CU
36 | CU
36 | CU
35.9 | CU
35.9 | CU
36.3 | CU
36.5 | CU
37.6 | CU
38.8 | CU
41 | CU
43 | CU
43.2 | CU
42.7 | CU
43.8 | CU
44.1 | CU
43.3 | CU
44.2 | CU
44.2 | CU
43.6 | CU
42.9 | CU
42.7 | CU
41.8 | CU
41.2 | CU
39.4 | CU
37.9 | CU
36.4 | CU
36 | CU
34.7 | CU
33.3 | CU
32.8 | CU
34.7 | CU
33.7 | CU
34.3 | CU
34.7 | CU
34.6 | CU
35.1 | CU
36.2 | CU
36.3 | CU
36.7 | CU
37 | CU
37.6 | CU
36.8 | CU
36.9 | CU
37 | CU
36.7 | CU
36.8 | CU
36.6 | CU
37.6 | CU
37.1 | CU
36.9 | CU
36.3 | CU
37.2 | CU
37.4 | CU
39.2 | CU
40 | CU
40.8 | CU
43 | CU
44.4 | CU
44.3 | CU
44.6 | CU
45.5 | CU
45.5 | CU
44.5 | CU
44.2 | CU
44.7 | CU
43.7 | CU
43.3 | CU
42.5 | CU
41.1 | CU
40.2 | CU
38.6 | CU
37.6 | CU
36.4 | CU
35.1 | CU
35.2 | CU
34.4 | CU
34.3 | CU
34.8 | CU
34.1 | CU
34.2 | CU
34.3 | CU
34.8 | CU
35.4 | CU
36 | CU
36.4 | CU
36 | CU
36.5 | CU
36.7 | CU
36.9 | CU
35.7 | CU
36 | CU
36.6 | CU
36.3 | CU
36.4 | CU
36.9 | CU
36.9 | CU
37.5 | CU
37 | CU
38 | CU
38.1 | CU
38.2 | CU
39.5 | CU
42.2 | CU
43.2 | CU
43.4 | CU
43.4 | CU
43.2 | CU
44 | CU
42.5 | CU
43.9 | CU
44 | CU
45.5 | CU
45 | CU
44.6 | CU
43.6 | CU
42 | CU
39.9 | CU
39.4 | CU
37.8 | CU
37.1 | CU
36.2 | CU
35.7 | CU
35.1 | CU
35 | CU
36 | CU
35.9 | CU
36.6 | CU
37.3 | CU
38.1 | CU
38.6 | CU
38.3 | CU
37.9 | CU
38.1 | CU
39 | CU
39.3 | CU
39.3 | CU
39.1 | CU
39.1 | CU
38.8 | CU
38.9 | CU
38.9 | CU
39.2 | CU
39.4 | CU
39.6 | CU
40.6 | CU
39.9 | CU
39.4 | CU
40 | CU
40.7 | CU
41.8 | CU
43 | CU
44.3 | CU
44.6 | CU
44.3 | CU
44.9 | CU
44.7 | CU
45.6 | CU
45.4 | CU
45.4 | CU
45 | CU
44.8 | CU
43.4 | CU
42.2 | CU
40.4 | CU
39.2 | CU
38.6 | CU
37 | CU
36.8 | CU
35.4 | CU
36 | CU
37.2 | CU
37.5 | CU
38.1 | CU
38 | CU
38.1 | CU
38.1 | CU
38.4 | CU
38.5 | CU
38.6 | CU
38.8 | CU
39.1 | CU
39.1 | CU
39.5 | CU
39.5 | CU
39.3 | CU
39.3 | CU
39.3 | CU
39.5 | CU
39.4 | CU
40.2 | CU
40.4 | CU
39.9 | CU
40.5 | CU
40.9 | CU
41.5 | CU
42.4 | CU
44.5 | CU
44.4 | CU
44.3 | CU
45 | CU
45.1 | CU
45 | CU
45.3 | CU
45.6 | CU
45.3 | CU
45 | CU
43.6 | CU
43 | CU
41.8 | CU
40.3 | CU
39.1 | CU
37.8 | CU
37.2 | CU
37.1 | CU
36.3 | CU
36 | CU
37.1 | CU
36.9 | CU
36.7 | CU
37.5 | CU
37.8 | CU
38.2 | CU
37.8 | CU
38 | CU
38.3 | CU
38.7 | CU
38.7 | CU
38.7 | CU
39.3 | CU
39.2 | CU
39.6 | CU
39.8 | CU
39.7 | CU
39.3 | CU
39.3 | CU
39.6 | CU
39.7 | CU
40.2 | CU
40.6 | CU
41 | CU
41.5 | CU
42.8 | CU
44.4 | CU
44.5 | CU
44.8 | CU
45.2 | CU
45 | CU
44.9 | CU
46.1 | CU
45.8 | CU
46 | CU
44.5 | CU
43.9 | CU
42.4 | CU
41.7 | CU
40 | CU
39.7 | CU
38.4 | CU
38.5 | CU
38 | CU
37.7 | CU
37.4 | CU
38.8 | CU
38.8 | CU
38.9 | CU
39.2 | CU
39.7 | CU
39.7 | CU
39.9 | CU
39.8 | CU
40.3 | CU
39.9 | CU
40.2 | CU
40 | CU
39.8 | CU
39.9 | CU
40.1 | CU
40.2 | CU
39.7 | CU
40.4 | CU
40.3 | CU
40.1 | CU
40.9 | CU
40.8 | CU
40.9 | CU
40.8 | CU
41.9 | CU
43.3 | CU
44.6 | CU
44.8 | CU
45.2 | CU
45.3 | CU
46 | CU
46.2 | CU
46 | CU
45.7 | CU
46.8 | CU
46 | CU
44.5 | CU
43 | CU
42.2 | CU
40.9 | CU
39.4 | CU
38.2 | CU
37.4 | CU
36.4 | CU
36.7 | CU
36.8 | CU
37.6 | CU
37.7 | CU
37.9 | CU
38.5 | CU
38.8 | CU
39.1 | CU
39.7 | CU
39.6 | CU
39.7 | CU
39.6 | CU
39.8 | CU
40 | CU
39.9 | CU
40 | CU
40.1 | CU
40.2 | CU
40.1 | CU
40.1 | CU
40.4 | CU
40.9 | CU
41.1 | CU
41.1 | CU
40.8 | CU
41 | CU
42.7 | CU
43.8 | CU
45.5 | CU
45.9 | CU
45.9 | CU
45.2 | CU
45.2 | CU
46.1 | CU
46.9 | CU
48.2 | CU
47.3 | CU
47 | CU
46.3 | CU
46.2 | CU
44.3 | CU
41.5 | CU
39.8 | CU
38.3 | CU
37.5 | CU
36.8 | CU
37.1 | CU
37.2 | CU
38.3 | CU
38.1 | CU
38.3 | CU
38.8 | CU
39.2 | CU
39.2 | CU
39.8 | CU
39.5 | CU
39.5 | CU
39.9 | CU
39.7 | CU
40 | CU
39.9 | CU
40 | CU
39.9 | CU
40.1 | CU
39.9 | CU
39.5 | CU
39.8 | CU
40.2 | CU
40.2 | CU
40.4 | CU
41 | CU
41.4 | CU
42.4 | CU
43.4 | CU
45.1 | CU
44.5 | CU
44.9 | CU
45.9 | CU
45.8 | CU
46.2 | CU
46.1 | CU
46 | CU
45.9 | CU
46.8 | CU
47.6 | CU
47 | CU
46.4 | CU
45 | CU
43.7 | CU
41.3 | CU
39.3 | CU
38.8 | CU
38.7 | CU
39.4 | CU
40.7 | CU
40.7 | CU
40.8 | CU
41.3 | CU
41.6 | CU
41.8 | CU
41.9 | CU
42 | CU
42.3 | CU
42 | CU
41.8 | CU
42.4 | CU
42.2 | CU
42.4 | CU
42.4 | CU
42.2 | CU
42.3 | CU
42.1 | CU
42.3 | CU
42.2 | CU
42.2 | CU
42.3 | CU
42.5 | CU
42.8 | CU
44.2 | CU
45.2 | CU
45.8 | CU
45.9 | CU
45.8 | CU
44.8 | CU
46.8 | CU
46.1 | CU
46.9 | CU
46.4 | CU
46.6 | CU
47.1 | CU
47.5 | CU
47.7 | CU
46.7 | CU
45.2 | CU
43.9 | CU
42.1 | CU
41 | CU
39.4 | CU
37.2 | CU
36.8 | CU
38.1 | CU
38 | CU
38.3 | CU
38.3 | CU
39.6 | CU
39.6 | CU
39.9 | CU
40 | CU
40 | CU
39.4 | CU
39.8 | CU
39.6 | CU
39.5 | CU
39.9 | CU
40.1 | CU
40 | CU
40.1 | CU
40.1 | CU
40.1 | CU
40.1 | CU
40.1 | CU
39.9 | CU
40.3 | CU
40.6 | CU
40.8 | CU
41.4 | CU
42.1 | CU
43.3 | CU
43.6 | CU
43 | CU
44.8 | CU
46.3 | CU
44.7 | CU
44.9 | CU
44.8 | CU
45.1 | CU
45.2 | CU
44 | CU
44.6 | CU
42.8 | CU
41.9 | CU
40.8 | CU
40 | CU
38.7 | CU
37.4 | CU
37 | CU
36.4 | CU
36.1 | CU
37.8 | CU
37.9 | CU
38.7 | CU
39.3 | CU
39.4 | CU
39.5 | CU
40.1 | CU
40.1 | CU
39.7 | CU
39.8 | CU
39.5 | CU
39.3 | CU
39 | CU
39.1 | CU
39.2 | CU
39.6 | CU
39.4 | CU
39.5 | CU
40 | CU
39.9 | CU
40.1 | CU
40.9 | CU
40.9 | CU
41.6 | CU
42.9 | CU
44.3 | CU
45.2 | CU
44 | CU
44.6 | CU
44.5 | CU
45 | CU
45 | CU
45.5 | CU
44.4 | CU
44.2 | CU
44.4 | CU
44.4 | CU
43.4 | CU
42.9 | CU
42.2 | CU
40.3 | CU
39.1 | CU
37.8 | CU
37.4 | CU
37 | CU
37.6 | CU
37.2 | CU
38.4 | CU
38.2 | CU
38.7 | CU
39.2 | CU
39.3 | CU
40 | CU
39.7 | CU
39.6 | CU
39.5 | CU
39.6 | CU
39.6 | CU
39.6 | CU
39.4 | CU
39.3 | CU
39.4 | CU
39.4 | CU
40 | CU
39.5 | CU
39.9 | CU
39.9 | CU
39.7 | CU
39.4 | CU
40.1 | CU
40.3 | CU
41.7 | CU
43.2 | CU
45.5 | CU
46.3 | CU
45.9 | CU
44.7 | CU
44.5 | CU
43.7 | CU
44.2 | CU
45.1 | CU
44.5 | CU
42.7 | CU
43.2 | CU
43.7 | CU
42.2 | CU
39.8 | CU
39 | CU
38.1 | CU
40.2 | CU
37.9 | CU
38.4 | CU
38.6 | CU
39.5 | CU
39.3 | CU
39.4 | CU
40.3 | CU
40.3 | CU
40.8 | CU
41.4 | CU
40.8 | CU
40.7 | CU
40.9 | CU
40.4 | CU
40.8 | CU
40.2 | CU
40.2 | CU
40.1 | CU
39.7 | CU
40.4 | CU
40.3 | CU
40.5 | CU
40.5 | CU
41.4 | CU
40.5 | CU
41.3 | CU
41.6 | CU
42 | CU
42.5 | CU
42 | CU
42.5 | CU
42.6 | CU
43.2 | CU
42.6 | CU
43.4 | CU
43.6 | CU
42.4 | CU
43 | CU
43 | CU
42.8 | CU
42.9 | CU
41 | CU
39.5 | CU
38.8 | CU
42.1 | CU
38.8 | CU
39.4 | CU
40.4 | CU
39.6 | CU
40.6 | CU
41.3 | CU
39.6 | CU
41.6 | CU
41.7 | CU
41.9 | CU
41.5 | CU
41.7 | CU
41.1 | CU
40.9 | CU
40.7 | CU
41.2 | CU
40.7 | CU
40.6 | CU
40.5 | CU
40.8 | CU
41.2 | CU
40.9 | CU
41.1 | CU
41.2 | CU
41.4 | CU
41.4 | CU
41.3 | CU
41.9 | CU
42.1 | CU
42.1 | CU
42.3 | CU
42.4 | CU
42.7 | CU
42.3 | CU
42.7 | CU
42 | CU
42.6 | CU
42.5 | CU
42.6 | CU
41.4 | CU
41.3 | CU
40.4 | CU
39.4 | CU
39.1 | CU
40.5 | CU
39.6 | CU
39.1 | CU
39.1 | CU
38.2 | CU
39.3 | CU
39.7 | CU
39 | CU
39.6 | CU
39.8 | CU
40.1 | CU
41.5 | CU
40.1 | CU
39.8 | CU
40.3 | CU
41.2 | CU
41.1 | CU
40.7 | CU
39.4 | CU
40.6 | CU
41.1 | CU
40.5 | CU
40.5 | CU
40.6 | CU
40.8 | CU
41.1 | CU
41.2 | CU
41.4 | CU
41.5 | CU
42.4 | CU
43 | CU
43.6 | CU
43.7 | CU
44.1 | CU
45.2 | CU
44.9 | CU
45.9 | CU
45.6 | CU
46.2 | CU
45 | CU
45.1 | CU
43.7 | CU
42.9 | CU
43.1 | CU
42.3 | CU
41.1 | CU
41 | CU
39.8 | CU
38.4 | CU
39.4 | CU
39.8 | CU
39.9 | CU
40 | CU
40.1 | CU
40.3 | CU
40.5 | CU
41 | CU
41.3 | CU
41.8 | CU
41.7 | CU
42.2 | CU
42.3 | CU
42 | CU
42.2 | CU
42.1 | CU
42.2 | CU
42.3 | CU
41.8 | CU
42.1 | CU
42.2 | CU
42.1 | CU
42.2 | CU
41.7 | CU
41.9 | CU
42.4 | CU
42.9 | CU
43.6 | CU
44.4 | CU
45.3 | CU
47.1 | CU
45.4 | CU
45.2 | CU
45.8 | CU
45.4 | CU
45.7 | CU
46.3 | CU
45.3 | CU
44.4 | CU
44.8 | CU
44 | CU
44 | CU
43.7 | CU
42 | CU
40.3 | CU
40.4 | CU
40.6 | CU
39.8 | CU
41 | CU
41.7 | CU
41.8 | CU
41.9 | CU
42.2 | CU
42.5 | CU
42.9 | CU
42.7 | CU
42.9 | CU
43 | CU
43.3 | CU
43.3 | CU
43.7 | CU
43.7 | CU
43.6 | CU
42.8 | CU
42.9 | CU
42.9 | CU
43 | CU
43 | CU
43.2 | CU
43.4 | CU
43.2 | CU
43.8 | CU
44.6 | CU
45.7 | CU
46.7 | CU
48.4 | CU
47.4 | CU
47.4 | CU
48.2 | CU
48.2 | CU
48 | CU
47.9 | CU
48.2 | CU
48.2 | CU
48.2 | CU
47.7 | CU
47.2 | CU
46 | CU
44.1 | CU
43.3 | CU
42.4 | CU
42.2 | CU
41.3 | CU
40.6 | CU
41.3 | CU
41.9 | CU
41.8 | CU
42.1 | CU
42.4 | CU
42.8 | CU
42.8 | CU
42.6 | CU
42.9 | CU
43.3 | CU
43.4 | CU
43.6 | CU
43.3 | CU
43.1 | CU
43.1 | CU
43 | CU
43 | CU
43.2 | CU
43.4 | CU
43.5 | CU
43.4 | CU
43.3 | CU
43.7 | CU
44.3 | CU
46 | CU
47.6 | CU
48.1 | CU
48.2 | CU
48.7 | CU
48.8 | CU
49 | CU
49.1 | CU
49.1 | CU
49.6 | CU
48.9 | CU
48 | CU
46.7 | CU
45.3 | CU
42.7 | CU
43.3 | CU
43.3 | CU
42.6 | CU
42.5 | CU
42.6 | CU
43 | CU
42.8 | CU
42.8 | CU
43 | CU
42.9 | CU
43.6 | CU
44.4 | CU
44.4 | CU
45.5 | CU
44.6 | CU
45.2 | CU
45.7 | CU
46.1 | CU
43.9 | CU
44.6 | CU
44.8 | CU
45.1 | CU
46.1 | CU
45.3 | CU
44.4 | CU
43.6 | CU
43.7 | CU
44 | CU
43.7 | CU
43.7 | CU
43.9 | CU
44 | CU
45.7 | CU
45.8 | CU
46.1 | CU
46.6 | CU
48.2 | CU
47.8 | CU
48.3 | CU
48.8 | CU
49.5 | CU
49.9 | CU
50.6 | CU
50.3 | CU
49.6 | CU
50 | CU
49.4 | CU
49.9 | CU
48.8 | CU
49.9 | CU
48.9 | CU
51.1 | CU
39.7 | CU
39.6 | CU
39.4 | CU
39.4 | CU
39.4 | CU
39.2 | CU
39.3 | CU
39 | CU
39 | CU
39.2 | CU
39.1 | CU
39.2 | CU
39.2 | CU
39.3 | CU
39.4 | CU
39.2 | CU
39.1 | CU
39.2 | CU
39.2 | CU
39.3 | CU
39.4 | CU
39.3 | CU
39.2 | CU
39.3 | CU
39.2 | CU
39.2 | CU
39 | CU
39.1 | CU
39.4 | CU
39.6 | CU
39.6 | CU
39.6 | CU
39.6 | CU
39.6 | CU
39.6 | CU
39.7 | CU
40 | CU
39.9 | CU
40.1 | CU
40.3 | CU
40.4 | CU
40.9 | CU
40.7 | CU
40.6 | CU
40.5 | CU
40.1 | CU
38.5 | CU
38.3 | CU
39.7 | CU
39.4 | CU
39.6 | CU
39.8 | CU
40.1 | CU
40.5 | CU
41.3 | CU
41.7 | CU
42.2 | CU
42.2 | CU
41.7 | CU
41.6 | CU
41.6 | CU
41.4 | CU
41.7 | CU
42 | CU
41.7 | CU
42.1 | CU
42.2 | CU
42.2 | CU
42.4 | CU
42.2 | CU
42.3 | CU
42.6 | CU
43.3 | CU
43.2 | CU
44.7 | CU
45.1 | CU
45.1 | CU
46.1 | CU
47.1 | CU
46.2 | CU
45.9 | CU
47.4 | CU
46.8 | CU
46.9 | CU
46.2 | CU
44.2 | CU
43.7 | CU
43.1 | CU
42.7 | CU
42.5 | CU
41.7 | CU
43.1 | CU
41.6 | CU
43 | CU
43.6 | CU
43.3 | CU
43.9 | CU
44.5 | CU
44.6 | CU
45.7 | CU
45.9 | CU
45.9 | CU
44.3 | CU
45.9 | CU
46 | CU
46.5 | CU
45.5 | CU
44.8 | CU
44.8 | CU
45 | CU
44.9 | CU
44.7 | CU
44.9 | CU
45.5 | CU
44.3 | CU
44.6 | CU
44.6 | CU
44.9 | CU
45.4 | CU
45.4 | CU
46 | CU
46.6 | CU
47.1 | CU
46 | CU
46.8 | CU
46 | CU
45.9 | CU
47.9 | CU
47.1 | CU
48.1 | CU
48.2 | CU
46.4 | CU
46.4 | CU
45.5 | CU
44.6 | CU
44 | CU
42.6 | CU
44.3 | CU
44 | CU
44.4 | CU
43.7 | CU
44.1 | CU
44.3 | CU
44.9 | CU
45.3 | CU
45.8 | CU
45 | CU
45.8 | CU
46.1 | CU
45.8 | CU
46.5 | CU
45.1 | CU
45.9 | CU
45.6 | CU
45.6 | CU
44.1 | CU
45 | CU
44.6 | CU
43.7 | CU
45.3 | CU
45.4 | CU
43.8 | CU
44.8 | CU
44.5 | CU
44.4 | CU
44.7 | CU
45.5 | CU
46.7 | CU
48 | CU
46 | CU
48.1 | CU
44.9 | CU
47.8 | CU
47.4 | CU
46.8 | CU
46.7 | CU
45.5 | CU
44.7 | CU
43.9 | CU
42 | CU
42.4 | CU
42.7 | CU
42.5 | CU
42.3 | CU
42.7 | CU
42.7 | CU
43.1 | CU
43.1 | CU
43.8 | CU
43.7 | CU
44 | CU
44.3 | CU
44.3 | CU
43.9 | CU
44.2 | CU
44.2 | CU
44.3 | CU
44.1 | CU
44.4 | CU
44.2 | CU
43.4 | CU
43.3 | CU
43.5 | CU
43.3 | CU
43.6 | CU
44 | CU
43.5 | CU
44 | CU
44 | CU
44.3 | CU
44.6 | CU
45 | CU
45.6 | CU
46.8 | CU
45.9 | CU
46.6 | CU
46.9 | CU
50.8 | CU
47.5 | CU
46.8 | CU
46.9 | CU
46.7 | CU
46.4 | CU
45.4 | CU
44.4 | CU
44.5 | CU
43.7 | CU
43.1 | CU
43.1 | CU
43 | CU
43.3 | CU
43.5 | CU
44 | CU
43.2 | CU
43.8 | CU
43.7 | CU
43.4 | CU
43.4 | CU
44.2 | CU
43.9 | CU
45.3 | CU
45.2 | CU
45.9 | CU
45.3 | CU
44.7 | CU
44.4 | CU
44.4 | CU
45.6 | CU
44.4 | CU
44.4 | CU
45.1 | CU
44.1 | CU
43 | CU
43.8 | CU
44.4 | CU
42.8 | CU
45.5 | CU
45.8 | CU
47.3 | CU
46.4 | CU
47 | CU
46.8 | CU
48.2 | CU
48 | CU
47.9 | CU
48.3 | CU
48.1 | CU
47 | CU
45 | CU
44.9 | CU
44.9 | CU
43.9 | CU
43.5 | CU
42.8 | CU
42.4 | CU
42.2 | CU
43.1 | CU
43.4 | CU
43.4 | CU
44.1 | CU
44.9 | CU
45.3 | CU
45.5 | CU
46.1 | CU
45.1 | CU
46.2 | CU
45.8 | CU
44.6 | CU
45.4 | CU
44.7 | CU
44.8 | CU
43.2 | CU
43.4 | CU
45 | CU
44.6 | CU
43.8 | CU
44.6 | CU
44.5 | CU
44.5 | CU
45.6 | CU
44.7 | CU
45.2 | CU
44.3 | CU
46.1 | CU
47 | CU
46 | CU
46.8 | CU
47.5 | CU
46.7 | CU
46.3 | CU
46.8 | CU
47.7 | CU
47.4 | CU
46.1 | CU
46.4 | CU
46.8 | CU
46.9 | CU
47 | CU
46.5 | CU
44.8 | CU
42.3 | CU
43.3 | CU
43.6 | CU
43.1 | CU
44 | CU
43.5 | CU
43.9 | CU
44.1 | CU
44.2 | CU
44.4 | CU
45 | CU
44.6 | CU
44.8 | CU
44.4 | CU
44.3 | CU
44.8 | CU
44.2 | CU
44.1 | CU
44.4 | CU
44.6 | CU
44.6 | CU
44.4 | CU
44.5 | CU
44.1 | CU
43.9 | CU
43.9 | CU
44.5 | CU
44.5 | CU
45 | CU
46.2 | CU
46.5 | CU
43.8 | CU
46.5 | CU
47.1 | CU
45.6 | CU
45.9 | CU
46.3 | CU
46.4 | CU
48.2 | CU
46.3 | CU
47.6 | CU
47.3 | CU
44.5 | CU
46.4 | CU
45.4 | CU
44.2 | CU
43.8 | CU
43.1 | CU
43.9 | CU
43 | CU
44.2 | CU
45 | CU
44.8 | CU
45.5 | CU
45.5 | CU
45.8 | CU
45 | CU
45.8 | CU
45.8 | CU
44.9 | CU
45.6 | CU
44.9 | CU
44.7 | CU
45.5 | CU
44.6 | CU
44.9 | CU
44.6 | CU
44.3 | CU
43.9 | CU
44.2 | CU
44.4 | CU
44.3 | CU
44.9 | CU
44.7 | CU
45.6 | CU
46.3 | CU
46.5 | CU
47.4 | CU
47.7 | CU
47.8 | CU
48.7 | CU
49.7 | CU
49.1 | CU
50.6 | CU
50.1 | CU
47.7 | CU
48.4 | CU
49.3 | CU
48.3 | CU
46.7 | CU
45.2 | CU
43.4 | CU
42.9 | CU
41.6 | CU
41.2 | CU
40.6 | CU
41.4 | CU
42.3 | CU
42.1 | CU
43.1 | CU
43.3 | CU
43.8 | CU
44.2 | CU
43.9 | CU
43.9 | CU
44.3 | CU
44.4 | CU
44.6 | CU
44.3 | CU
45.1 | CU
44.8 | CU
44.7 | CU
44.7 | CU
45.3 | CU
45.6 | CU
45 | CU
45.1 | CU
45.6 | CU
46 | CU
45.9 | CU
46.3 | CU
47.4 | CU
47.8 | CU
48.3 | CU
49.1 | CU
50.2 | CU
51.3 | CU
48.9 | CU
52.4 | CU
52.4 | CU
53.7 | CU
53.6 | CU
53.6 | CU
53.2 | CU
51.8 | CU
50.4 | CU
48.2 | CU
46.6 | CU
45.8 | CU
44.3 | CU
43.7 | CU
43.4 | CU
44.6 | CU
45.8 | CU
45.9 | CU
45.8 | CU
45.9 | CU
46.1 | CU
46.8 | CU
47.1 | CU
47.4 | CU
47.4 | CU
47.7 | CU
47.4 | CU
46.7 | CU
47.1 | CU
46.6 | CU
47.1 | CU
47 | CU
46.9 | CU
47.2 | CU
47 | CU
47.4 | CU
47.7 | CU
48.1 | CU
48.7 | CU
49.4 | CU
50.8 | CU
51.3 | CU
52 | CU
51.9 | CU
51.8 | CU
52 | CU
52.5 | CU
52.4 | CU
52.1 | CU
52.9 | CU
52.6 | CU
52.8 | CU
52.6 | CU
51.3 | CU
50.1 | CU
47.9 | CU
48.8 | CU
46.6 | CU
45.2 | CU
45.1 | CU
46.3 | CU
43.9 | CU
42.2 | CU
43.6 | CU
45.5 | CU
46 | CU
45.9 | CU
46.6 | CU
46.9 | CU
46.8 | CU
47.1 | CU
47.8 | CU
47.4 | CU
47.5 | CU
47.7 | CU
47.5 | CU
47.7 | CU
47.6 | CU
47.6 | CU
47.1 | CU
47.9 | CU
48.1 | CU
47.4 | CU
47.2 | CU
48.1 | CU
48.9 | CU
49.3 | CU
50.8 | CU
51.4 | CU
51.8 | CU
51.9 | CU
51.7 | CU
52.2 | CU
52.1 | CU
52.7 | CU
52.3 | CU
53.2 | CU
53.1 | CU
52.6 | CU
52.4 | CU
51.5 | CU
49.8 | CU
48.5 | CU
46.9 | CU
45.1 | CU
44.2 | CU
45.4 | CU
45 | CU
43.8 | CU
44.8 | CU
45.8 | CU
45.6 | CU
46.4 | CU
46.5 | CU
46.6 | CU
46.7 | CU
46.9 | CU
46.7 | CU
47.9 | CU
47.6 | CU
47.4 | CU
47.4 | CU
47.4 | CU
47.7 | CU
47.7 | CU
47.7 | CU
48 | CU
48 | CU
48 | CU
48.2 | CU
48 | CU
48.3 | CU
47.8 | CU
50 | CU
51.4 | CU
51.7 | CU
51.6 | CU
51.5 | CU
51.9 | CU
52 | CU
52.1 | CU
52.3 | CU
52.7 | CU
52.6 | CU
52.7 | CU
52.8 | CU
52.9 | CU
52.5 | CU
52 | CU
50.2 | CU
48 | CU
46.1 | CU
45.1 | CU
44 | CU
43.5 | CU
43.9 | CU
45.1 | CU
45.9 | CU
46.8 | CU
46.6 | CU
47.3 | CU
48.3 | CU
48.1 | CU
47.2 | CU
47.8 | CU
47.8 | CU
47.8 | CU
48.2 | CU
49.1 | CU
48.6 | CU
48.2 | CU
47.8 | CU
46.9 | CU
47 | CU
46.9 | CU
47 | CU
47.3 | CU
48.1 | CU
48.5 | CU
49.1 | CU
50.5 | CU
50.9 | CU
50.7 | CU
50.6 | CU
51.8 | CU
50.7 | CU
51.7 | CU
50.2 | CU
51.8 | CU
50.8 | CU
49.6 | CU
49.9 | CU
51.6 | CU
51.2 | CU
50.4 | CU
48.5 | CU
46 | CU
46.5 | CU
43.9 | CU
41.2 | CU
41.3 | CU
41.1 | CU
41.9 | CU
43.2 | CU
43.6 | CU
43.7 | CU
44.6 | CU
44.3 | CU
44.2 | CU
44.7 | CU
44.8 | CU
45.5 | CU
45.8 | CU
45.3 | CU
45 | CU
44.3 | CU
45.5 | CU
45.7 | CU
45.5 | CU
45.1 | CU
44.2 | CU
44.6 | CU
44.8 | CU
44.4 | CU
45 | CU
46 | CU
47.6 | CU
48.3 | CU
49.1 | CU
49.2 | CU
48.9 | CU
49.6 | CU
50.2 | CU
50.2 | CU
50.1 | CU
50.8 | CU
50.6 | CU
50.6 | CU
50.3 | CU
49.8 | CU
48.3 | CU
48 | CU
46.4 | CU
45.2 | CU
43 | CU
42.1 | CU
41.2 | CU
41.3 | CU
42.5 | CU
43.5 | CU
43.6 | CU
43.7 | CU
43.6 | CU
44.6 | CU
44.6 | CU
44.3 | CU
44.6 | CU
45.2 | CU
45.2 | CU
44.8 | CU
45.1 | CU
45.1 | CU
44.9 | CU
45.1 | CU
45.4 | CU
44.8 | CU
44.8 | CU
44.4 | CU
44.9 | CU
45.4 | CU
46 | CU
46.6 | CU
48.1 | CU
48.7 | CU
48.5 | CU
48.2 | CU
49 | CU
49.6 | CU
48.7 | CU
47.6 | CU
50.2 | CU
50.6 | CU
50.5 | CU
51.1 | CU
50.3 | CU
49.3 | CU
49.1 | CU
47.6 | CU
46.1 | CU
45.7 | CU
40.5 | CU
43 | CU
41.8 | CU
41.9 | CU
42.3 | CU
43.7 | CU
44.3 | CU
44.9 | CU
45.4 | CU
45.7 | CU
45.6 | CU
45.7 | CU
45.9 | CU
45.4 | CU
46.2 | CU
45.8 | CU
46 | CU
45.7 | CU
45.6 | CU
46.2 | CU
45.5 | CU
45.9 | CU
45.8 | CU
45.6 | CU
45.8 | CU
46 | CU
46.3 | CU
46.5 | CU
47.1 | CU
48.6 | CU
48.5 | CU
49.5 | CU
50 | CU
49 | CU
50.7 | CU
50.8 | CU
50 | CU
51.3 | CU
50.4 | CU
50.9 | CU
51.4 | CU
49.5 | CU
47.9 | CU
47.1 | CU
46.2 | CU
44.9 | CU
44.4 | CU
42.5 | CU
42.3 | CU
42.5 | CU
44.1 | CU
45.3 | CU
45.3 | CU
45.4 | CU
45.4 | CU
45.6 | CU
46.3 | CU
46.3 | CU
46.7 | CU
47.1 | CU
46.9 | CU
46.9 | CU
46.5 | CU
46.9 | CU
46.4 | CU
45.7 | CU
45.4 | CU
45.5 | CU
45.7 | CU
45.9 | CU
45.6 | CU
46 | CU
46.4 | CU
46.8 | CU
46.9 | CU
47.7 | CU
48.7 | CU
49.9 | CU
49.3 | CU
49.6 | CU
50.3 | CU
49.9 | CU
50.8 | CU
50.9 | CU
50.6 | CU
51 | CU
50.5 | CU
49.4 | CU
48.8 | CU
47.3 | CU
45.3 | CU
43.5 | CU
43.4 | CU
42.7 | CU
43 | CU
42.4 | CU
42.8 | CU
43.4 | CU
43.8 | CU
43.7 | CU
44.1 | CU
44.5 | CU
44.1 | CU
44.7 | CU
45 | CU
45 | CU
45.5 | CU
45.6 | CU
45.5 | CU
44.6 | CU
44.7 | CU
45.1 | CU
45.8 | CU
45.9 | CU
45.3 | CU
45.7 | CU
46 | CU
45.7 | CU
46.2 | CU
45.8 | CU
46.8 | CU
47.8 | CU
49.3 | CU
50.8 | CU
51.6 | CU
50.9 | CU
51.1 | CU
51.8 | CU
51.4 | CU
52.1 | CU
52 | CU
52.4 | CU
51.9 | CU
51.5 | CU
50.2 | CU
48.5 | CU
46.7 | CU
44.6 | CU
43.8 | CU
42.4 | CU
42.3 | CU
41.6 | CU
41.7 | CU
42.4 | CU
42.5 | CU
42.9 | CU
42.6 | CU
42.9 | CU
43.2 | CU
43.6 | CU
43.9 | CU
44 | CU
44 | CU
43.9 | CU
43.8 | CU
43.8 | CU
43.8 | CU
44.2 | CU
44.1 | CU
43.8 | CU
44 | CU
43.6 | CU
44.1 | CU
43.8 | CU
44.7 | CU
45.2 | CU
45.2 | CU
45.3 | CU
46.7 | CU
49 | CU
51.2 | CU
51.7 | CU
51.6 | CU
51.6 | CU
51.7 | CU
52 | CU
52.8 | CU
52.6 | CU
52.6 | CU
50.5 | CU
50.8 | CU
48.1 | CU
47.3 | CU
44.8 | CU
43.2 | CU
43.7 | CU
42.7 | CU
43 | CU
42.8 | CU
44.7 | CU
45 | CU
45.8 | CU
45.2 | CU
46 | CU
46.8 | CU
46.7 | CU
47.3 | CU
47.3 | CU
48 | CU
48.5 | CU
48.4 | CU
48 | CU
47.6 | CU
47.6 | CU
48.2 | CU
48 | CU
47.7 | CU
48.4 | CU
48.2 | CU
48 | CU
48.1 | CU
48.9 | CU
49.2 | CU
49.9 | CU
51.4 | CU
52.4 | CU
53.7 | CU
56 | CU
54.1 | CU
54.3 | CU
54.4 | CU
54.6 | CU
54.5 | CU
54.8 | CU
55.6 | CU
52.8 | CU
43.8 | CU
52.8 | CU
52.9 | CU
53.2 | CU
48.2 | CU
48.1 | CU
47.9 | CU
47.8 | CU
47.9 | CU
47.7 | CU
47.7 | CU
47.6 | CU
47.5 | CU
47.5 | CU
47.6 | CU
47.6 | CU
47.7 | CU
47.7 | CU
47.5 | CU
47.6 | CU
47.3 | CU
47.6 | CU
47.5 | CU
47.5 | CU
47.6 | CU
47.7 | CU
47.4 | CU
47.6 | CU
47.4 | CU
47.3 | CU
47.4 | CU
47.4 | CU
47.2 | CU
47 | CU
47.5 | CU
47.2 | CU
47.6 | CU
47.3 | CU
47.3 | CU
47.4 | CU
47.4 | CU
47.3 | CU
47.3 | CU
47.7 | CU
47.7 | CU
47.6 | CU
47.9 | CU
48.3 | CU
48.6 | CU
48.4 | CU
48.6 | CU
48.3 | CU
48 | CU
47.7 | CU
47.7 | CU
47.1 | CU
47.2 | CU
47.1 | CU
47 | CU
47.1 | CU
47.5 | CU
47.1 | CU
47.3 | CU
47 | CU
47 | CU
47.1 | CU
47.1 | CU
47 | CU
47.2 | CU
47.4 | CU
47.1 | CU
47 | CU
47.1 | CU
47.1 | CU
47.1 | CU
47.1 | CU
47.1 | CU
47.1 | CU
46.9 | CU
47.2 | CU
46.9 | CU
47.2 | CU
47.8 | CU
47.3 | CU
47.5 | CU
49.3 | CU
49.5 | CU
50.4 | CU
50.1 | CU
49.5 | CU
50.4 | CU
50.5 | CU
50.1 | CU
48.5 | CU
47.4 | CU
46.6 | CU
43 | CU
40.9 | CU
40.7 | CU
40 | CU
40.6 | CU
42.1 | CU
42.2 | CU
42.4 | CU
42.3 | CU
42.5 | CU
42.7 | CU
43.1 | CU
43.3 | CU
43.4 | CU
43.7 | CU
43.5 | CU
43.3 | CU
43.6 | CU
44 | CU
44.5 | CU
44.7 | CU
44.5 | CU
44.4 | CU
44.4 | CU
44.4 | CU
43.6 | CU
43.6 | CU
44 | CU
44 | CU
45 | CU
46.4 | CU
48 | CU
49.4 | CU
49.2 | CU
49.1 | CU
49.4 | CU
49.9 | CU
50.1 | CU
49.9 | CU
50.2 | CU
50.3 | CU
50.2 | CU
52 | CU
51.3 | CU
50.2 | CU
48.5 | CU
46.5 | CU
44.5 | CU
43.5 | CU
41.5 | CU
41.1 | CU
42.5 | CU
42.5 | CU
43 | CU
42.4 | CU
43 | CU
43.4 | CU
43.7 | CU
43.8 | CU
44.3 | CU
45.1 | CU
45.2 | CU
44.5 | CU
44.9 | CU
44.8 | CU
45.6 | CU
45.7 | CU
44.5 | CU
45.3 | CU
45.5 | CU
45.1 | CU
45.7 | CU
45.7 | CU
46.3 | CU
46.1 | CU
46.6 | CU
48.2 | CU
50 | CU
50.3 | CU
49.7 | CU
49.5 | CU
49.8 | CU
50.5 | CU
50.1 | CU
50.3 | CU
51.1 | CU
51.3 | CU
52.2 | CU
52 | CU
51.1 | CU
49 | CU
48.7 | CU
45.8 | CU
44.7 | CU
42.7 | CU
43.2 | CU
43.2 | CU
43.9 | CU
44.1 | CU
45.6 | CU
45.5 | CU
45.4 | CU
45.4 | CU
46.1 | CU
46.1 | CU
45.7 | CU
46.3 | CU
46.2 | CU
46.5 | CU
46.3 | CU
46.4 | CU
46 | CU
46.2 | CU
46.5 | CU
45.7 | CU
45.6 | CU
45.9 | CU
45.8 | CU
45.3 | CU
45.5 | CU
44.9 | CU
46.1 | CU
45.9 | CU
46.9 | CU
47.3 | CU
48.3 | CU
48.4 | CU
48.9 | CU
49.2 | CU
48 | CU
48.7 | CU
50.3 | CU
49.1 | CU
50.4 | CU
49.4 | CU
48.3 | CU
47.7 | CU
48.3 | CU
44.8 | CU
46.3 | CU
44 | CU
42.3 | CU
41.3 | CU
42.5 | CU
42.5 | CU
42.7 | CU
43.4 | CU
44.1 | CU
44.7 | CU
44.5 | CU
43.9 | CU
44.1 | CU
44.3 | CU
44.1 | CU
44.6 | CU
44.6 | CU
44.5 | CU
44.8 | CU
44.6 | CU
44.4 | CU
44 | CU
44.2 | CU
43.6 | CU
43.7 | CU
44.2 | CU
43.9 | CU
44.2 | CU
44.7 | CU
45 | CU
46.4 | CU
48.1 | CU
49.1 | CU
47.9 | CU
50.5 | CU
49.4 | CU
49.3 | CU
47.6 | CU
46 | CU
49.1 | CU
50.8 | CU
46.4 | CU
48.8 | CU
47.7 | CU
45.7 | CU
43 | CU
43.7 | CU
41.9 | CU
42.6 | CU
43.3 | CU
42.6 | CU
42.6 | CU
43.7 | CU
44.2 | CU
44 | CU
44.4 | CU
45.1 | CU
45.3 | CU
45.8 | CU
45.5 | CU
46 | CU
45.9 | CU
45.8 | CU
45.1 | CU
45.8 | CU
45.7 | CU
45.8 | CU
45.5 | CU
45.5 | CU
45.1 | CU
45.4 | CU
45.6 | CU
45.7 | CU
45.9 | CU
46.3 | CU
47.6 | CU
48.5 | CU
49.9 | CU
50.3 | CU
50.4 | CU
49.7 | CU
50 | CU
50.6 | CU
51 | CU
50.3 | CU
51 | CU
50.5 | CU
51.2 | CU
50 | CU
47.9 | CU
45.8 | CU
43.7 | CU
42.5 | CU
41 | CU
40.9 | CU
41.1 | CU
40.6 | CU
41.1 | CU
42.3 | CU
42.6 | CU
43.1 | CU
43.3 | CU
43.3 | CU
43.4 | CU
43.6 | CU
43.6 | CU
44.2 | CU
43.9 | CU
43.9 | CU
43.9 | CU
44.5 | CU
44.2 | CU
44.2 | CU
44.1 | CU
43.6 | CU
43.2 | CU
44.2 | CU
44.7 | CU
44.7 | CU
44.9 | CU
46.6 | CU
47.1 | CU
48.7 | CU
49.8 | CU
49.5 | CU
49 | CU
49.5 | CU
49.6 | CU
50.4 | CU
50.3 | CU
50 | CU
50.3 | CU
50.9 | CU
49.8 | CU
49.5 | CU
47.8 | CU
46.2 | CU
44.3 | CU
42.3 | CU
41.3 | CU
40.7 | CU
40.5 | CU
40.8 | CU
40.6 | CU
41.2 | CU
41.2 | CU
41.4 | CU
41.9 | CU
42.2 | CU
42.7 | CU
43.2 | CU
43.8 | CU
43.7 | CU
43 | CU
43.2 | CU
44 | CU
44.1 | CU
43.9 | CU
43.5 | CU
43.9 | CU
43.9 | CU
44.2 | CU
44.7 | CU
44.2 | CU
45.2 | CU
45.1 | CU
45 | CU
46 | CU
46.8 | CU
48.6 | CU
48.6 | CU
48.9 | CU
49.2 | CU
49.2 | CU
49.4 | CU
49.6 | CU
49.7 | CU
50.4 | CU
50.7 | CU
50.3 | CU
49.7 | CU
48.3 | CU
46.8 | CU
44.9 | CU
44.7 | CU
43.7 | CU
43 | CU
42.3 | CU
42.6 | CU
42.2 | CU
43.7 | CU
44.2 | CU
44.4 | CU
44.5 | CU
45 | CU
44.7 | CU
44.6 | CU
44.8 | CU
45.1 | CU
45.4 | CU
45.7 | CU
45.7 | CU
45.7 | CU
44.7 | CU
45 | CU
44.7 | CU
44.7 | CU
44.6 | CU
44.7 | CU
44.8 | CU
44.9 | CU
45.3 | CU
45.7 | CU
45.9 | CU
46.4 | CU
47.5 | CU
48.6 | CU
49 | CU
49.1 | CU
50.3 | CU
49.6 | CU
48.9 | CU
51.2 | CU
50.6 | CU
50.3 | CU
49.9 | CU
48.1 | CU
48.8 | CU
49.2 | CU
47.5 | CU
45.8 | CU
45.1 | CU
43.7 | CU
43.1 | CU
42.5 | CU
42.3 | CU
42.8 | CU
43 | CU
43.6 | CU
43.9 | CU
43.6 | CU
43.9 | CU
44.1 | CU
44.2 | CU
45.2 | CU
44.8 | CU
44.9 | CU
44.9 | CU
44.9 | CU
45.2 | CU
45.2 | CU
45.3 | CU
45.3 | CU
45.5 | CU
45.7 | CU
45.7 | CU
45.3 | CU
45.7 | CU
46.4 | CU
46.6 | CU
48 | CU
49 | CU
49.6 | CU
49.8 | CU
50.3 | CU
50.7 | CU
50.9 | CU
51.4 | CU
50.9 | CU
51.2 | CU
51.4 | CU
50.8 | CU
51.2 | CU
50.4 | CU
49.1 | CU
47.6 | CU
46.4 | CU
44 | CU
43.6 | CU
42.5 | CU
41.8 | CU
42.2 | CU
42.8 | CU
43.1 | CU
43 | CU
43.4 | CU
43.5 | CU
43.9 | CU
44.4 | CU
44.1 | CU
44.5 | CU
44.6 | CU
44.9 | CU
45 | CU
44.8 | CU
45.2 | CU
45.4 | CU
45 | CU
44.9 | CU
45.5 | CU
45.2 | CU
45.4 | CU
45.3 | CU
45.4 | CU
45.9 | CU
47.1 | CU
48.2 | CU
49.8 | CU
51.3 | CU
49.8 | CU
49.7 | CU
49.2 | CU
49.3 | CU
51.6 | CU
51.6 | CU
50.9 | CU
52 | CU
51.6 | CU
50.9 | CU
49.4 | CU
47.1 | CU
46.2 | CU
43.8 | CU
42.3 | CU
41.4 | CU
40.7 | CU
40.3 | CU
41 | CU
41 | CU
39 | CU
39.4 | CU
39.4 | CU
40.4 | CU
41.6 | CU
42.7 | CU
43 | CU
43.5 | CU
43.2 | CU
43.8 | CU
43.6 | CU
43 | CU
43.1 | CU
43.2 | CU
43.2 | CU
43.5 | CU
42.4 | CU
43.1 | CU
43 | CU
42.8 | CU
42.6 | CU
43.8 | CU
45.7 | CU
49.3 | CU
50.3 | CU
50 | CU
49.2 | CU
49.4 | CU
50.3 | CU
49.9 | CU
50.1 | CU
50.4 | CU
51.2 | CU
51.2 | CU
50.8 | CU
50.3 | CU
47.5 | CU
45.3 | CU
42.8 | CU
43 | CU
42.8 | CU
42.3 | CU
41.2 | CU
40.9 | CU
41.1 | CU
41.1 | CU
40.1 | CU
40.1 | CU
39.7 | CU
39.8 | CU
40.3 | CU
41 | CU
41.5 | CU
41.1 | CU
40.8 | CU
40.5 | CU
40.5 | CU
39.9 | CU
39.9 | CU
40.3 | CU
40.1 | CU
40.2 | CU
40.3 | CU
40.8 | CU
41.6 | CU
41.9 | CU
42.4 | CU
43 | CU
43.5 | CU
43.5 | CU
44 | CU
47.5 | CU
49.4 | CU
49.2 | CU
49.5 | CU
49.9 | CU
50.1 | CU
50.3 | CU
50.3 | CU
50.2 | CU
49.7 | CU
48.3 | CU
47.4 | CU
45.7 | CU
44.8 | CU
44.5 | CU
43.3 | CU
41.4 | CU
40.7 | CU
40.3 | CU
40.4 | CU
41.4 | CU
41.8 | CU
41.6 | CU
40.7 | CU
40.2 | CU
40.7 | CU
40.8 | CU
40.8 | CU
40.7 | CU
41.3 | CU
41.9 | CU
42 | CU
43.3 | CU
43.8 | CU
43.9 | CU
44.1 | CU
44.5 | CU
44.4 | CU
44.1 | CU
44.5 | CU
44.2 | CU
43.5 | CU
43.9 | CU
44.9 | CU
45.3 | CU
46.6 | CU
48.7 | CU
50.6 | CU
50.8 | CU
49.9 | CU
51.5 | CU
50.9 | CU
51.2 | CU
51.8 | CU
51 | CU
51 | CU
50.3 | CU
48.8 | CU
48.2 | CU
46.1 | CU
44.7 | CU
43.7 | CU
43.2 | CU
42.9 | CU
43.4 | CU
44.3 | CU
44.4 | CU
44.5 | CU
43.7 | CU
44.2 | CU
44.8 | CU
45.8 | CU
46.3 | CU
46 | CU
46.2 | CU
46.2 | CU
46.7 | CU
46.4 | CU
46.4 | CU
46.4 | CU
46.8 | CU
46.5 | CU
46.8 | CU
46.8 | CU
46.4 | CU
46.4 | CU
46.4 | CU
46.7 | CU
46.4 | CU
46.5 | CU
47.9 | CU
48.6 | CU
49.1 | CU
50.2 | CU
51.4 | CU
51.4 | CU
51.5 | CU
52 | CU
52.1 | CU
52.9 | CU
52.7 | CU
52.4 | CU
51.3 | CU
49.9 | CU
50.2 | CU
48.8 | CU
47.5 | CU
46.8 | CU
46.3 | CU
45.5 | CU
45.4 | CU
45.3 | CU
45.7 | CU
45.4 | CU
45.7 | CU
45.4 | CU
45.9 | CU
46.2 | CU
46.7 | CU
47.1 | CU
47.3 | CU
47.4 | CU
47.4 | CU
47.3 | CU
47.3 | CU
47.1 | CU
46.8 | CU
46.9 | CU
47 | CU
46.3 | CU
46.4 | CU
46.7 | CU
47.4 | CU
48 | CU
48 | CU
47.8 | CU
48 | CU
48.1 | CU
48.8 | CU
50.4 | CU
50.9 | CU
52.1 | CU
52 | CU
52.5 | CU
52.9 | CU
53 | CU
54.6 | CU
55.4 | CU
3.9 | CU
1.6 | CU
11.9 | CU
49 | CU
47 | CU
46.2 | CU
44.9 | CU
44.9 | CU
44 | CU
44.7 | CU
46.3 | CU
46 | CU
46.3 | CU
46.7 | CU
47 | CU
47.5 | CU
47.4 | CU
48 | CU
47.8 | CU
48.4 | CU
48.1 | CU
47.8 | CU
47.5 | CU
47.7 | CU
47.8 | CU
47.6 | CU
48 | CU
47.8 | CU
48.1 | CU
47.3 | CU
46.9 | CU
47.4 | CU
46.6 | CU
46.7 | CU
47.2 | CU
47.8 | CU
47 | CU
47.5 | CU
48.3 | CU
49 | CU
49.8 | CU
49.2 | CU
50.3 | CU
50.4 | CU
51.2 | CU
51.2 | CU
51.5 | CU
50.9 | CU
47.4 | CU
48.7 | CU
45.3 | CU
44.8 | CU
44.7 | CU
43.7 | CU
44.5 | CU
44.8 | CU
46.4 | CU
46.1 | CU
45.9 | CU
45.7 | CU
46.3 | CU
47.2 | CU
47.5 | CU
47.5 | CU
48.1 | CU
48 | CU
47.8 | CU
47.7 | CU
47.7 | CU
47.7 | CU
47.2 | CU
47.1 | CU
47 | CU
47.4 | CU
47.5 | CU
47.7 | CU
47.1 | CU
47.1 | CU
47.3 | CU
47.2 | CU
48 | CU
47.9 | CU
48.8 | CU
49.8 | CU
50.8 | CU
50.3 | CU
51.3 | CU
51.9 | CU
51.5 | CU
51.6 | CU
52.4 | CU
52.6 | CU
51.5 | CU
52.9 | CU
53.3 | CU
52.5 | CU
52 | CU
51.1 | CU
46.9 | CU
46.4 | CU
46.3 | CU
47.4 | CU
48.4 | CU
48.6 | CU
49.7 | CU
50 | CU
49.6 | CU
50 | CU
49.7 | CU
49.1 | CU
49.1 | CU
48.7 | CU
48.8 | CU
48.7 | CU
48.1 | CU
48.1 | CU
48.4 | CU
47.2 | CU
47.3 | CU
47.5 | CU
46.5 | CU
47.8 | CU
47.4 | CU
48 | CU
49 | CU
47.7 | CU
48.6 | CU
48.3 | CU
49 | CU
50.8 | CU
50.5 | CU
50.8 | CU
50.6 | CU
52.2 | CU
51.6 | CU
51.8 | CU
51.4 | CU
51.9 | CU
50.9 | CU
49 | CU
48.9 | CU
48.4 | CU
47.4 | CU
47.5 | CU
45.9 | CU
42.6 | CU
41.1 | CU
42.5 | CU
42.9 | CU
45.8 | CU
45.8 | CU
45.8 | CU
45.8 | CU
45.8 | CU
45.8 | CU
45.8 | CU
45.8 | CU
45.8 | CU
45.8 | CU
44.6 | CU
44.3 | CU
43.8 | CU
44.6 | CU
45.2 | CU
44.6 | CU
43.9 | CU
44.3 | CU
44.2 | CU
43.7 | CU
43.5 | CU
44 | CU
44 | CU
43.7 | CU
43.5 | CU
43.5 | CU
43 | CU
43.2 | CU
43.3 | CU
43.5 | CU
44.6 | CU
44.5 | CU
45.5 | CU
46.1 | CU
47.8 | CU
48.9 | CU
49.9 | CU
49.8 | CU
49.6 | CU
49.5 | CU
49.1 | CU
49.6 | CU
49.1 | CU
50.3 | CU
49.7 | CU
49.8 | CU
49.7 | CU
49.5 | CU
49.1 | CU
47.5 | CU
46.2 | CU
45 | CU
43.3 | CU
42 | CU
41.7 | CU
42.6 | CU
43 | CU
43.6 | CU
44 | CU
44.4 | CU
44.1 | CU
45 | CU
45.4 | CU
45.7 | CU
45.6 | CU
45.7 | CU
45.6 | CU
45.6 | CU
46.2 | CU
45.6 | CU
45.9 | CU
45.1 | CU
45.2 | CU
45.3 | CU
45.8 | CU
45.7 | CU
46.5 | CU
46.2 | CU
46.8 | CU
47.1 | CU
48.4 | CU
49.4 | CU
50.7 | CU
50.7 | CU
50.5 | CU
50.5 | CU
51 | CU
50.9 | CU
51.2 | CU
51.2 | CU
51.3 | CU
51.8 | CU
51.5 | CU
51.2 | CU
49.7 | CU
47.6 | CU
46.1 | CU
44.5 | CU
43.4 | CU
42.7 | CU
41.8 | CU
42 | CU
42.2 | CU
42.5 | CU
43.3 | CU
44.1 | CU
44.4 | CU
44.8 | CU
45 | CU
45.3 | CU
45 | CU
45.2 | CU
45.7 | CU
44.7 | CU
44.7 | CU
45 | CU
45.2 | CU
45.1 | CU
45.1 | CU
45.1 | CU
45.4 | CU
45.2 | CU
45.9 | CU
46.3 | CU
46.7 | CU
47.4 | CU
47.9 | CU
49.1 | CU
50 | CU
50.9 | CU
50.5 | CU
51.1 | CU
50.6 | CU
50.9 | CU
51.7 | CU
51.5 | CU
51.4 | CU
51.9 | CU
52 | CU
51.5 | CU
50.3 | CU
49.4 | CU
47.8 | CU
46.3 | CU
44.6 | CU
43.5 | CU
42.6 | CU
42.6 | CU
43.3 | CU
43.6 | CU
43.5 | CU
43.6 | CU
44 | CU
45 | CU
45.5 | CU
45.7 | CU
46.2 | CU
46.1 | CU
46.1 | CU
46 | CU
46.1 | CU
45.9 | CU
45.7 | CU
46.2 | CU
45.6 | CU
45.9 | CU
45.7 | CU
46.3 | CU
46.9 | CU
46.5 | CU
47.3 | CU
48.1 | CU
48.9 | CU
51.1 | CU
52 | CU
51.7 | CU
51 | CU
51.1 | CU
51.6 | CU
51.9 | CU
52 | CU
51.7 | CU
52 | CU
52.4 | CU
52.1 | CU
52.1 | CU
51.4 | CU
49.1 | CU
49.6 | CU
48.2 | CU
47.4 | CU
46.4 | CU
46.5 | CU
46.8 | CU
46.3 | CU
46.9 | CU
46.9 | CU
47.4 | CU
48 | CU
48.1 | CU
48.4 | CU
48.6 | CU
48.4 | CU
49.1 | CU
49.2 | CU
48.5 | CU
47.9 | CU
48.5 | CU
48.6 | CU
48.1 | CU
48.1 | CU
48.1 | CU
48 | CU
47.8 | CU
48.2 | CU
48.7 | CU
49.2 | CU
50 | CU
50.7 | CU
51.2 | CU
51.8 | CU
52.4 | CU
52.7 | CU
52.2 | CU
52.7 | CU
53.5 | CU
53 | CU
52.7 | CU
53.4 | CU
52.7 | CU
52.3 | CU
53.5 | CU
52.5 | CU
50.3 | CU
47.8 | CU
44.3 | CU
43.9 | CU
43.9 | CU
44.2 | CU
43.9 | CU
44.1 | CU
44.7 | CU
45.6 | CU
45.4 | CU
45.4 | CU
45.7 | CU
45.9 | CU
46.4 | CU
46.9 | CU
47.1 | CU
46.4 | CU
47.2 | CU
46.4 | CU
46.4 | CU
45.9 | CU
45.5 | CU
45.7 | CU
45.9 | CU
46.7 | CU
47 | CU
47.5 | CU
47.9 | CU
48.3 | CU
49 | CU
50 | CU
50.7 | CU
51.1 | CU
51 | CU
50.3 | CU
50.9 | CU
50.7 | CU
50.9 | CU
51.9 | CU
51.8 | CU
51.5 | CU
51.1 | CU
49.2 | CU
46.5 | CU
46.2 | CU
43.3 | CU
40.7 | CU
41.8 | CU
41.3 | CU
42.2 | CU
41.6 | CU
41.9 | CU
42.1 | CU
42.2 | CU
42.8 | CU
42.6 | CU
42.9 | CU
43.2 | CU
43.4 | CU
43.1 | CU
43.3 | CU
43.6 | CU
43.4 | CU
43.1 | CU
44.3 | CU
43.8 | CU
43.2 | CU
42.7 | CU
43.1 | CU
43 | CU
43.6 | CU
43.5 | CU
44.1 | CU
45 | CU
46.4 | CU
47.7 | CU
49 | CU
49.2 | CU
48.8 | CU
49.2 | CU
49.5 | CU
49.2 | CU
49.4 | CU
47.9 | CU
51.3 | CU
48.9 | CU
47.6 | CU
48.4 | CU
47.7 | CU
45.8 | CU
43.7 | CU
42.9 | CU
42.5 | CU
41.2 | CU
41.2 | CU
41.1 | CU
40.7 | CU
41.8 | CU
42.3 | CU
42.2 | CU
42.4 | CU
42.7 | CU
42.8 | CU
43.4 | CU
42.9 | CU
43.4 | CU
43.9 | CU
43.7 | CU
43.5 | CU
43.3 | CU
43.5 | CU
43.8 | CU
43.2 | CU
43 | CU
43.3 | CU
43.8 | CU
43.2 | CU
44 | CU
44.4 | CU
44.4 | CU
44.8 | CU
45.7 | CU
46.7 | CU
47.4 | CU
48.9 | CU
48.3 | CU
49.4 | CU
47.8 | CU
48.5 | CU
49.1 | CU
50.1 | CU
49.3 | CU
49.5 | CU
47.6 | CU
46 | CU
44.2 | CU
42.7 | CU
41.8 | CU
40.4 | CU
40.6 | CU
40.4 | CU
39.5 | CU
40.1 | CU
40.8 | CU
40.9 | CU
41 | CU
41.5 | CU
41.9 | CU
42.5 | CU
42.3 | CU
42.7 | CU
42.9 | CU
42.9 | CU
42.6 | CU
43 | CU
43.1 | CU
43.4 | CU
43.1 | CU
43.3 | CU
43.1 | CU
43.2 | CU
43 | CU
43.4 | CU
44 | CU
44.7 | CU
45.1 | CU
45.8 | CU
47 | CU
48.4 | CU
48.9 | CU
48.5 | CU
48.8 | CU
49.3 | CU
49.3 | CU
49.8 | CU
49.9 | CU
50.2 | CU
50.6 | CU
49.6 | CU
49.1 | CU
47.7 | CU
45.6 | CU
44 | CU
42.7 | CU
41.4 | CU
41.2 | CU
41.1 | CU
40.7 | CU
41.3 | CU
41.7 | CU
41.4 | CU
42.9 | CU
43.2 | CU
43.2 | CU
42.9 | CU
43.3 | CU
43.8 | CU
43.5 | CU
43.3 | CU
43 | CU
42.9 | CU
43 | CU
43.2 | CU
43.3 | CU
43.4 | CU
43.7 | CU
44.4 | CU
45.4 | CU
46 | CU
47.7 | CU
49 | CU
48.5 | CU
48.3 | CU
48.3 | CU
48.3 | CU
47.4 | CU
46.7 | CU
46 | CU
45.6 | CU
45 | CU
44.9 | CU
43.6 | CU
43.1 | CU
42.3 | CU
42.4 | CU
42.9 | CU
42.3 | CU
42.4 | CU
42.5 | CU
41.6 | CU
42.8 | CU
42.8 | CU
42.9 | CU
42.8 | CU
43.5 | CU
43.8 | CU
44.6 | CU
44 | CU
43.9 | CU
44.5 | CU
43.1 | CU
42.4 | CU
42.1 | CU
42.2 | CU
42.7 | CU
42.1 | CU
41.9 | CU
41.4 | CU
41.5 | CU
41.3 | CU
41.1 | CU
40.9 | CU
41.2 | CU
41.9 | CU
43.9 | CU
45.9 | CU
46.5 | CU
48.9 | CU
47.5 | CU
46.2 | CU
46.3 | CU
45.3 | CU
45.1 | CU
44.4 | CU
44.4 | CU
44.1 | CU
43.1 | CU
42.6 | CU
41.5 | CU
41.7 | CU
40.8 | CU
40.5 | CU
40.5 | CU
41.2 | CU
41.3 | CU
41.4 | CU
41.3 | CU
42 | CU
42.5 | CU
42.9 | CU
42.9 | CU
42.7 | CU
42.7 | CU
42.5 | CU
42.5 | CU
42.5 | CU
42.3 | CU
42.2 | CU
41.9 | CU
42.2 | CU
42.4 | CU
42 | CU
41.8 | CU
42 | CU
42.1 | CU
41.8 | CU
42.4 | CU
42.7 | CU
43.2 | CU
43.4 | CU
44.3 | CU
45.4 | CU
46.1 | CU
47.9 | CU
48 | CU
48.4 | CU
48.2 | CU
48.7 | CU
48.4 | CU
47.7 | CU
46.9 | CU
46.3 | CU
45.5 | CU
44.9 | CU
43.8 | CU
43.3 | CU
42.1 | CU
42.7 | CU
43.2 | CU
42 | CU
43.2 | CU
44.1 | CU
44 | CU
44.6 | CU
45 | CU
45.5 | CU
46.4 | CU
47 | CU
46 | CU
45.9 | CU
46.1 | CU
46.4 | CU
46.7 | CU
47.1 | CU
47.5 | CU
46.6 | CU
46.6 | CU
46.7 | CU
46.4 | CU
47.5 | CU
48.8 | CU
49.8 | CU
50.9 | CU
54 | CU
55 | CU
51.3 | CU
51.3 | CU
50.8 | CU
50.9 | CU
51.6 | CU
52 | CU
52 | CU
52.5 | CU
52.8 | CU
53 | CU
52.5 | CU
52.3 | CU
53.3 | CU
57.6 | CU
47 | CU
46.8 | CU
46.7 | CU
46.6 | CU
46.6 | CU
46.1 | CU
46 | CU
46 | CU
46 | CU
45.9 | CU
45.9 | CU
46 | CU
45.9 | CU
46.1 | CU
46.1 | CU
46.2 | CU
46.1 | CU
46.2 | CU
46.2 | CU
46.2 | CU
46.1 | CU
46.1 | CU
46.1 | CU
46 | CU
46.2 | CU
46.2 | CU
46.1 | CU
45.9 | CU
45.7 | CU
45.7 | CU
46.3 | CU
45.9 | CU
47.4 | CU
46.7 | CU
47.1 | CU
46.8 | CU
47.2 | CU
48 | CU
47.3 | CU
47.3 | CU
46.6 | CU
45.1 | CU
44.8 | CU
43.6 | CU
41.1 | CU
40.2 | CU
39.8 | CU
39.3 | CU
39.7 | CU
40.1 | CU
40 | CU
40 | CU
40.4 | CU
40.8 | CU
41 | CU
41.8 | CU
41.7 | CU
41.8 | CU
41.6 | CU
41.7 | CU
41.5 | CU
41.3 | CU
40.7 | CU
40.8 | CU
40.5 | CU
40.7 | CU
40.8 | CU
40.8 | CU
41 | CU
40.6 | CU
40.5 | CU
40.8 | CU
40.9 | CU
40.7 | CU
41.2 | CU
41.4 | CU
41.7 | CU
42.2 | CU
42.9 | CU
44 | CU
45.3 | CU
46 | CU
45.3 | CU
46.1 | CU
45.8 | CU
45.8 | CU
46.4 | CU
47.3 | CU
45.8 | CU
44.2 | CU
42.8 | CU
42 | CU
40.8 | CU
40.3 | CU
39.3 | CU
40.3 | CU
40 | CU
40.4 | CU
41 | CU
40.8 | CU
41 | CU
41.4 | CU
42.1 | CU
42 | CU
42.3 | CU
42 | CU
41.5 | CU
41.7 | CU
41.7 | CU
41.6 | CU
41.3 | CU
41.5 | CU
41.2 | CU
41.2 | CU
41.4 | CU
41.6 | CU
41.7 | CU
42.2 | CU
42.8 | CU
43.3 | CU
44.8 | CU
45.7 | CU
46.9 | CU
46.6 | CU
46.9 | CU
48 | CU
47.8 | CU
48 | CU
46.6 | CU
46.8 | CU
46.8 | CU
47.4 | CU
45.9 | CU
44.9 | CU
43.2 | CU
41.6 | CU
40.7 | CU
40.8 | CU
40.4 | CU
40.6 | CU
41.8 | CU
42 | CU
42.1 | CU
42.6 | CU
43.3 | CU
43.4 | CU
43.7 | CU
43.6 | CU
43.8 | CU
44.1 | CU
44.1 | CU
44 | CU
44.5 | CU
44.2 | CU
43.8 | CU
43.7 | CU
43.9 | CU
44 | CU
44.3 | CU
44.5 | CU
45 | CU
45.5 | CU
46.4 | CU
46.9 | CU
48.1 | CU
48.8 | CU
48.9 | CU
48.6 | CU
48.3 | CU
48.6 | CU
48.6 | CU
48.7 | CU
48.3 | CU
48.6 | CU
49.1 | CU
48.2 | CU
47.3 | CU
46.1 | CU
45.4 | CU
43.9 | CU
42.9 | CU
40.2 | CU
40.3 | CU
40.5 | CU
41.6 | CU
41.8 | CU
42.2 | CU
42.8 | CU
43 | CU
42.7 | CU
43 | CU
43.1 | CU
43 | CU
43.4 | CU
43 | CU
43.2 | CU
43.2 | CU
42.8 | CU
42.9 | CU
43.2 | CU
43.2 | CU
43 | CU
43.3 | CU
43.6 | CU
43.3 | CU
44 | CU
44 | CU
44.5 | CU
45.2 | CU
46.3 | CU
47.2 | CU
48.2 | CU
48.1 | CU
47.7 | CU
47.9 | CU
48.4 | CU
48.5 | CU
48.5 | CU
48.7 | CU
48.7 | CU
48.6 | CU
48.2 | CU
47.6 | CU
46.6 | CU
45.6 | CU
43.5 | CU
42.8 | CU
41.9 | CU
41.6 | CU
41.1 | CU
40.6 | CU
41 | CU
41.2 | CU
41.8 | CU
41.9 | CU
42 | CU
41.9 | CU
42 | CU
42.6 | CU
42.5 | CU
42.4 | CU
42.7 | CU
42.5 | CU
42.4 | CU
42.7 | CU
42.5 | CU
42 | CU
42.4 | CU
42.9 | CU
42.5 | CU
42.6 | CU
42.8 | CU
43.4 | CU
44.2 | CU
44.3 | CU
45.2 | CU
47.3 | CU
48.4 | CU
48.1 | CU
48.5 | CU
48.7 | CU
48.4 | CU
47.8 | CU
48 | CU
47.8 | CU
48.7 | CU
48.5 | CU
48.4 | CU
47.6 | CU
47.3 | CU
45.9 | CU
44.8 | CU
43 | CU
42.3 | CU
41.3 | CU
41 | CU
40.6 | CU
40.4 | CU
42.2 | CU
42.4 | CU
43.6 | CU
43.5 | CU
44.1 | CU
44.5 | CU
44.3 | CU
44.4 | CU
43.9 | CU
44.3 | CU
44.3 | CU
44.6 | CU
44.7 | CU
44.2 | CU
44.3 | CU
44.2 | CU
44.7 | CU
44.5 | CU
44.8 | CU
45.1 | CU
46 | CU
46.5 | CU
48 | CU
48.5 | CU
48.6 | CU
48.4 | CU
48.8 | CU
48.9 | CU
49.1 | CU
49.3 | CU
49.5 | CU
49.7 | CU
50.2 | CU
49.8 | CU
49.6 | CU
48.8 | CU
47.7 | CU
46.5 | CU
44.1 | CU
42 | CU
41 | CU
40.6 | CU
40.6 | CU
40.3 | CU
41.7 | CU
41.4 | CU
41.7 | CU
41.7 | CU
42.5 | CU
42.6 | CU
43.1 | CU
43.2 | CU
43.5 | CU
43.7 | CU
43.4 | CU
43.2 | CU
43.2 | CU
43.1 | CU
43.6 | CU
43.4 | CU
43.4 | CU
43.2 | CU
43.6 | CU
43.3 | CU
43.5 | CU
43.4 | CU
44 | CU
45.1 | CU
46.3 | CU
46.8 | CU
46.8 | CU
47.3 | CU
47.4 | CU
46.8 | CU
46.9 | CU
47.3 | CU
47.1 | CU
49.2 | CU
48.7 | CU
48.3 | CU
48.1 | CU
47.5 | CU
45.9 | CU
44.5 | CU
42.8 | CU
41.7 | CU
41.2 | CU
40.8 | CU
40.7 | CU
40.9 | CU
41.7 | CU
41.9 | CU
42.3 | CU
43.1 | CU
42.9 | CU
43.2 | CU
43.5 | CU
43.9 | CU
43.7 | CU
43.8 | CU
43.9 | CU
43.8 | CU
43.9 | CU
43.8 | CU
43.6 | CU
43.8 | CU
43.7 | CU
43.6 | CU
43.8 | CU
43.9 | CU
44.9 | CU
46.1 | CU
46.7 | CU
47.9 | CU
48.1 | CU
47.9 | CU
47.5 | CU
47.2 | CU
48.7 | CU
48.6 | CU
49.3 | CU
49.7 | CU
49.8 | CU
49.3 | CU
47.7 | CU
46.9 | CU
46.3 | CU
44.7 | CU
43.5 | CU
42 | CU
41.6 | CU
40.9 | CU
41 | CU
40.9 | CU
42 | CU
42.2 | CU
42.6 | CU
43 | CU
43.3 | CU
43.5 | CU
43.4 | CU
43.6 | CU
44.4 | CU
44.1 | CU
44.4 | CU
43.7 | CU
44.2 | CU
44.2 | CU
43.5 | CU
44 | CU
44.1 | CU
43.7 | CU
43.9 | CU
43.8 | CU
44.5 | CU
44.2 | CU
45 | CU
45.8 | CU
46.4 | CU
47.7 | CU
48.3 | CU
48.3 | CU
48.2 | CU
48.5 | CU
48.6 | CU
48.3 | CU
49 | CU
48.9 | CU
48.8 | CU
48.6 | CU
47.7 | CU
46.6 | CU
44.9 | CU
43.9 | CU
42.9 | CU
41.8 | CU
40.9 | CU
40.6 | CU
40.7 | CU
41.1 | CU
41.5 | CU
41.2 | CU
41.9 | CU
41.5 | CU
42.1 | CU
42.5 | CU
42.9 | CU
43.3 | CU
43.5 | CU
43.6 | CU
43.6 | CU
43.6 | CU
43.5 | CU
43.7 | CU
44.1 | CU
44.4 | CU
43.6 | CU
44.3 | CU
44.4 | CU
44.4 | CU
44.7 | CU
45.2 | CU
46.1 | CU
46.6 | CU
48.3 | CU
50 | CU
49.2 | CU
48.5 | CU
48.4 | CU
48.7 | CU
48.8 | CU
49 | CU
49.2 | CU
48.9 | CU
49.4 | CU
49.3 | CU
48.7 | CU
47.6 | CU
46.5 | CU
45.4 | CU
44 | CU
42.3 | CU
41.9 | CU
41.8 | CU
41.2 | CU
41.6 | CU
41.7 | CU
41.4 | CU
41.2 | CU
42.2 | CU
42.6 | CU
42.8 | CU
43.6 | CU
43.6 | CU
44 | CU
43.9 | CU
44 | CU
43.9 | CU
44.3 | CU
44 | CU
44.2 | CU
43.8 | CU
43.5 | CU
44.8 | CU
44 | CU
44.3 | CU
44.1 | CU
45.1 | CU
46 | CU
47 | CU
47.8 | CU
49.4 | CU
48.9 | CU
48.5 | CU
48.6 | CU
49.3 | CU
49.1 | CU
49.2 | CU
49.5 | CU
50.1 | CU
49.9 | CU
49.9 | CU
49.5 | CU
48.9 | CU
47.6 | CU
45.9 | CU
44.3 | CU
43.3 | CU
43 | CU
42.4 | CU
42 | CU
42 | CU
41.9 | CU
42.1 | CU
42.5 | CU
42.3 | CU
42.9 | CU
43.1 | CU
43.5 | CU
43.4 | CU
43.8 | CU
43.1 | CU
43.2 | CU
43.3 | CU
43.4 | CU
44 | CU
43.4 | CU
43.4 | CU
42.9 | CU
43.5 | CU
42.8 | CU
43.4 | CU
44.3 | CU
44.2 | CU
45.3 | CU
46.4 | CU
47.6 | CU
48.7 | CU
49 | CU
49.3 | CU
48.3 | CU
48.9 | CU
48.7 | CU
48.7 | CU
48.7 | CU
49 | CU
49.9 | CU
49.1 | CU
48.4 | CU
47.3 | CU
45.7 | CU
43.2 | CU
42.4 | CU
41.7 | CU
41.7 | CU
41.4 | CU
40.9 | CU
41.3 | CU
40.8 | CU
41 | CU
40.8 | CU
40.9 | CU
41.1 | CU
40.9 | CU
41.3 | CU
41.4 | CU
41.5 | CU
41.5 | CU
41.6 | CU
41.7 | CU
41.7 | CU
41.5 | CU
42.1 | CU
41.6 | CU
41.6 | CU
41.4 | CU
41.5 | CU
41.5 | CU
41.4 | CU
41.7 | CU
41.6 | CU
42.6 | CU
44 | CU
45.1 | CU
46.4 | CU
47.1 | CU
47.1 | CU
46.7 | CU
47.2 | CU
47.5 | CU
47.2 | CU
47 | CU
46.6 | CU
46.8 | CU
47 | CU
44.9 | CU
44.3 | CU
43.9 | CU
44.4 | CU
41.7 | CU
41.4 | CU
41 | CU
40.7 | CU
40.4 | CU
39.8 | CU
40 | CU
39.7 | CU
39.3 | CU
40.1 | CU
40.2 | CU
40.4 | CU
40.6 | CU
40.7 | CU
40.5 | CU
40.5 | CU
40.7 | CU
40.5 | CU
40.6 | CU
40.9 | CU
40.9 | CU
41 | CU
40.5 | CU
41 | CU
40.9 | CU
41.4 | CU
41.1 | CU
41.6 | CU
41.8 | CU
42 | CU
42.8 | CU
45 | CU
47.3 | CU
47 | CU
46.6 | CU
47.5 | CU
48 | CU
46.7 | CU
47.7 | CU
49 | CU
48.6 | CU
47.6 | CU
46.7 | CU
46.1 | CU
45.2 | CU
44.3 | CU
43.1 | CU
42 | CU
42.4 | CU
42.3 | CU
41.4 | CU
41.4 | CU
41.2 | CU
41.3 | CU
41.2 | CU
41.2 | CU
41.6 | CU
41.7 | CU
42 | CU
42.1 | CU
42 | CU
42.2 | CU
42.2 | CU
41.9 | CU
42 | CU
42 | CU
42.1 | CU
42.3 | CU
42.1 | CU
42.6 | CU
42.1 | CU
42.1 | CU
42.1 | CU
42.2 | CU
42.5 | CU
42.3 | CU
42.3 | CU
42.6 | CU
43.3 | CU
43.7 | CU
44.5 | CU
45.7 | CU
46.4 | CU
45.8 | CU
45.4 | CU
44.4 | CU
44.2 | CU
43.2 | CU
43.3 | CU
43.2 | CU
42.5 | CU
41.8 | CU
41.9 | CU
42.1 | CU
41.7 | CU
41.8 | CU
42.3 | CU
41.2 | CU
41.5 | CU
41.5 | CU
42.1 | CU
42.4 | CU
42.9 | CU
42.8 | CU
42.7 | CU
42.7 | CU
43 | CU
43.1 | CU
42.9 | CU
43.4 | CU
43.5 | CU
43.4 | CU
42.5 | CU
42.4 | CU
42.6 | CU
42.5 | CU
42.3 | CU
42.6 | CU
43.1 | CU
43.3 | CU
44 | CU
45.5 | CU
46.7 | CU
47.5 | CU
47.8 | CU
48.5 | CU
49.2 | CU
49 | CU
48.8 | CU
48.9 | CU
48.5 | CU
47.8 | CU
47.3 | CU
46.1 | CU
44.6 | CU
43.7 | CU
43.1 | CU
42.9 | CU
42.6 | CU
42.7 | CU
42.8 | CU
42.7 | CU
43 | CU
43.4 | CU
44.1 | CU
44.2 | CU
44.4 | CU
44.8 | CU
44.8 | CU
45.1 | CU
45.1 | CU
45.2 | CU
45.3 | CU
44.9 | CU
44.8 | CU
45.2 | CU
44.8 | CU
45.1 | CU
45 | CU
45.2 | CU
45.1 | CU
45.7 | CU
46 | CU
47.5 | CU
48.6 | CU
49 | CU
49.2 | CU
49.2 | CU
49.5 | CU
49.5 | CU
49.6 | CU
49.3 | CU
49.7 | CU
49 | CU
48.5 | CU
47.5 | CU
46.7 | CU
45.8 | CU
45.1 | CU
44.3 | CU
43.7 | CU
43.1 | CU
42.9 | CU
42.9 | CU
43.6 | CU
44.2 | CU
44.3 | CU
44.9 | CU
45.2 | CU
45.5 | CU
45.5 | CU
45.4 | CU
45.4 | CU
45.7 | CU
45.3 | CU
45.4 | CU
45.4 | CU
45 | CU
44.9 | CU
45 | CU
44.8 | CU
44.5 | CU
44.5 | CU
44.5 | CU
44.4 | CU
44.7 | CU
45.4 | CU
45.4 | CU
46.5 | CU
47.2 | CU
47.6 | CU
47.9 | CU
48 | CU
48.2 | CU
48.7 | CU
48.7 | CU
48.5 | CU
48.5 | CU
48.2 | CU
48.5 | CU
48.3 | CU
47.8 | CU
46.5 | CU
45.6 | CU
45.4 | CU
44.8 | CU
44 | CU
43.8 | CU
43.7 | CU
43.9 | CU
44.8 | CU
45.2 | CU
45.6 | CU
46.2 | CU
46.4 | CU
46.6 | CU
46.7 | CU
46.7 | CU
46.9 | CU
47.1 | CU
47.4 | CU
46.8 | CU
47 | CU
47.1 | CU
46.8 | CU
47 | CU
46.7 | CU
46.7 | CU
47.1 | CU
47.4 | CU
47.6 | CU
47.9 | CU
48.4 | CU
48.9 | CU
49.6 | CU
50.7 | CU
51.1 | CU
51.9 | CU
52.9 | CU
53.8 | CU
54.8 | CU
48.3 | CU
48.4 | CU
48.1 | CU
48.6 | CU
48.7 | CU
48.6 | CU
48.6 | CU
49.1 | CU
49 | CU
46.9 | CU
44 | CU
43.2 | CU
42.8 | CU
42.5 | CU
42.9 | CU
43.1 | CU
43.5 | CU
43.7 | CU
44.3 | CU
44.5 | CU
44.5 | CU
44.6 | CU
44.6 | CU
44.9 | CU
45 | CU
45.3 | CU
44.8 | CU
44.9 | CU
44.7 | CU
44.5 | CU
44.2 | CU
44.7 | CU
44.6 | CU
44.7 | CU
45.2 | CU
45.2 | CU
45.8 | CU
46.3 | CU
47.1 | CU
47.4 | CU
48.3 | CU
48.6 | CU
49.1 | CU
49.3 | CU
49.2 | CU
49.7 | CU
49.7 | CU
49.9 | CU
49.5 | CU
50 | CU
50.6 | CU
50.3 | CU
50.1 | CU
50.1 | CU
49.2 | CU
48.8 | CU
47.6 | CU
46.9 | CU
43.7 | CU
45.7 | CU
45.9 | CU
45.6 | CU
46.2 | CU
46.7 | CU
47 | CU
46.9 | CU
47.2 | CU
47.7 | CU
47.9 | CU
48.1 | CU
48.2 | CU
48.2 | CU
47.9 | CU
48.1 | CU
48.2 | CU
48 | CU
48.2 | CU
48.2 | CU
48.3 | CU
48.4 | CU
47.7 | CU
47.7 | CU
47.9 | CU
48.3 | CU
48.9 | CU
49.1 | CU
50.8 | CU
51.8 | CU
53.3 | CU
50.3 | CU
50.2 | CU
50 | CU
49.6 | CU
50.3 | CU
50.2 | CU
50.2 | CU
50 | CU
50.5 | CU
50.6 | CU
49.7 | CU
49.5 | CU
48.3 | CU
47.5 | CU
46.3 | CU
44.5 | CU
45.6 | CU
45.4 | CU
45.6 | CU
46.1 | CU
46.3 | CU
46.7 | CU
47.3 | CU
47.1 | CU
47.3 | CU
47.5 | CU
47.8 | CU
47.4 | CU
47.4 | CU
46.7 | CU
46.5 | CU
46 | CU
45.7 | CU
45.3 | CU
45.4 | CU
44.9 | CU
45 | CU
45.4 | CU
46 | CU
46.3 | CU
46.2 | CU
46.5 | CU
46.9 | CU
47.5 | CU
48.2 | CU
48.7 | CU
49 | CU
49.3 | CU
49.4 | CU
49.6 | CU
49.8 | CU
49.4 | CU
49.6 | CU
49.6 | CU
49.7 | CU
49.7 | CU
49.2 | CU
49.3 | CU
47.8 | CU
47.2 | CU
46.2 | CU
45.3 | CU
45 | CU
45.1 | CU
45.7 | CU
46 | CU
45.9 | CU
46.7 | CU
47.2 | CU
47.2 | CU
47.2 | CU
47.4 | CU
47.3 | CU
47.3 | CU
47.3 | CU
47.1 | CU
47 | CU
47.2 | CU
46.9 | CU
46.3 | CU
46.8 | CU
46.3 | CU
46.3 | CU
46.3 | CU
46.6 | CU
46.7 | CU
46.9 | CU
47.3 | CU
47.4 | CU
47.9 | CU
48.9 | CU
49.3 | CU
49.3 | CU
49.1 | CU
49.7 | CU
49.9 | CU
49.7 | CU
49.6 | CU
49.9 | CU
48.9 | CU
49.3 | CU
48.7 | CU
48.1 | CU
47.5 | CU
47.5 | CU
46.5 | CU
46.3 | CU
46 | CU
45.6 | CU
45.6 | CU
46.2 | CU
46 | CU
46.8 | CU
46.7 | CU
46.8 | CU
47.3 | CU
47.3 | CU
47.4 | CU
47.6 | CU
47.6 | CU
47.6 | CU
47.6 | CU
47.6 | CU
47.2 | CU
46.3 | CU
45 | CU
45.6 | CU
45.4 | CU
44.9 | CU
44.9 | CU
44.8 | CU
44.5 | CU
44.9 | CU
45.5 | CU
45.7 | CU
45.6 | CU
46.2 | CU
47 | CU
47.2 | CU
47.5 | CU
48.1 | CU
47.9 | CU
47.6 | CU
47.4 | CU
47.8 | CU
47.9 | CU
46.9 | CU
46.8 | CU
45.2 | CU
44.6 | CU
43.7 | CU
43.5 | CU
43.4 | CU
42.6 | CU
41.7 | CU
42.4 | CU
42.7 | CU
42.7 | CU
43.5 | CU
43.9 | CU
43.8 | CU
44.1 | CU
44.2 | CU
44.5 | CU
45.2 | CU
44.8 | CU
45 | CU
45.1 | CU
44.9 | CU
44.3 | CU
44.7 | CU
45.5 | CU
45.1 | CU
44.7 | CU
43.9 | CU
45.1 | CU
45.3 | CU
45.6 | CU
45.6 | CU
45.8 | CU
46.6 | CU
47.3 | CU
47.8 | CU
48.6 | CU
48.8 | CU
48.8 | CU
48.8 | CU
49.2 | CU
49.4 | CU
49 | CU
49.2 | CU
49.1 | CU
48.7 | CU
48.6 | CU
48.3 | CU
47.3 | CU
46 | CU
45.8 | CU
42.8 | CU
41.1 | CU
39 | CU
40 | CU
39.6 | CU
39.1 | CU
40.5 | CU
41.6 | CU
41.8 | CU
42.2 | CU
42.8 | CU
42.9 | CU
43.2 | CU
43 | CU
43 | CU
43.1 | CU
43.2 | CU
42.9 | CU
42.7 | CU
42.7 | CU
42.4 | CU
42.7 | CU
42.7 | CU
42.8 | CU
42.9 | CU
43.2 | CU
43.9 | CU
44.7 | CU
44.8 | CU
44.7 | CU
45.2 | CU
46.5 | CU
46.7 | CU
46.5 | CU
47 | CU
46.7 | CU
46.9 | CU
46.5 | CU
45.5 | CU
47.3 | CU
47.5 | CU
47.1 | CU
46.7 | CU
45.7 | CU
45.4 | CU
45.5 | CU
45.5 | CU
45.8 | CU
56.6 | CU
42 | CU
41.9 | CU
41.4 | CU
41.5 | CU
41.5 | CU
42.2 | CU
42.3 | CU
42.6 | CU
42.5 | CU
42.2 | CU
42.5 | CU
42.5 | CU
42.3 | CU
42.9 | CU
42.6 | CU
42.3 | CU
43.1 | CU
42.5 | CU
42.5 | CU
43 | CU
43.2 | CU
43.4 | CU
43.5 | CU
43.8 | CU
44.8 | CU
45.2 | CU
45.9 | CU
46.7 | CU
47.1 | CU
47.6 | CU
47.4 | CU
47.8 | CU
47.1 | CU
47.1 | CU
47.1 | CU
47.4 | CU
46.3 | CU
47.1 | CU
46.5 | CU
45.6 | CU
44.7 | CU
43.4 | CU
42.6 | CU
42.1 | CU
41.5 | CU
40.8 | CU
41.2 | CU
41.1 | CU
41.8 | CU
42.9 | CU
43.1 | CU
43.2 | CU
43.3 | CU
43.5 | CU
44.2 | CU
44.3 | CU
44.3 | CU
44.2 | CU
44.5 | CU
44.4 | CU
44.4 | CU
44 | CU
43.8 | CU
43.9 | CU
43.6 | CU
43.5 | CU
44 | CU
44.5 | CU
44.6 | CU
45.2 | CU
45.6 | CU
46.4 | CU
47 | CU
47.9 | CU
48.2 | CU
48.6 | CU
48.3 | CU
47.8 | CU
47.8 | CU
48.8 | CU
47.9 | CU
47.5 | CU
48 | CU
48 | CU
46.5 | CU
45 | CU
44 | CU
40.4 | CU
39.7 | CU
39.1 | CU
39.2 | CU
38.8 | CU
38.7 | CU
38.5 | CU
38.8 | CU
39.8 | CU
39.9 | CU
40.4 | CU
40.9 | CU
41.1 | CU
41.5 | CU
41.4 | CU
41.7 | CU
42.1 | CU
42 | CU
41.2 | CU
41.1 | CU
41.2 | CU
41.3 | CU
41.4 | CU
41.6 | CU
41.3 | CU
41.3 | CU
41.9 | CU
42.3 | CU
42.8 | CU
43.3 | CU
43.5 | CU
44.2 | CU
45 | CU
44.6 | CU
44.7 | CU
44.8 | CU
45 | CU
45 | CU
45.2 | CU
45.3 | CU
45.3 | CU
45.4 | CU
45.1 | CU
45.1 | CU
48.2 | CU
43.2 | CU
47 | CU
46.3 | CU
44.9 | CU
44.5 | CU
43.1 | CU
42.5 | CU
42.9 | CU
43.6 | CU
43.8 | CU
44.3 | CU
44.6 | CU
44.7 | CU
45.1 | CU
44.9 | CU
45.1 | CU
44.9 | CU
45.1 | CU
45.6 | CU
45.2 | CU
45.8 | CU
45.9 | CU
45.8 | CU
45.5 | CU
45.4 | CU
45.5 | CU
44.7 | CU
44.8 | CU
44.7 | CU
45.3 | CU
46 | CU
46.4 | CU
47.6 | CU
49.1 | CU
49.8 | CU
49.5 | CU
49.1 | CU
49.5 | CU
50.4 | CU
50.6 | CU
49.6 | CU
49.9 | CU
50 | CU
49.3 | CU
49.3 | CU
49 | CU
48.1 | CU
47.2 | CU
45.4 | CU
44.2 | CU
43.9 | CU
44.3 | CU
43.8 | CU
43.5 | CU
42.7 | CU
42.6 | CU
43.5 | CU
43.8 | CU
43.9 | CU
43.9 | CU
44.7 | CU
45 | CU
45.2 | CU
45 | CU
45.5 | CU
45.4 | CU
45.6 | CU
45.3 | CU
45.3 | CU
45.6 | CU
45.1 | CU
45.3 | CU
45 | CU
45.1 | CU
44.7 | CU
44.5 | CU
44.6 | CU
44.9 | CU
45.4 | CU
45.5 | CU
47.6 | CU
49.6 | CU
50.1 | CU
50.1 | CU
48.9 | CU
47.6 | CU
50.3 | CU
49.4 | CU
48.2 | CU
48.3 | CU
48 | CU
47.7 | CU
46.4 | CU
46.8 | CU
44.2 | CU
45 | CU
45.5 | CU
42.5 | CU
42.5 | CU
41.9 | CU
41.9 | CU
42.1 | CU
43.6 | CU
44 | CU
44.2 | CU
44.5 | CU
44.8 | CU
44.6 | CU
45.3 | CU
44.9 | CU
45 | CU
45 | CU
45 | CU
45 | CU
45.1 | CU
44.9 | CU
44.8 | CU
44.9 | CU
44.6 | CU
44.3 | CU
44 | CU
44.5 | CU
44.1 | CU
44.5 | CU
44.4 | CU
44.5 | CU
45.1 | CU
45.6 | CU
46.9 | CU
48.8 | CU
49.4 | CU
47.6 | CU
48.9 | CU
49.9 | CU
50.8 | CU
48.7 | CU
48.1 | CU
47.2 | CU
44.8 | CU
44.7 | CU
44.2 | CU
41.1 | CU
41.4 | CU
41 | CU
40.6 | CU
40 | CU
40.1 | CU
40.3 | CU
41.8 | CU
42 | CU
42.4 | CU
42.8 | CU
42.6 | CU
43 | CU
42.6 | CU
43.2 | CU
43.1 | CU
43.4 | CU
43.1 | CU
43.1 | CU
42.7 | CU
43.1 | CU
43 | CU
43.1 | CU
43 | CU
42.9 | CU
43.2 | CU
42.8 | CU
42.7 | CU
43.1 | CU
43.4 | CU
43.9 | CU
44.7 | CU
45.8 | CU
46.4 | CU
46.6 | CU
47.1 | CU
46.8 | CU
46.5 | CU
47.5 | CU
47.6 | CU
46.7 | CU
46.2 | CU
46.2 | CU
46.1 | CU
49.8 | CU
49.5 | CU
47.9 | CU
44.9 | CU
43.6 | CU
43.8 | CU
43.8 | CU
43.8 | CU
44.3 | CU
45.6 | CU
46.2 | CU
46.4 | CU
46.5 | CU
46.6 | CU
47.3 | CU
47.2 | CU
47.9 | CU
48.1 | CU
47.9 | CU
47.5 | CU
48.1 | CU
47.9 | CU
47.9 | CU
47.6 | CU
47.9 | CU
48.3 | CU
47.9 | CU
47.7 | CU
48.1 | CU
48.6 | CU
49 | CU
49.2 | CU
49.8 | CU
50.3 | CU
50.9 | CU
50.9 | CU
51.1 | CU
51.5 | CU
52 | CU
52.3 | CU
52.1 | CU
52.1 | CU
52.1 | CU
51.4 | CU
51.3 | CU
50.8 | CU
50 | CU
48.5 | CU
47.9 | CU
46.6 | CU
45.5 | CU
45 | CU
43.9 | CU
44 | CU
44.8 | CU
46.8 | CU
47.5 | CU
47.5 | CU
48 | CU
48.3 | CU
48.4 | CU
48.6 | CU
48.8 | CU
48.8 | CU
48.6 | CU
48.4 | CU
48.5 | CU
48.2 | CU
48.6 | CU
48.7 | CU
48.7 | CU
48.5 | CU
48.8 | CU
48.8 | CU
49.1 | CU
49.8 | CU
50.5 | CU
50.6 | CU
51 | CU
51.4 | CU
51.9 | CU
52 | CU
51.4 | CU
51.4 | CU
51.6 | CU
51.6 | CU
51 | CU
50.7 | CU
50.8 | CU
49.3 | CU
48.1 | CU
47.2 | CU
43.3 | CU
41.7 | CU
39.2 | CU
38.9 | CU
38.9 | CU
39 | CU
39.8 | CU
41 | CU
41.7 | CU
41.7 | CU
42 | CU
42.2 | CU
42.1 | CU
42.3 | CU
42.2 | CU
42.4 | CU
42.3 | CU
42.5 | CU
42.4 | CU
42.4 | CU
42.5 | CU
42.1 | CU
41.8 | CU
41.7 | CU
42.1 | CU
42.1 | CU
41.9 | CU
42.2 | CU
42.2 | CU
42.3 | CU
42.7 | CU
43.1 | CU
43.1 | CU
44 | CU
44.4 | CU
44.4 | CU
45.2 | CU
45.1 | CU
44.8 | CU
45.1 | CU
45.1 | CU
46 | CU
46.4 | CU
46.5 | CU
46.5 | CU
46.7 | CU
45.3 | CU
43.9 | CU
43.5 | CU
42.7 | CU
42.1 | CU
41.7 | CU
42.3 | CU
43.8 | CU
43.7 | CU
44.1 | CU
44.6 | CU
44.8 | CU
45.2 | CU
45.2 | CU
45.3 | CU
45.7 | CU
45.8 | CU
45.6 | CU
45.6 | CU
45.5 | CU
45.8 | CU
45.8 | CU
45.7 | CU
44.7 | CU
45 | CU
45.2 | CU
45.7 | CU
45.6 | CU
46 | CU
46.4 | CU
47.2 | CU
47.9 | CU
47.7 | CU
48.9 | CU
49 | CU
48.6 | CU
48.6 | CU
48.2 | CU
48.1 | CU
47.6 | CU
47.8 | CU
47.4 | CU
47.6 | CU
46.9 | CU
46.7 | CU
45.9 | CU
45.1 | CU
44.4 | CU
43.3 | CU
42.3 | CU
41.6 | CU
41.8 | CU
41.8 | CU
43 | CU
43.3 | CU
43 | CU
43.4 | CU
43.1 | CU
43.2 | CU
43.4 | CU
43.8 | CU
43.9 | CU
44.1 | CU
43.9 | CU
43.5 | CU
43.6 | CU
43.7 | CU
43.6 | CU
43.7 | CU
43.6 | CU
43.1 | CU
43.3 | CU
43.6 | CU
43.9 | CU
43.9 | CU
44.2 | CU
45.1 | CU
45.8 | CU
46.8 | CU
47.3 | CU
47.1 | CU
47.2 | CU
48.3 | CU
47.6 | CU
46.8 | CU
46.2 | CU
47.2 | CU
47.6 | CU
44.7 | CU
45 | CU
45.2 | CU
44.9 | CU
44.6 | CU
45.9 | CU
45.7 | CU
43.1 | CU
47.7 | CU
5.8 | CU
39 | CU
40.2 | CU
39.8 | CU
40.8 | CU
41.2 | CU
41.6 | CU
41.7 | CU
42.1 | CU
42.1 | CU
42.4 | CU
42 | CU
42.1 | CU
42.2 | CU
42.3 | CU
42.1 | CU
42.1 | CU
42.6 | CU
42.4 | CU
42.6 | CU
42.2 | CU
42.6 | CU
42.8 | CU
43 | CU
43.4 | CU
44.2 | CU
44.9 | CU
45.6 | CU
46.7 | CU
47.8 | CU
48.5 | CU
48.4 | CU
48.4 | CU
48.4 | CU
47.8 | CU
47 | CU
47 | CU
46.8 | CU
47 | CU
45.7 | CU
45.4 | CU
44.9 | CU
43.9 | CU
43.3 | CU
43 | CU
42.4 | CU
42.6 | CU
41.5 | CU
41.6 | CU
41.3 | CU
42.4 | CU
43.7 | CU
43.7 | CU
44.2 | CU
44.3 | CU
44.4 | CU
44.2 | CU
44.3 | CU
45.1 | CU
44.9 | CU
44.3 | CU
44.3 | CU
44.5 | CU
43.6 | CU
44.4 | CU
44.4 | CU
44.5 | CU
44.1 | CU
44.1 | CU
43.9 | CU
44.2 | CU
44.4 | CU
44.6 | CU
45.1 | CU
45.5 | CU
46 | CU
47 | CU
47.8 | CU
48.1 | CU
48.2 | CU
47.6 | CU
46.8 | CU
45.7 | CU
45.5 | CU
45.7 | CU
46.7 | CU
46.7 | CU
46 | CU
45.2 | CU
43.3 | CU
43.5 | CU
43.5 | CU
43.8 | CU
44.2 | CU
44.6 | CU
45 | CU
45.9 | CU
46.3 | CU
45.7 | CU
43.9 | CU
44.9 | CU
45.5 | CU
47.8 | CU
47.4 | CU
46.3 | CU
46.3 | CU
45.9 | CU
45.5 | CU
45.2 | CU
44.5 | CU
43.8 | CU
43.1 | CU
42 | CU
39.5 | CU
39.5 | CU
40.2 | CU
39.9 | CU
39.6 | CU
40.6 | CU
41.7 | CU
41.9 | CU
42.1 | CU
42.3 | CU
42.2 | CU
42.5 | CU
42.6 | CU
42.6 | CU
42.3 | CU
42.4 | CU
42.6 | CU
42.2 | CU
42.2 | CU
42.3 | CU
42.3 | CU
42 | CU
41.6 | CU
41.3 | CU
41.3 | CU
41.5 | CU
42 | CU
42.1 | CU
43 | CU
43 | CU
43.5 | CU
45.2 | CU
46.2 | CU
46.3 | CU
44.9 | CU
44.1 | CU
45.5 | CU
44.9 | CU
46.4 | CU
45.3 | CU
45.5 | CU
42.9 | CU
44.5 | CU
43.7 | CU
42.9 | CU
42.3 | CU
41.3 | CU
40.8 | CU
39.4 | CU
39.9 | CU
39.4 | CU
39.4 | CU
39.4 | CU
40.2 | CU
41.3 | CU
41.8 | CU
41.9 | CU
41.6 | CU
41.4 | CU
41.2 | CU
41.4 | CU
41.6 | CU
41.4 | CU
41 | CU
40.6 | CU
40.2 | CU
39.9 | CU
40 | CU
40.1 | CU
40 | CU
39.6 | CU
39.6 | CU
39.8 | CU
40.2 | CU
39.4 | CU
40.1 | CU
40.5 | CU
40.5 | CU
41.8 | CU
42.4 | CU
42 | CU
42.3 | CU
42.6 | CU
43.8 | CU
43.1 | CU
40.8 | CU
41.6 | CU
39.5 | CU
40.9 | CU
39.6 | CU
39.6 | CU
39.2 | CU
39.4 | CU
36.5 | CU
35.4 | CU
34.6 | CU
34.1 | CU
33.9 | CU
34.3 | CU
34.6 | CU
35.1 | CU
35.4 | CU
35.1 | CU
35.1 | CU
35.3 | CU
35.8 | CU
35.5 | CU
35.5 | CU
35.7 | CU
35.4 | CU
35.2 | CU
34.7 | CU
35 | CU
35 | CU
34.8 | CU
35 | CU
34.8 | CU
34.7 | CU
35 | CU
35.5 | CU
35.7 | CU
36 | CU
37 | CU
37.1 | CU
37.1 | CU
38.2 | CU
38.7 | CU
39.6 | CU
39.8 | CU
39.1 | CU
38 | CU
38.7 | CU
38.9 | CU
38.7 | CU
38.7 | CU
38.1 | CU
37.2 | CU
37.3 | CU
36.8 | CU
36.4 | CU
35.4 | CU
34.7 | CU
34 | CU
34.1 | CU
33.1 | CU
34.3 | CU
34.1 | CU
34.3 | CU
34.8 | CU
35 | CU
35.2 | CU
35.6 | CU
35.5 | CU
35.6 | CU
36.3 | CU
36.2 | CU
36.7 | CU
36.4 | CU
36.5 | CU
36.7 | CU
36.8 | CU
36.6 | CU
36.6 | CU
36.5 | CU
36.8 | CU
36.8 | CU
36.6 | CU
37.1 | CU
36.5 | CU
37.2 | CU
37.7 | CU
38.3 | CU
39.1 | CU
38.9 | CU
39.9 | CU
40.8 | CU
40.8 | CU
43 | CU
41.3 | CU
41.7 | CU
41.9 | CU
40.1 | CU
39.4 | CU
38.4 | CU
37.2 | CU
36.6 | CU
35.6 | CU
35.2 | CU
34.4 | CU
34.3 | CU
35.2 | CU
35.9 | CU
36.1 | CU
36.6 | CU
37.4 | CU
37.7 | CU
37.6 | CU
37.9 | CU
38.1 | CU
38.1 | CU
38.5 | CU
38.1 | CU
37.8 | CU
37.5 | CU
37.1 | CU
37.5 | CU
37.3 | CU
37.3 | CU
37.5 | CU
37.2 | CU
36.9 | CU
37.1 | CU
37.5 | CU
37.9 | CU
38.6 | CU
38.9 | CU
39.9 | CU
40.4 | CU
40.8 | CU
41.5 | CU
41.4 | CU
41.5 | CU
42 | CU
41.9 | CU
40.7 | CU
39.9 | CU
39.6 | CU
38.8 | CU
38.2 | CU
37.1 | CU
37 | CU
36.1 | CU
35.7 | CU
34.8 | CU
34 | CU
33.5 | CU
33.6 | CU
33.3 | CU
33 | CU
33.3 | CU
34.4 | CU
34.6 | CU
35.3 | CU
35.5 | CU
35.7 | CU
35.7 | CU
36.4 | CU
36.1 | CU
36.2 | CU
35.9 | CU
35.7 | CU
35.5 | CU
35.3 | CU
35.5 | CU
35.4 | CU
36.1 | CU
35.6 | CU
35.6 | CU
36.2 | CU
35.8 | CU
36.6 | CU
37 | CU
37.7 | CU
38.8 | CU
42.8 | CU
38 | CU
38.1 | CU
37.8 | CU
37.9 | CU
37.9 | CU
38.6 | CU
38.6 | CU
39.2 | CU
38.7 | CU
38.7 | CU
38.1 | CU
38.3 | CU
37.1 | CU
36.2 | CU
34.9 | CU
33.9 | CU
32.6 | CU
31.7 | CU
31 | CU
31.4 | CU
31.5 | CU
31.9 | CU
32.7 | CU
33.2 | CU
33.8 | CU
34 | CU
33.9 | CU
34.2 | CU
34.3 | CU
34.2 | CU
34.4 | CU
34.3 | CU
34.2 | CU
33.8 | CU
33.8 | CU
33.2 | CU
33.3 | CU
32.7 | CU
32.6 | CU
32.7 | CU
32.6 | CU
33.2 | CU
33.2 | CU
33.3 | CU
33.7 | CU
34.2 | CU
34.6 | CU
35.1 | CU
35.5 | CU
35.7 | CU
35.9 | CU
36.3 | CU
36 | CU
36.6 | CU
35.8 | CU
36.2 | CU
35.7 | CU
35.6 | CU
35 | CU
34.5 | CU
33.6 | CU
32.7 | CU
32.3 | CU
32.2 | CU
31.7 | CU
31.6 | CU
31.2 | CU
31.7 | CU
31.5 | CU
32 | CU
32.4 | CU
32.9 | CU
32.8 | CU
33 | CU
33.3 | CU
33.6 | CU
33.9 | CU
33.7 | CU
33.8 | CU
33.9 | CU
33.6 | CU
33.6 | CU
33 | CU
32.8 | CU
33 | CU
32.9 | CU
32.3 | CU
49.3 | SN1
49.3 | SN1
49.2 | SN1
49.2 | SN1
49.1 | SN1
49.4 | SN1
49.3 | SN1
48.9 | SN1
49.1 | SN1
48.5 | SN1
48.6 | SN1
48.3 | SN1
48.5 | SN1
48.6 | SN1
48.6 | SN1
48.7 | SN1
48.6 | SN1
48.9 | SN1
49 | SN1
49.1 | SN1
49.1 | SN1
49.3 | SN1
49.5 | SN1
50.1 | SN1
48.6 | SN1
50.3 | SN1
50.6 | SN1
50.7 | SN1
51.7 | SN1
51.2 | SN1
51.2 | SN1
51.1 | SN1
51.1 | SN1
50.6 | SN1
50.8 | SN1
50.1 | SN1
49.6 | SN1
49.1 | SN1
48.6 | SN1
47.9 | SN1
47.5 | SN1
47.1 | SN1
47 | SN1
47.1 | SN1
46.8 | SN1
47 | SN1
47 | SN1
47.1 | SN1
46.9 | SN1
47 | SN1
46.9 | SN1
46.7 | SN1
46.8 | SN1
46.7 | SN1
46.8 | SN1
46.5 | SN1
46.5 | SN1
46.4 | SN1
46.4 | SN1
46.3 | SN1
46.4 | SN1
46.5 | SN1
46.5 | SN1
46.2 | SN1
46.5 | SN1
46.5 | SN1
46.9 | SN1
47.2 | SN1
47.8 | SN1
48.1 | SN1
49.4 | SN1
49.4 | SN1
49.7 | SN1
50 | SN1
48.1 | SN1
48.3 | SN1
48 | SN1
48.1 | SN1
48.6 | SN1
49 | SN1
49 | SN1
48.3 | SN1
48.4 | SN1
55.8 | SN1
49.6 | SN1
48.9 | SN1
48.8 | SN1
48.6 | SN1
48.7 | SN1
48.5 | SN1
48.9 | SN1
48.5 | SN1
48.7 | SN1
48.5 | SN1
48.5 | SN1
48.3 | SN1
48.4 | SN1
48.5 | SN1
48.5 | SN1
48.5 | SN1
48.5 | SN1
48.2 | SN1
48.4 | SN1
48.3 | SN1
48.3 | SN1
48 | SN1
48 | SN1
47.9 | SN1
47.8 | SN1
48 | SN1
48.2 | SN1
47.9 | SN1
48.2 | SN1
48.5 | SN1
48.3 | SN1
48.7 | SN1
49.6 | SN1
49.8 | SN1
49.9 | SN1
49.9 | SN1
49.8 | SN1
49.6 | SN1
49.5 | SN1
49.3 | SN1
49.5 | SN1
48.8 | SN1
49.1 | SN1
49.1 | SN1
48.8 | SN1
48.9 | SN1
48.9 | SN1
48.7 | SN1
48.5 | SN1
48.8 | SN1
48.1 | SN1
48.2 | SN1
48.4 | SN1
48.3 | SN1
48.2 | SN1
48.6 | SN1
48.4 | SN1
48.7 | SN1
48.8 | SN1
48.7 | SN1
48.4 | SN1
48.3 | SN1
48.4 | SN1
48.5 | SN1
48.5 | SN1
48.2 | SN1
48.3 | SN1
48.2 | SN1
48.1 | SN1
48.6 | SN1
48.2 | SN1
48.1 | SN1
48.1 | SN1
48.3 | SN1
48 | SN1
48.7 | SN1
48.8 | SN1
47 | SN1
49 | SN1
48.9 | SN1
49.1 | SN1
49.7 | SN1
49 | SN1
49.7 | SN1
49.4 | SN1
49.5 | SN1
49.5 | SN1
49.6 | SN1
49.2 | SN1
48.6 | SN1
49.3 | SN1
48.5 | SN1
47.9 | SN1
48.2 | SN1
48.1 | SN1
47.6 | SN1
48.5 | SN1
48.5 | SN1
48.3 | SN1
51.9 | SN1
52.2 | SN1
52.4 | SN1
52.5 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.1 | SN1
51.8 | SN1
51.8 | SN1
51.4 | SN1
51.9 | SN1
51.6 | SN1
51.5 | SN1
51.4 | SN1
51.1 | SN1
50.9 | SN1
51.1 | SN1
51.4 | SN1
51 | SN1
51.4 | SN1
51.7 | SN1
51.5 | SN1
51.6 | SN1
51.8 | SN1
51.8 | SN1
51.7 | SN1
51.9 | SN1
51.5 | SN1
51.6 | SN1
51.5 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.5 | SN1
50.1 | SN1
50.6 | SN1
49.8 | SN1
50.2 | SN1
50.9 | SN1
51.2 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.7 | SN1
51.2 | SN1
51.9 | SN1
51.7 | SN1
51.9 | SN1
52.4 | SN1
52.3 | SN1
52.5 | SN1
52 | SN1
52 | SN1
52 | SN1
52.1 | SN1
51.9 | SN1
52 | SN1
52.1 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
51.8 | SN1
51.6 | SN1
51.7 | SN1
51.6 | SN1
51.9 | SN1
51.8 | SN1
52 | SN1
52.2 | SN1
52.7 | SN1
52.5 | SN1
52.2 | SN1
52.7 | SN1
52.4 | SN1
52.4 | SN1
52.6 | SN1
52.3 | SN1
52 | SN1
52.2 | SN1
52.1 | SN1
51.1 | SN1
51.5 | SN1
51.3 | SN1
51 | SN1
50.9 | SN1
50.6 | SN1
50.6 | SN1
50.9 | SN1
50.6 | SN1
50.2 | SN1
50.8 | SN1
50.3 | SN1
50.7 | SN1
50.7 | SN1
50.4 | SN1
50.8 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.9 | SN1
51.2 | SN1
50.7 | SN1
50.5 | SN1
50.7 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
50.3 | SN1
50.3 | SN1
50.7 | SN1
51.2 | SN1
50.8 | SN1
51.4 | SN1
52 | SN1
52.4 | SN1
52.3 | SN1
52 | SN1
52.3 | SN1
52.1 | SN1
52.8 | SN1
52.3 | SN1
52.2 | SN1
52 | SN1
51.3 | SN1
51.7 | SN1
51.5 | SN1
51.3 | SN1
51.6 | SN1
50.8 | SN1
50.6 | SN1
51 | SN1
51 | SN1
50.9 | SN1
50.6 | SN1
50.8 | SN1
50.9 | SN1
51.3 | SN1
50.9 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
53 | SN1
53.1 | SN1
52.9 | SN1
53 | SN1
53.1 | SN1
53.3 | SN1
52.9 | SN1
52.9 | SN1
53.1 | SN1
53.2 | SN1
53 | SN1
53 | SN1
53.3 | SN1
53.3 | SN1
53.3 | SN1
53.7 | SN1
53.6 | SN1
53.5 | SN1
53.7 | SN1
53.7 | SN1
54 | SN1
54.1 | SN1
54.3 | SN1
54.2 | SN1
54 | SN1
53.7 | SN1
53 | SN1
52.3 | SN1
52 | SN1
51.9 | SN1
51.9 | SN1
51.6 | SN1
51.6 | SN1
51.5 | SN1
51.5 | SN1
51.5 | SN1
51.8 | SN1
51.8 | SN1
51.6 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
52.1 | SN1
52 | SN1
52.4 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
52.8 | SN1
53 | SN1
52.8 | SN1
52.7 | SN1
53.2 | SN1
53 | SN1
52.9 | SN1
52.9 | SN1
53.4 | SN1
52.9 | SN1
53.4 | SN1
53.2 | SN1
53.3 | SN1
53.3 | SN1
53.6 | SN1
53.2 | SN1
53.1 | SN1
53.4 | SN1
53.6 | SN1
53.6 | SN1
53.9 | SN1
54 | SN1
52.9 | SN1
52.6 | SN1
52.5 | SN1
52.1 | SN1
52 | SN1
51.7 | SN1
51.9 | SN1
51.6 | SN1
51.7 | SN1
51.7 | SN1
51.8 | SN1
51.7 | SN1
51.4 | SN1
51.7 | SN1
51.7 | SN1
51.7 | SN1
52 | SN1
51.8 | SN1
52 | SN1
52.4 | SN1
52.3 | SN1
52.6 | SN1
52.7 | SN1
52.6 | SN1
52.4 | SN1
52.8 | SN1
52.9 | SN1
53.2 | SN1
53 | SN1
52.7 | SN1
53.3 | SN1
52.8 | SN1
53 | SN1
53.2 | SN1
53.2 | SN1
53.3 | SN1
53.4 | SN1
53.3 | SN1
53.1 | SN1
53.4 | SN1
53.6 | SN1
53.6 | SN1
53.3 | SN1
53.5 | SN1
53.9 | SN1
53.7 | SN1
53.9 | SN1
53.8 | SN1
53.4 | SN1
52.2 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.7 | SN1
51.7 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.6 | SN1
51.7 | SN1
51.6 | SN1
51.7 | SN1
51.5 | SN1
51.6 | SN1
51.7 | SN1
52.3 | SN1
52.2 | SN1
52.6 | SN1
52.6 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
52.8 | SN1
53.1 | SN1
53 | SN1
53 | SN1
52.9 | SN1
52.9 | SN1
53 | SN1
53.1 | SN1
52.9 | SN1
53.1 | SN1
53.1 | SN1
53.1 | SN1
53.1 | SN1
53.3 | SN1
53.2 | SN1
53.6 | SN1
53.8 | SN1
54 | SN1
54 | SN1
54.1 | SN1
54.2 | SN1
54.2 | SN1
53.9 | SN1
53.6 | SN1
53 | SN1
52.5 | SN1
52.1 | SN1
51.8 | SN1
51.9 | SN1
51.7 | SN1
51.7 | SN1
51.6 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
52.8 | SN1
52.9 | SN1
52.9 | SN1
53.1 | SN1
53.3 | SN1
53 | SN1
53 | SN1
53.3 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.8 | SN1
52.7 | SN1
52.5 | SN1
52.8 | SN1
52.8 | SN1
52.8 | SN1
52.9 | SN1
53 | SN1
53.3 | SN1
53.5 | SN1
53.7 | SN1
53.7 | SN1
53.8 | SN1
54.1 | SN1
54.2 | SN1
54 | SN1
54.2 | SN1
54.2 | SN1
54.1 | SN1
53.9 | SN1
53.7 | SN1
53.3 | SN1
53 | SN1
52.6 | SN1
52.1 | SN1
51.9 | SN1
51.6 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.3 | SN1
52.4 | SN1
52.5 | SN1
52.3 | SN1
52.5 | SN1
52.3 | SN1
52.7 | SN1
52.9 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.3 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
53.1 | SN1
53.2 | SN1
53.6 | SN1
53.7 | SN1
53.8 | SN1
54 | SN1
54.1 | SN1
54.3 | SN1
54.3 | SN1
54.4 | SN1
54.6 | SN1
54.6 | SN1
54.6 | SN1
54.7 | SN1
54.6 | SN1
54.6 | SN1
54.5 | SN1
54.3 | SN1
54.2 | SN1
53.7 | SN1
53.6 | SN1
52.8 | SN1
52.4 | SN1
52 | SN1
51.6 | SN1
51.5 | SN1
51.9 | SN1
52.2 | SN1
52.4 | SN1
52.6 | SN1
52.3 | SN1
52.4 | SN1
52.4 | SN1
52.3 | SN1
52.5 | SN1
52.6 | SN1
52.5 | SN1
52.1 | SN1
51.9 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
52 | SN1
52.3 | SN1
52.1 | SN1
52.3 | SN1
52.1 | SN1
52.3 | SN1
52.2 | SN1
52.3 | SN1
52.5 | SN1
52.7 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.6 | SN1
52.5 | SN1
52.6 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.9 | SN1
52.8 | SN1
52.6 | SN1
52.5 | SN1
52.6 | SN1
52.1 | SN1
51.8 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.4 | SN1
51.6 | SN1
51.6 | SN1
51.5 | SN1
51.7 | SN1
51.6 | SN1
51.8 | SN1
51.5 | SN1
51.5 | SN1
51.5 | SN1
51.4 | SN1
51.8 | SN1
52.3 | SN1
51.8 | SN1
52.4 | SN1
52.5 | SN1
52.4 | SN1
52.5 | SN1
52.4 | SN1
51.9 | SN1
52.2 | SN1
52.3 | SN1
52.2 | SN1
52 | SN1
52.3 | SN1
52.2 | SN1
52.4 | SN1
52.4 | SN1
52.4 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.3 | SN1
52.8 | SN1
53 | SN1
53.1 | SN1
53 | SN1
53.1 | SN1
53.2 | SN1
53.2 | SN1
52.7 | SN1
52.6 | SN1
52.1 | SN1
52 | SN1
51.6 | SN1
51.7 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
52.2 | SN1
52.6 | SN1
52.5 | SN1
52.5 | SN1
52.8 | SN1
52.5 | SN1
52.9 | SN1
53.4 | SN1
52.8 | SN1
52.7 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.2 | SN1
52.4 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.5 | SN1
52.5 | SN1
52.8 | SN1
53 | SN1
52.6 | SN1
53 | SN1
52.9 | SN1
53 | SN1
53.5 | SN1
53.4 | SN1
53.6 | SN1
53.5 | SN1
53.5 | SN1
53.2 | SN1
52.7 | SN1
52.5 | SN1
52.1 | SN1
52 | SN1
51.9 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.5 | SN1
51.6 | SN1
52.1 | SN1
51.7 | SN1
52 | SN1
51.8 | SN1
52.2 | SN1
52.5 | SN1
52.7 | SN1
52.9 | SN1
52.8 | SN1
52.7 | SN1
52.5 | SN1
53 | SN1
53.1 | SN1
53 | SN1
53.2 | SN1
53.3 | SN1
53.5 | SN1
53.5 | SN1
53.6 | SN1
53.5 | SN1
53.3 | SN1
53.6 | SN1
53.9 | SN1
53.9 | SN1
53.4 | SN1
54 | SN1
54.1 | SN1
54.1 | SN1
54.2 | SN1
54.3 | SN1
54.7 | SN1
54.3 | SN1
54.4 | SN1
54.6 | SN1
54.5 | SN1
54.2 | SN1
53.6 | SN1
53.1 | SN1
52.5 | SN1
52 | SN1
52 | SN1
51.8 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.5 | SN1
51.8 | SN1
52.4 | SN1
52.7 | SN1
53 | SN1
53.2 | SN1
53.2 | SN1
53.2 | SN1
53.5 | SN1
53.9 | SN1
54.2 | SN1
54.3 | SN1
54.4 | SN1
54.5 | SN1
54.6 | SN1
54.5 | SN1
55 | SN1
54.9 | SN1
55 | SN1
54.9 | SN1
55.1 | SN1
55.1 | SN1
55 | SN1
55.1 | SN1
55.2 | SN1
55.2 | SN1
55 | SN1
54.6 | SN1
53.8 | SN1
52.6 | SN1
52.1 | SN1
51.8 | SN1
51.7 | SN1
51.7 | SN1
51.8 | SN1
52 | SN1
52 | SN1
52 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
52 | SN1
34.7 | SN1
52.1 | SN1
52.4 | SN1
52.4 | SN1
52.5 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.5 | SN1
52.7 | SN1
52.4 | SN1
52.6 | SN1
52.6 | SN1
52.4 | SN1
52.2 | SN1
52.4 | SN1
52.5 | SN1
52.7 | SN1
52.5 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52.5 | SN1
52.6 | SN1
52.5 | SN1
52.5 | SN1
52.2 | SN1
52.3 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.4 | SN1
52.6 | SN1
53.2 | SN1
53 | SN1
53.2 | SN1
53 | SN1
52.7 | SN1
52.8 | SN1
52.4 | SN1
52.7 | SN1
52.6 | SN1
52.4 | SN1
52.9 | SN1
52.8 | SN1
52.7 | SN1
52.9 | SN1
52.7 | SN1
52.9 | SN1
53 | SN1
52.6 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.3 | SN1
52.3 | SN1
52 | SN1
51.9 | SN1
52.1 | SN1
52 | SN1
52.2 | SN1
52.3 | SN1
52.2 | SN1
51.9 | SN1
51.7 | SN1
52 | SN1
52.1 | SN1
52.2 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.4 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
52.1 | SN1
52 | SN1
51.7 | SN1
49.9 | SN1
46 | SN1
40 | SN1
31.5 | SN1
25.6 | SN1
22.1 | SN1
25.2 | SN1
22.4 | SN1
22.5 | SN1
21.2 | SN1
15 | SN1
10.4 | SN1
6.8 | SN1
4.4 | SN1
3.1 | SN1
3.1 | SN1
2.8 | SN1
2.5 | SN1
2.4 | SN1
2.7 | SN1
3.3 | SN1
3.8 | SN1
4.4 | SN1
4.6 | SN1
4.7 | SN1
4.6 | SN1
4.6 | SN1
4.7 | SN1
4.6 | SN1
4.4 | SN1
4.1 | SN1
3.8 | SN1
3.7 | SN1
3.6 | SN1
3.4 | SN1
3 | SN1
2.7 | SN1
2.5 | SN1
2.4 | SN1
2.4 | SN1
2.4 | SN1
2.1 | SN1
2.2 | SN1
2.4 | SN1
2.2 | SN1
1.8 | SN1
1.5 | SN1
1.2 | SN1
1 | SN1
0.9 | SN1
0.8 | SN1
0.7 | SN1
0.8 | SN1
0.9 | SN1
1 | SN1
1 | SN1
0.9 | SN1
0.9 | SN1
0.9 | SN1
1 | SN1
1.1 | SN1
1.2 | SN1
1.2 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
52.4 | SN1
52.6 | SN1
52.5 | SN1
52.7 | SN1
53 | SN1
52.9 | SN1
53 | SN1
52.8 | SN1
52.9 | SN1
53.2 | SN1
53.2 | SN1
53.6 | SN1
53.5 | SN1
53.9 | SN1
53.9 | SN1
54 | SN1
54 | SN1
53.7 | SN1
53.8 | SN1
53.6 | SN1
53.5 | SN1
53.4 | SN1
53.2 | SN1
52.6 | SN1
52.3 | SN1
52 | SN1
51.7 | SN1
51.7 | SN1
51.6 | SN1
51.8 | SN1
51.8 | SN1
51.5 | SN1
51.7 | SN1
51.5 | SN1
51.3 | SN1
51.6 | SN1
51.5 | SN1
51.5 | SN1
51.5 | SN1
51.9 | SN1
52 | SN1
52.3 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.7 | SN1
52.5 | SN1
52.5 | SN1
52.9 | SN1
53 | SN1
52.6 | SN1
52.9 | SN1
52.9 | SN1
52.9 | SN1
53 | SN1
53 | SN1
53.2 | SN1
53.3 | SN1
53.6 | SN1
53.7 | SN1
53.6 | SN1
53.8 | SN1
53.8 | SN1
54.1 | SN1
54.1 | SN1
54.1 | SN1
53.9 | SN1
53.6 | SN1
53.1 | SN1
52.9 | SN1
52.2 | SN1
51.8 | SN1
51.6 | SN1
51.6 | SN1
51.5 | SN1
51.6 | SN1
51.5 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
51.7 | SN1
51.8 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
52.5 | SN1
52.5 | SN1
52.3 | SN1
52.6 | SN1
52.4 | SN1
52.7 | SN1
52.7 | SN1
52.9 | SN1
52.9 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
53.3 | SN1
53.1 | SN1
53.2 | SN1
53.4 | SN1
53.5 | SN1
54 | SN1
54.1 | SN1
54.1 | SN1
54.2 | SN1
54.1 | SN1
54 | SN1
53.7 | SN1
53.4 | SN1
53 | SN1
52.6 | SN1
52 | SN1
52 | SN1
51.9 | SN1
51.5 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.8 | SN1
51.7 | SN1
51.5 | SN1
51.8 | SN1
51.7 | SN1
51.5 | SN1
51.8 | SN1
51.7 | SN1
51.7 | SN1
51.8 | SN1
52.4 | SN1
51.9 | SN1
52.3 | SN1
52.2 | SN1
52.4 | SN1
52.4 | SN1
52.4 | SN1
52.2 | SN1
52.6 | SN1
52.5 | SN1
52.9 | SN1
52.9 | SN1
52.8 | SN1
53 | SN1
53 | SN1
53.4 | SN1
53 | SN1
53.3 | SN1
53.3 | SN1
53.2 | SN1
53.5 | SN1
53.7 | SN1
53.9 | SN1
54 | SN1
53.9 | SN1
53.6 | SN1
53.3 | SN1
52.9 | SN1
52.4 | SN1
52 | SN1
51.8 | SN1
51.6 | SN1
51.7 | SN1
51.5 | SN1
51.6 | SN1
51.5 | SN1
51.6 | SN1
51.5 | SN1
51.5 | SN1
51.5 | SN1
51.7 | SN1
52.2 | SN1
51.8 | SN1
51.9 | SN1
52.1 | SN1
52.2 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.5 | SN1
52.7 | SN1
53 | SN1
52.6 | SN1
52.6 | SN1
52.8 | SN1
52.7 | SN1
52.9 | SN1
52.5 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
53 | SN1
52.9 | SN1
52.2 | SN1
52.5 | SN1
52.4 | SN1
52.7 | SN1
52.1 | SN1
52 | SN1
51.8 | SN1
51.6 | SN1
51.4 | SN1
51.4 | SN1
51.6 | SN1
51.5 | SN1
51.5 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
52.1 | SN1
51.8 | SN1
52 | SN1
52 | SN1
52.9 | SN1
52.4 | SN1
52.7 | SN1
52.5 | SN1
52.8 | SN1
52.9 | SN1
52.8 | SN1
53 | SN1
52.9 | SN1
53.2 | SN1
53.1 | SN1
53 | SN1
53 | SN1
53 | SN1
53.3 | SN1
53.3 | SN1
53.2 | SN1
53.2 | SN1
53.3 | SN1
53.7 | SN1
53.5 | SN1
53.3 | SN1
53.6 | SN1
53.5 | SN1
53.4 | SN1
53.7 | SN1
53.7 | SN1
53.9 | SN1
53.8 | SN1
54.1 | SN1
54.1 | SN1
53.6 | SN1
52.8 | SN1
52.2 | SN1
51.8 | SN1
51.8 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
52 | SN1
52 | SN1
51.9 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
52.4 | SN1
52.5 | SN1
52.7 | SN1
52.7 | SN1
52.9 | SN1
53.1 | SN1
53.1 | SN1
53.1 | SN1
53.1 | SN1
53.1 | SN1
53.2 | SN1
53.5 | SN1
53.4 | SN1
52.9 | SN1
53.5 | SN1
53.5 | SN1
53.6 | SN1
54 | SN1
53.7 | SN1
53.9 | SN1
54.1 | SN1
54.4 | SN1
54.4 | SN1
54.1 | SN1
54.4 | SN1
54.4 | SN1
54.5 | SN1
54.2 | SN1
54.2 | SN1
53.6 | SN1
53.2 | SN1
52.1 | SN1
52.1 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.7 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
52.4 | SN1
52.3 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
52.9 | SN1
53.1 | SN1
52.8 | SN1
53.2 | SN1
52.9 | SN1
52.7 | SN1
53.1 | SN1
52.9 | SN1
53.2 | SN1
53 | SN1
53.2 | SN1
53.1 | SN1
53.2 | SN1
53.4 | SN1
53.1 | SN1
53.1 | SN1
53.4 | SN1
53.5 | SN1
53.4 | SN1
53.4 | SN1
53.7 | SN1
53.6 | SN1
53.4 | SN1
52.9 | SN1
52.8 | SN1
52.2 | SN1
51.8 | SN1
51.5 | SN1
52 | SN1
51.7 | SN1
51.7 | SN1
51.9 | SN1
51.7 | SN1
51.8 | SN1
51.6 | SN1
51.8 | SN1
51.7 | SN1
51.7 | SN1
52 | SN1
52.2 | SN1
52.4 | SN1
52.7 | SN1
52.8 | SN1
52.9 | SN1
52.8 | SN1
52.7 | SN1
53.1 | SN1
52.9 | SN1
52.9 | SN1
53 | SN1
52.8 | SN1
53.1 | SN1
53.4 | SN1
53.1 | SN1
52.9 | SN1
53.1 | SN1
53 | SN1
53.3 | SN1
53.3 | SN1
53.2 | SN1
53.2 | SN1
53.4 | SN1
53.5 | SN1
53.6 | SN1
53.7 | SN1
53.5 | SN1
0 | SN1
53.7 | SN1
53 | SN1
53.5 | SN1
52.9 | SN1
52.3 | SN1
51.9 | SN1
51.8 | SN1
51.6 | SN1
51.6 | SN1
51.7 | SN1
51.7 | SN1
51.9 | SN1
51.8 | SN1
51.7 | SN1
51.7 | SN1
52 | SN1
52.1 | SN1
52 | SN1
51.7 | SN1
52.1 | SN1
52.4 | SN1
52.6 | SN1
52.8 | SN1
52.8 | SN1
52.8 | SN1
52.9 | SN1
52.8 | SN1
53 | SN1
53.1 | SN1
52.8 | SN1
52.6 | SN1
52.6 | SN1
52.9 | SN1
52.9 | SN1
52.8 | SN1
52.8 | SN1
52.9 | SN1
52.6 | SN1
52.7 | SN1
52.5 | SN1
52.9 | SN1
52.7 | SN1
52.5 | SN1
53 | SN1
52.8 | SN1
53 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
52.4 | SN1
52.1 | SN1
52.2 | SN1
51.7 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.3 | SN1
51.8 | SN1
51.6 | SN1
51.4 | SN1
51.8 | SN1
52.1 | SN1
52.1 | SN1
51.8 | SN1
52.2 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.6 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
52.7 | SN1
53 | SN1
52.6 | SN1
53 | SN1
52.5 | SN1
52.9 | SN1
52.7 | SN1
52.7 | SN1
52.9 | SN1
52.9 | SN1
52.7 | SN1
53.1 | SN1
52.7 | SN1
52.4 | SN1
52.8 | SN1
52.7 | SN1
52.7 | SN1
53 | SN1
52.9 | SN1
52.9 | SN1
52.7 | SN1
52.5 | SN1
52.1 | SN1
52 | SN1
51.8 | SN1
51.9 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.6 | SN1
51.5 | SN1
51.7 | SN1
51.8 | SN1
51.6 | SN1
51.8 | SN1
52.1 | SN1
52.5 | SN1
52.7 | SN1
52.9 | SN1
52.8 | SN1
52.7 | SN1
52.5 | SN1
52.9 | SN1
52.7 | SN1
52.5 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.5 | SN1
52.7 | SN1
52.8 | SN1
52.9 | SN1
53 | SN1
52.9 | SN1
52.9 | SN1
52.9 | SN1
53.1 | SN1
52.9 | SN1
53 | SN1
53 | SN1
53 | SN1
53 | SN1
53.2 | SN1
52.9 | SN1
53 | SN1
53 | SN1
52.5 | SN1
52.4 | SN1
52.4 | SN1
52.1 | SN1
52 | SN1
51.9 | SN1
52 | SN1
51.6 | SN1
51.9 | SN1
51.9 | SN1
51.7 | SN1
52 | SN1
52 | SN1
52.3 | SN1
52.6 | SN1
52.7 | SN1
52.6 | SN1
52.4 | SN1
53 | SN1
53.1 | SN1
53 | SN1
52.8 | SN1
52.9 | SN1
53.1 | SN1
52.9 | SN1
52.9 | SN1
52.9 | SN1
52.9 | SN1
52.8 | SN1
52.9 | SN1
52.8 | SN1
52.7 | SN1
52.6 | SN1
53 | SN1
52.6 | SN1
52.6 | SN1
52.8 | SN1
52.7 | SN1
53 | SN1
52.8 | SN1
53.2 | SN1
53.1 | SN1
52.8 | SN1
53 | SN1
53.1 | SN1
53.4 | SN1
53.4 | SN1
52.9 | SN1
0 | SN1
52 | SN1
51.8 | SN1
51.9 | SN1
51.7 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.5 | SN1
51.7 | SN1
51.9 | SN1
51.7 | SN1
51.8 | SN1
52.1 | SN1
52.3 | SN1
52.2 | SN1
52.3 | SN1
52.6 | SN1
53 | SN1
52.8 | SN1
52.8 | SN1
52.9 | SN1
52.8 | SN1
53 | SN1
53.1 | SN1
52.9 | SN1
53.3 | SN1
53.3 | SN1
52.8 | SN1
53.5 | SN1
53.5 | SN1
53.8 | SN1
53.8 | SN1
53.8 | SN1
54.1 | SN1
53.9 | SN1
54.1 | SN1
54.3 | SN1
54.2 | SN1
54.6 | SN1
54.6 | SN1
54.5 | SN1
54.6 | SN1
54.5 | SN1
53.9 | SN1
53.3 | SN1
53.2 | SN1
52.9 | SN1
52.3 | SN1
52.4 | SN1
52.2 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
52 | SN1
52.1 | SN1
52.3 | SN1
51.8 | SN1
52.1 | SN1
52.4 | SN1
52.4 | SN1
52.7 | SN1
52.7 | SN1
52.9 | SN1
52.9 | SN1
53 | SN1
52.8 | SN1
53 | SN1
53.1 | SN1
53 | SN1
53.2 | SN1
53 | SN1
53.1 | SN1
53.1 | SN1
53.6 | SN1
53.6 | SN1
53.3 | SN1
53.6 | SN1
53.5 | SN1
53.6 | SN1
53.8 | SN1
53.9 | SN1
54.1 | SN1
53.8 | SN1
54.1 | SN1
54 | SN1
53.9 | SN1
54 | SN1
53.9 | SN1
54 | SN1
53.8 | SN1
53.3 | SN1
52.6 | SN1
52.2 | SN1
51.9 | SN1
51.8 | SN1
52.3 | SN1
52 | SN1
52.2 | SN1
52.2 | SN1
51.7 | SN1
51.7 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.6 | SN1
51.6 | SN1
51.9 | SN1
52.3 | SN1
52.8 | SN1
53.1 | SN1
53.4 | SN1
53.3 | SN1
53.4 | SN1
53 | SN1
53.5 | SN1
53.7 | SN1
53.8 | SN1
54.1 | SN1
54 | SN1
54.2 | SN1
54.2 | SN1
54.3 | SN1
54.4 | SN1
54.3 | SN1
54.4 | SN1
54.3 | SN1
54.4 | SN1
54.5 | SN1
54.6 | SN1
54.6 | SN1
54.2 | SN1
54.7 | SN1
54.6 | SN1
54.3 | SN1
53.9 | SN1
53.5 | SN1
52.8 | SN1
52.9 | SN1
52.8 | SN1
52.4 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.2 | SN1
52 | SN1
52 | SN1
52 | SN1
52 | SN1
51.8 | SN1
52.2 | SN1
52 | SN1
52.2 | SN1
52.5 | SN1
52.8 | SN1
53.1 | SN1
53.3 | SN1
53.4 | SN1
53.7 | SN1
54 | SN1
54.3 | SN1
54.4 | SN1
54.4 | SN1
54.6 | SN1
54.9 | SN1
54.8 | SN1
54.6 | SN1
54.7 | SN1
54.6 | SN1
54.8 | SN1
54.6 | SN1
54.7 | SN1
54.8 | SN1
54.7 | SN1
54.8 | SN1
54.5 | SN1
54.5 | SN1
54.5 | SN1
54.6 | SN1
54.8 | SN1
54.6 | SN1
54.4 | SN1
54 | SN1
53.2 | SN1
52.4 | SN1
52.1 | SN1
51.9 | SN1
51.9 | SN1
52 | SN1
52 | SN1
52.4 | SN1
51.9 | SN1
52.2 | SN1
52 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
51.8 | SN1
51.6 | SN1
51.8 | SN1
52.3 | SN1
52.7 | SN1
52.9 | SN1
53.2 | SN1
53.4 | SN1
53.2 | SN1
52.8 | SN1
53 | SN1
53.2 | SN1
53.2 | SN1
53.6 | SN1
53.3 | SN1
53.5 | SN1
53.8 | SN1
53.9 | SN1
53.9 | SN1
54 | SN1
54.1 | SN1
54 | SN1
54 | SN1
54.2 | SN1
54.3 | SN1
54.6 | SN1
54.5 | SN1
54.5 | SN1
54.4 | SN1
54.2 | SN1
54 | SN1
53.3 | SN1
52.8 | SN1
52.1 | SN1
51.6 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
51.7 | SN1
51.6 | SN1
51.9 | SN1
51.7 | SN1
52 | SN1
51.8 | SN1
52 | SN1
51.9 | SN1
51.7 | SN1
51.9 | SN1
52.4 | SN1
52.4 | SN1
53 | SN1
53.1 | SN1
53.1 | SN1
53.1 | SN1
53.1 | SN1
53.2 | SN1
53.1 | SN1
53.1 | SN1
53.2 | SN1
53.2 | SN1
53.4 | SN1
53.3 | SN1
53 | SN1
53.5 | SN1
53.4 | SN1
53.7 | SN1
54.3 | SN1
54.5 | SN1
54.7 | SN1
54.6 | SN1
54.6 | SN1
54.6 | SN1
54.7 | SN1
54.7 | SN1
54.7 | SN1
54.3 | SN1
54.2 | SN1
53.5 | SN1
53 | SN1
52.9 | SN1
52.8 | SN1
52.4 | SN1
52.1 | SN1
52.4 | SN1
51.8 | SN1
52 | SN1
51.7 | SN1
52 | SN1
51.8 | SN1
51.7 | SN1
52.3 | SN1
52.1 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
52.7 | SN1
53.1 | SN1
52.7 | SN1
53 | SN1
53.2 | SN1
53.1 | SN1
53.1 | SN1
53.2 | SN1
53.4 | SN1
53.5 | SN1
53.4 | SN1
53.7 | SN1
53.8 | SN1
54.2 | SN1
54.2 | SN1
54.5 | SN1
54.3 | SN1
54.5 | SN1
54.2 | SN1
54.4 | SN1
54.6 | SN1
54.5 | SN1
54.6 | SN1
54.6 | SN1
54.4 | SN1
54.4 | SN1
53.9 | SN1
54 | SN1
53.6 | SN1
53 | SN1
52.6 | SN1
52.3 | SN1
52.4 | SN1
52.2 | SN1
52.1 | SN1
52.2 | SN1
52 | SN1
52 | SN1
52.1 | SN1
52 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.5 | SN1
52.4 | SN1
52.6 | SN1
52.9 | SN1
53.1 | SN1
53.1 | SN1
52.7 | SN1
53 | SN1
53 | SN1
53.2 | SN1
53 | SN1
53 | SN1
53.3 | SN1
53.2 | SN1
53.5 | SN1
53.6 | SN1
53.7 | SN1
53.6 | SN1
53.6 | SN1
53.5 | SN1
53.7 | SN1
53.7 | SN1
53.7 | SN1
53.8 | SN1
53.9 | SN1
53.5 | SN1
53.8 | SN1
54.1 | SN1
54 | SN1
53.9 | SN1
53.8 | SN1
53.3 | SN1
53 | SN1
52.8 | SN1
52.4 | SN1
52.1 | SN1
52 | SN1
52.2 | SN1
51.7 | SN1
52 | SN1
52.2 | SN1
52 | SN1
52.1 | SN1
52.2 | SN1
52.3 | SN1
51.9 | SN1
52 | SN1
52.1 | SN1
52.5 | SN1
52.6 | SN1
52.9 | SN1
52.7 | SN1
53.2 | SN1
53.1 | SN1
53.1 | SN1
53.1 | SN1
52.9 | SN1
52.7 | SN1
52.9 | SN1
53.1 | SN1
53 | SN1
53.3 | SN1
53.6 | SN1
53.5 | SN1
53.5 | SN1
53.8 | SN1
53.9 | SN1
54 | SN1
54 | SN1
53.9 | SN1
54.2 | SN1
54 | SN1
54.2 | SN1
53.7 | SN1
54.1 | SN1
53.2 | SN1
53.4 | SN1
52.7 | SN1
52.4 | SN1
52.2 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
51.9 | SN1
52 | SN1
51.9 | SN1
51.9 | SN1
52 | SN1
52 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
52 | SN1
52.2 | SN1
52.5 | SN1
52.3 | SN1
52.6 | SN1
52.9 | SN1
52.7 | SN1
52.8 | SN1
52.6 | SN1
52.8 | SN1
52.6 | SN1
53 | SN1
52.8 | SN1
53.1 | SN1
53.3 | SN1
53.5 | SN1
53.7 | SN1
53.8 | SN1
53.8 | SN1
54 | SN1
54.1 | SN1
54.1 | SN1
54.2 | SN1
54.2 | SN1
54.3 | SN1
54.2 | SN1
54.1 | SN1
53.9 | SN1
53.3 | SN1
52.3 | SN1
52.1 | SN1
52 | SN1
52 | SN1
52 | SN1
51.9 | SN1
52 | SN1
51.9 | SN1
52.1 | SN1
52 | SN1
52 | SN1
52 | SN1
51.9 | SN1
51.9 | SN1
52 | SN1
52 | SN1
52.1 | SN1
52.2 | SN1
52.1 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52.2 | SN1
52.4 | SN1
52.3 | SN1
52.2 | SN1
52.4 | SN1
52.2 | SN1
52.3 | SN1
52.4 | SN1
52.2 | SN1
52.5 | SN1
52.2 | SN1
52.3 | SN1
52.6 | SN1
52.4 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.7 | SN1
52.5 | SN1
52.8 | SN1
52.7 | SN1
2.4 | SN1
0.7 | SN1
2.4 | SN1
52.2 | SN1
51.7 | SN1
51.5 | SN1
51.6 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
51.7 | SN1
52.3 | SN1
51.9 | SN1
51.6 | SN1
51.6 | SN1
51.7 | SN1
52 | SN1
52.5 | SN1
52 | SN1
52.6 | SN1
52.6 | SN1
52.9 | SN1
52.9 | SN1
52.7 | SN1
52.5 | SN1
52.4 | SN1
52.7 | SN1
52.6 | SN1
52.7 | SN1
52.4 | SN1
52.9 | SN1
52.8 | SN1
53 | SN1
52.8 | SN1
52.9 | SN1
52.8 | SN1
52.8 | SN1
52.7 | SN1
53 | SN1
52.9 | SN1
52.8 | SN1
52.6 | SN1
52.9 | SN1
52.7 | SN1
52.9 | SN1
52.8 | SN1
52.9 | SN1
52.8 | SN1
52.7 | SN1
52.1 | SN1
51.9 | SN1
51.8 | SN1
51.6 | SN1
51.7 | SN1
52.2 | SN1
52.1 | SN1
52.1 | SN1
52.3 | SN1
52.1 | SN1
52.4 | SN1
52.6 | SN1
52.2 | SN1
52.8 | SN1
52.7 | SN1
52.7 | SN1
52.9 | SN1
52.8 | SN1
53 | SN1
52.9 | SN1
53 | SN1
53 | SN1
52.8 | SN1
52.9 | SN1
53.1 | SN1
53.1 | SN1
53.2 | SN1
53.2 | SN1
53.1 | SN1
53.2 | SN1
53.1 | SN1
53.3 | SN1
53.2 | SN1
53.2 | SN1
53.3 | SN1
53.4 | SN1
53.6 | SN1
53.3 | SN1
53.4 | SN1
53.5 | SN1
53.7 | SN1
53.7 | SN1
53.7 | SN1
53.4 | SN1
53.3 | SN1
53.1 | SN1
52.6 | SN1
52.5 | SN1
52.1 | SN1
51.9 | SN1
52.1 | SN1
51.7 | SN1
51.6 | SN1
51.7 | SN1
51.7 | SN1
51.8 | SN1
51.9 | SN1
51.8 | SN1
51.6 | SN1
52 | SN1
52.6 | SN1
52.5 | SN1
52.8 | SN1
52.7 | SN1
52.5 | SN1
52.8 | SN1
52.9 | SN1
53 | SN1
53.2 | SN1
53.1 | SN1
53.1 | SN1
53.1 | SN1
53.4 | SN1
53.4 | SN1
53.4 | SN1
53.4 | SN1
53.5 | SN1
53.6 | SN1
53.9 | SN1
53.7 | SN1
53.9 | SN1
53.8 | SN1
54.1 | SN1
54 | SN1
54.1 | SN1
54 | SN1
54.1 | SN1
54.2 | SN1
53.8 | SN1
53.9 | SN1
49.3 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
52 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
51.8 | SN1
52.1 | SN1
52 | SN1
52 | SN1
51.8 | SN1
52.1 | SN1
51.8 | SN1
52.1 | SN1
52.3 | SN1
52.5 | SN1
52.4 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.6 | SN1
52.9 | SN1
52.8 | SN1
52.9 | SN1
52.9 | SN1
52.9 | SN1
52.9 | SN1
53 | SN1
53.3 | SN1
53.2 | SN1
53.5 | SN1
53.6 | SN1
53.5 | SN1
53.5 | SN1
53.6 | SN1
53.8 | SN1
53.6 | SN1
54 | SN1
53.9 | SN1
53.7 | SN1
53.6 | SN1
53.5 | SN1
52.7 | SN1
52.5 | SN1
52.3 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
52.2 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
51.9 | SN1
52 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.4 | SN1
52.8 | SN1
53.1 | SN1
53 | SN1
53.4 | SN1
53.6 | SN1
53.9 | SN1
54 | SN1
54.2 | SN1
54.1 | SN1
54.1 | SN1
54.3 | SN1
54.2 | SN1
54.5 | SN1
54.6 | SN1
54 | SN1
54.2 | SN1
54.3 | SN1
54.5 | SN1
54.4 | SN1
54.6 | SN1
54.7 | SN1
54.4 | SN1
54.4 | SN1
54.5 | SN1
54.2 | SN1
53.8 | SN1
53.1 | SN1
52.5 | SN1
52.2 | SN1
52.1 | SN1
51.9 | SN1
51.9 | SN1
52 | SN1
52 | SN1
52.1 | SN1
52 | SN1
52 | SN1
52.1 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
52.4 | SN1
52.6 | SN1
52.6 | SN1
52.8 | SN1
52.7 | SN1
52.7 | SN1
52.9 | SN1
52.8 | SN1
53 | SN1
53.2 | SN1
53.5 | SN1
53.5 | SN1
53.7 | SN1
53.6 | SN1
53.8 | SN1
53.7 | SN1
53.6 | SN1
53.9 | SN1
54.2 | SN1
53.8 | SN1
54.1 | SN1
54.1 | SN1
54 | SN1
54.2 | SN1
54 | SN1
54.2 | SN1
54.2 | SN1
53.9 | SN1
53.6 | SN1
53.2 | SN1
52.7 | SN1
52.4 | SN1
52.3 | SN1
52.3 | SN1
52.1 | SN1
52.2 | SN1
52 | SN1
52 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
52.1 | SN1
52.2 | SN1
51.8 | SN1
51.9 | SN1
52 | SN1
52 | SN1
52.2 | SN1
52.2 | SN1
52.4 | SN1
52.7 | SN1
52.6 | SN1
52.8 | SN1
52.6 | SN1
52.8 | SN1
52.9 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
52.6 | SN1
52.8 | SN1
53.2 | SN1
53.3 | SN1
53.4 | SN1
53.5 | SN1
53.6 | SN1
53.8 | SN1
53.9 | SN1
53.6 | SN1
53.7 | SN1
53.5 | SN1
53.1 | SN1
52.6 | SN1
52.1 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
51.7 | SN1
52 | SN1
51.9 | SN1
51.9 | SN1
51.7 | SN1
51.7 | SN1
51.8 | SN1
52 | SN1
52.4 | SN1
52.4 | SN1
52.6 | SN1
53.2 | SN1
53.5 | SN1
53.3 | SN1
53.6 | SN1
53.9 | SN1
53.9 | SN1
54.1 | SN1
54.2 | SN1
54.3 | SN1
54.5 | SN1
54.7 | SN1
54.7 | SN1
54.7 | SN1
55 | SN1
55 | SN1
55.2 | SN1
55.2 | SN1
54.9 | SN1
55.1 | SN1
55.4 | SN1
55.1 | SN1
54.8 | SN1
54.5 | SN1
54.4 | SN1
53.3 | SN1
52.5 | SN1
52 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
52 | SN1
52 | SN1
51.9 | SN1
51.8 | SN1
51.9 | SN1
52 | SN1
52 | SN1
52 | SN1
52 | SN1
51.8 | SN1
51.7 | SN1
51.7 | SN1
51.8 | SN1
51.9 | SN1
52.3 | SN1
52.2 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52.6 | SN1
52.7 | SN1
52.9 | SN1
53.1 | SN1
52.9 | SN1
53.4 | SN1
53.1 | SN1
53.4 | SN1
53.3 | SN1
53.2 | SN1
53.4 | SN1
53.5 | SN1
53.5 | SN1
53.4 | SN1
53.7 | SN1
53.3 | SN1
53.4 | SN1
53.6 | SN1
53.4 | SN1
53.1 | SN1
52.8 | SN1
52.4 | SN1
52.1 | SN1
52 | SN1
51.7 | SN1
51.7 | SN1
51.8 | SN1
51.9 | SN1
52.1 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
51.7 | SN1
51.7 | SN1
51.6 | SN1
52 | SN1
51.9 | SN1
52.4 | SN1
52.3 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.8 | SN1
52.7 | SN1
52.6 | SN1
52.6 | SN1
52.3 | SN1
52.6 | SN1
52.6 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.5 | SN1
52.4 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.9 | SN1
52.4 | SN1
51.9 | SN1
51.6 | SN1
51.6 | SN1
51.4 | SN1
51.5 | SN1
51.7 | SN1
51.7 | SN1
51.5 | SN1
52 | SN1
51.9 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
52 | SN1
52 | SN1
51.6 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
51.8 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
52 | SN1
52 | SN1
51.9 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
51.9 | SN1
51.6 | SN1
52.2 | SN1
51.8 | SN1
51.9 | SN1
51.7 | SN1
51.8 | SN1
51.9 | SN1
52 | SN1
52.1 | SN1
52.2 | SN1
52.5 | SN1
52.4 | SN1
52 | SN1
52.2 | SN1
52.2 | SN1
51.7 | SN1
51.7 | SN1
52 | SN1
51.4 | SN1
51.4 | SN1
51.7 | SN1
51.5 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.9 | SN1
51.8 | SN1
51.6 | SN1
52 | SN1
51.7 | SN1
51.5 | SN1
51.6 | SN1
51.2 | SN1
51.5 | SN1
52.1 | SN1
51.7 | SN1
51.6 | SN1
52.2 | SN1
52.1 | SN1
51.9 | SN1
52 | SN1
52.5 | SN1
52.1 | SN1
52.2 | SN1
51.9 | SN1
52.3 | SN1
51.9 | SN1
52.3 | SN1
52.4 | SN1
52.7 | SN1
52.6 | SN1
52.7 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
52.7 | SN1
52.8 | SN1
52.7 | SN1
52.4 | SN1
52.3 | SN1
52.2 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.7 | SN1
51.5 | SN1
51.8 | SN1
51.5 | SN1
51.9 | SN1
51.7 | SN1
52 | SN1
52.1 | SN1
51.5 | SN1
51.7 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
52.5 | SN1
52.4 | SN1
52.8 | SN1
52.8 | SN1
52.9 | SN1
53 | SN1
53 | SN1
53.1 | SN1
53.1 | SN1
53.1 | SN1
53.2 | SN1
53.4 | SN1
53.2 | SN1
53.1 | SN1
53.5 | SN1
53.9 | SN1
53.9 | SN1
53.9 | SN1
53.8 | SN1
54.1 | SN1
54.6 | SN1
54.6 | SN1
54.9 | SN1
54.9 | SN1
54 | SN1
53.8 | SN1
53.4 | SN1
53 | SN1
52.5 | SN1
52.1 | SN1
51.4 | SN1
51.6 | SN1
51.2 | SN1
51.6 | SN1
51.7 | SN1
51.3 | SN1
51.6 | SN1
51.5 | SN1
51.4 | SN1
51.6 | SN1
51.3 | SN1
51.6 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51.5 | SN1
51.5 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
51.9 | SN1
52 | SN1
51.7 | SN1
52.1 | SN1
52 | SN1
51.7 | SN1
52.2 | SN1
52.3 | SN1
52.2 | SN1
52 | SN1
52.1 | SN1
51.9 | SN1
52 | SN1
52.3 | SN1
52.3 | SN1
52.6 | SN1
52.4 | SN1
52.5 | SN1
52.2 | SN1
52.3 | SN1
52.5 | SN1
52.4 | SN1
52.3 | SN1
52.1 | SN1
51.8 | SN1
51.6 | SN1
51.2 | SN1
51.6 | SN1
51.3 | SN1
51.5 | SN1
51.4 | SN1
51.5 | SN1
52.1 | SN1
51.7 | SN1
51.7 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.5 | SN1
51.7 | SN1
51.7 | SN1
51.4 | SN1
51.8 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
52.2 | SN1
52.1 | SN1
52 | SN1
51.9 | SN1
52.3 | SN1
52.1 | SN1
52.3 | SN1
52.4 | SN1
52.8 | SN1
52.5 | SN1
52.6 | SN1
52.7 | SN1
52.6 | SN1
52.7 | SN1
52.9 | SN1
52.9 | SN1
52.8 | SN1
52.8 | SN1
53 | SN1
52.9 | SN1
53.2 | SN1
53 | SN1
52.9 | SN1
52.9 | SN1
52.2 | SN1
52 | SN1
51.3 | SN1
51.6 | SN1
51.5 | SN1
51.8 | SN1
51.7 | SN1
51.7 | SN1
52 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
51.6 | SN1
51.9 | SN1
51.6 | SN1
52 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
51.8 | SN1
52.4 | SN1
52.1 | SN1
52.2 | SN1
52 | SN1
51.9 | SN1
52.1 | SN1
52.3 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
52.3 | SN1
52.6 | SN1
52.3 | SN1
52.3 | SN1
52.5 | SN1
52.4 | SN1
52.7 | SN1
52.8 | SN1
52.7 | SN1
52.7 | SN1
52.4 | SN1
52 | SN1
51.6 | SN1
51.5 | SN1
51.5 | SN1
51.6 | SN1
51.7 | SN1
51.7 | SN1
51.6 | SN1
51.6 | SN1
51.7 | SN1
51.9 | SN1
52 | SN1
51.7 | SN1
51.7 | SN1
51.8 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
52.2 | SN1
52.1 | SN1
52 | SN1
52.3 | SN1
52.4 | SN1
52.3 | SN1
52.6 | SN1
52.1 | SN1
52.6 | SN1
52.7 | SN1
52.3 | SN1
52.7 | SN1
52.6 | SN1
52.6 | SN1
53.1 | SN1
52.8 | SN1
53 | SN1
52.8 | SN1
52.8 | SN1
52.8 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
53.1 | SN1
53.1 | SN1
53.2 | SN1
53.1 | SN1
52.8 | SN1
52.8 | SN1
52.4 | SN1
51.3 | SN1
51.6 | SN1
51.5 | SN1
51.5 | SN1
51.5 | SN1
51.5 | SN1
51.6 | SN1
51.6 | SN1
51.9 | SN1
51.7 | SN1
52.1 | SN1
51.6 | SN1
52.1 | SN1
52.4 | SN1
52.2 | SN1
52.1 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.2 | SN1
52.5 | SN1
52.4 | SN1
52.6 | SN1
52.4 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.8 | SN1
52.7 | SN1
53 | SN1
52.9 | SN1
52.7 | SN1
52.9 | SN1
52.8 | SN1
52.9 | SN1
52.9 | SN1
52.7 | SN1
52.8 | SN1
53 | SN1
53 | SN1
53 | SN1
52.9 | SN1
52.9 | SN1
52.5 | SN1
52.4 | SN1
51.9 | SN1
51.9 | SN1
51.6 | SN1
51.8 | SN1
51.6 | SN1
51.6 | SN1
51.4 | SN1
52 | SN1
51.9 | SN1
52.2 | SN1
51.8 | SN1
52.1 | SN1
52.1 | SN1
52.5 | SN1
52.2 | SN1
52.3 | SN1
52.1 | SN1
52.3 | SN1
52.5 | SN1
52.1 | SN1
52.5 | SN1
52.3 | SN1
52.4 | SN1
52.6 | SN1
52.2 | SN1
52.4 | SN1
52.3 | SN1
52.4 | SN1
52.3 | SN1
52.3 | SN1
52.5 | SN1
52.6 | SN1
52.5 | SN1
52.2 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.6 | SN1
52.8 | SN1
52.6 | SN1
52.6 | SN1
52.8 | SN1
52.8 | SN1
52.4 | SN1
52.4 | SN1
52.3 | SN1
52.4 | SN1
52.4 | SN1
52.2 | SN1
52.1 | SN1
51.9 | SN1
51.9 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52.4 | SN1
52.2 | SN1
52.2 | SN1
52.4 | SN1
52.8 | SN1
52.3 | SN1
52.4 | SN1
52.6 | SN1
52.8 | SN1
52.6 | SN1
52.8 | SN1
52.6 | SN1
52.2 | SN1
52.3 | SN1
52.4 | SN1
52.3 | SN1
52.6 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
53.1 | SN1
52.7 | SN1
52.6 | SN1
52.8 | SN1
52.7 | SN1
52.8 | SN1
52.6 | SN1
52.5 | SN1
53.2 | SN1
53.1 | SN1
52.9 | SN1
52.9 | SN1
53 | SN1
53 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52.4 | SN1
52.4 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
52.2 | SN1
51.9 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.3 | SN1
52.2 | SN1
52.5 | SN1
52.4 | SN1
52.3 | SN1
52.3 | SN1
52.6 | SN1
52.5 | SN1
52.3 | SN1
52.6 | SN1
52.5 | SN1
52.7 | SN1
52.8 | SN1
53 | SN1
52.6 | SN1
52.6 | SN1
53.1 | SN1
52.8 | SN1
52.6 | SN1
52.5 | SN1
52.5 | SN1
52.7 | SN1
52.5 | SN1
52.6 | SN1
52.9 | SN1
52.8 | SN1
52.7 | SN1
52.8 | SN1
52.7 | SN1
52.6 | SN1
52.5 | SN1
52.4 | SN1
52.3 | SN1
52.2 | SN1
52.2 | SN1
52.1 | SN1
52.1 | SN1
51.9 | SN1
52 | SN1
51.8 | SN1
52 | SN1
52 | SN1
52.2 | SN1
52 | SN1
51.7 | SN1
52 | SN1
51.8 | SN1
52.2 | SN1
52.4 | SN1
52.3 | SN1
52.7 | SN1
52.6 | SN1
52.8 | SN1
52.5 | SN1
52.6 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.4 | SN1
52.9 | SN1
52.4 | SN1
52.4 | SN1
52.6 | SN1
53.1 | SN1
53.3 | SN1
53.9 | SN1
54 | SN1
54.2 | SN1
53.8 | SN1
54 | SN1
53.7 | SN1
53.7 | SN1
53.5 | SN1
53.5 | SN1
53.4 | SN1
53.1 | SN1
53.1 | SN1
52.8 | SN1
52.7 | SN1
52.3 | SN1
52.5 | SN1
52.7 | SN1
52.5 | SN1
52.4 | SN1
52.3 | SN1
52.2 | SN1
52.4 | SN1
52.3 | SN1
52.3 | SN1
52.7 | SN1
52.5 | SN1
52.4 | SN1
52.8 | SN1
52.6 | SN1
52.8 | SN1
52.6 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.8 | SN1
52.7 | SN1
52.6 | SN1
52.3 | SN1
52.4 | SN1
52.5 | SN1
52.4 | SN1
52.4 | SN1
52.3 | SN1
52.5 | SN1
52.7 | SN1
52.6 | SN1
52.3 | SN1
52.7 | SN1
52.6 | SN1
52.4 | SN1
52.3 | SN1
52.1 | SN1
51.9 | SN1
52 | SN1
51.7 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
51.7 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
52 | SN1
51.9 | SN1
52 | SN1
52 | SN1
51.9 | SN1
52 | SN1
51.9 | SN1
52.2 | SN1
52.6 | SN1
52.6 | SN1
52.3 | SN1
52.3 | SN1
52.2 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
52.2 | SN1
52.4 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
53 | SN1
52.8 | SN1
52.9 | SN1
52.9 | SN1
52.7 | SN1
52.6 | SN1
52.8 | SN1
52.9 | SN1
52.6 | SN1
52.8 | SN1
52.7 | SN1
52.7 | SN1
52.5 | SN1
52.3 | SN1
52.6 | SN1
52.4 | SN1
52.2 | SN1
51.9 | SN1
52.1 | SN1
52.3 | SN1
52.1 | SN1
52.3 | SN1
52.4 | SN1
52.6 | SN1
52.9 | SN1
52.9 | SN1
52.8 | SN1
52.6 | SN1
52.6 | SN1
52.6 | SN1
52.7 | SN1
52.6 | SN1
53 | SN1
52.9 | SN1
53.2 | SN1
52.9 | SN1
52.9 | SN1
53 | SN1
53.1 | SN1
53 | SN1
53.3 | SN1
53.2 | SN1
53.3 | SN1
53.2 | SN1
53 | SN1
53.1 | SN1
53.2 | SN1
53.2 | SN1
53.2 | SN1
53.2 | SN1
53.2 | SN1
53.2 | SN1
53.3 | SN1
53.3 | SN1
53.2 | SN1
53.4 | SN1
53.1 | SN1
53.1 | SN1
53 | SN1
53 | SN1
52.9 | SN1
52.4 | SN1
52 | SN1
52.2 | SN1
52.1 | SN1
51.9 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.5 | SN1
51.7 | SN1
51.6 | SN1
51.6 | SN1
52.1 | SN1
51.7 | SN1
52.4 | SN1
52 | SN1
52.4 | SN1
52.7 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
52.8 | SN1
52.6 | SN1
52.9 | SN1
52.9 | SN1
52.6 | SN1
52.8 | SN1
52.9 | SN1
52.8 | SN1
53.1 | SN1
52.9 | SN1
53 | SN1
53.1 | SN1
53.2 | SN1
53.6 | SN1
53.7 | SN1
54.1 | SN1
54.3 | SN1
53.9 | SN1
54.1 | SN1
53.9 | SN1
54.1 | SN1
54 | SN1
53.9 | SN1
53.7 | SN1
53.7 | SN1
53.1 | SN1
52.6 | SN1
52.3 | SN1
51.9 | SN1
52 | SN1
51.7 | SN1
51.9 | SN1
51.7 | SN1
51.8 | SN1
51.7 | SN1
51.7 | SN1
51.5 | SN1
51.7 | SN1
51.7 | SN1
51.9 | SN1
52 | SN1
52.6 | SN1
52.6 | SN1
53.1 | SN1
53.3 | SN1
53.3 | SN1
53.5 | SN1
53.4 | SN1
53.5 | SN1
53.9 | SN1
54 | SN1
54 | SN1
54.4 | SN1
54.7 | SN1
54.6 | SN1
54.5 | SN1
54.4 | SN1
54.5 | SN1
54.2 | SN1
54.7 | SN1
54.8 | SN1
54.5 | SN1
54.6 | SN1
54 | SN1
54.2 | SN1
54.2 | SN1
54.2 | SN1
54.2 | SN1
53.8 | SN1
52.8 | SN1
52.4 | SN1
52.2 | SN1
52.2 | SN1
51.9 | SN1
51.8 | SN1
51.9 | SN1
51.7 | SN1
51.6 | SN1
51.9 | SN1
52.2 | SN1
52.2 | SN1
52.9 | SN1
52.5 | SN1
52.9 | SN1
52.5 | SN1
52.4 | SN1
52.6 | SN1
52.8 | SN1
52.9 | SN1
52.9 | SN1
53.2 | SN1
53.1 | SN1
53.3 | SN1
53.1 | SN1
53.1 | SN1
53.1 | SN1
53.3 | SN1
53.6 | SN1
53.7 | SN1
53.9 | SN1
53.8 | SN1
53.5 | SN1
53.5 | SN1
53.4 | SN1
53.6 | SN1
53.3 | SN1
53.3 | SN1
53.5 | SN1
53.4 | SN1
53.6 | SN1
53.5 | SN1
53.5 | SN1
53.3 | SN1
53.3 | SN1
52.9 | SN1
52.9 | SN1
52.5 | SN1
52.6 | SN1
52.8 | SN1
52.8 | SN1
52.6 | SN1
52.4 | SN1
52 | SN1
52.1 | SN1
52 | SN1
52 | SN1
51.8 | SN1
52.1 | SN1
52 | SN1
52.2 | SN1
52.4 | SN1
51.9 | SN1
52 | SN1
52 | SN1
52.2 | SN1
52.6 | SN1
52.7 | SN1
53 | SN1
53.1 | SN1
53.3 | SN1
53.2 | SN1
53.3 | SN1
53.2 | SN1
53.1 | SN1
53.4 | SN1
53.2 | SN1
53.3 | SN1
53.6 | SN1
53.7 | SN1
53.7 | SN1
54.1 | SN1
53.9 | SN1
53.8 | SN1
53.9 | SN1
53.8 | SN1
53.7 | SN1
53.8 | SN1
53.8 | SN1
53.8 | SN1
53.7 | SN1
53.6 | SN1
53.4 | SN1
53.3 | SN1
52.7 | SN1
52.4 | SN1
52.3 | SN1
52.4 | SN1
52.2 | SN1
51.8 | SN1
52 | SN1
52.2 | SN1
51.9 | SN1
52.2 | SN1
52 | SN1
52.2 | SN1
52 | SN1
52.3 | SN1
51.9 | SN1
52.1 | SN1
52.5 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
52.5 | SN1
53.2 | SN1
53.1 | SN1
52.9 | SN1
53.5 | SN1
53.2 | SN1
53.2 | SN1
53.8 | SN1
53.4 | SN1
53.5 | SN1
53.6 | SN1
53.5 | SN1
53.8 | SN1
53.9 | SN1
54 | SN1
54.3 | SN1
54 | SN1
54.2 | SN1
54.1 | SN1
54 | SN1
54 | SN1
53.9 | SN1
53.8 | SN1
53.7 | SN1
53.4 | SN1
53.3 | SN1
53 | SN1
52.6 | SN1
52.3 | SN1
52.2 | SN1
52.2 | SN1
52.2 | SN1
51.9 | SN1
52.2 | SN1
51.9 | SN1
52.4 | SN1
52.3 | SN1
52.1 | SN1
52.2 | SN1
51.6 | SN1
52.3 | SN1
52.4 | SN1
52.5 | SN1
52.8 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
52.6 | SN1
52.8 | SN1
53 | SN1
53.1 | SN1
52.9 | SN1
52.8 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
52.9 | SN1
52.9 | SN1
53.1 | SN1
53 | SN1
53.2 | SN1
53.6 | SN1
53.7 | SN1
53.9 | SN1
53.8 | SN1
53.8 | SN1
53.5 | SN1
53.6 | SN1
53.2 | SN1
53 | SN1
53.3 | SN1
52.9 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52 | SN1
51.9 | SN1
52 | SN1
51.9 | SN1
51.8 | SN1
51.7 | SN1
52.1 | SN1
52.2 | SN1
52.2 | SN1
52 | SN1
52.2 | SN1
52.3 | SN1
52.4 | SN1
52.4 | SN1
52.6 | SN1
52.5 | SN1
52.9 | SN1
53 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.9 | SN1
53.1 | SN1
52.9 | SN1
52.6 | SN1
52.9 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
52.8 | SN1
53.2 | SN1
53 | SN1
53.9 | SN1
53.5 | SN1
53.9 | SN1
53.7 | SN1
54 | SN1
53.8 | SN1
54 | SN1
53.8 | SN1
53.8 | SN1
54 | SN1
53.5 | SN1
53.9 | SN1
53.1 | SN1
53.2 | SN1
53.1 | SN1
53 | SN1
53 | SN1
53 | SN1
53.2 | SN1
53 | SN1
53 | SN1
52.9 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
52.9 | SN1
52.9 | SN1
52.7 | SN1
52.7 | SN1
53.1 | SN1
53 | SN1
52.9 | SN1
53.4 | SN1
53.1 | SN1
53.3 | SN1
52.8 | SN1
53.2 | SN1
53.4 | SN1
53.1 | SN1
53.1 | SN1
52.9 | SN1
52.7 | SN1
52.9 | SN1
52.6 | SN1
52.8 | SN1
52.5 | SN1
52.6 | SN1
52.3 | SN1
52.1 | SN1
52 | SN1
52.1 | SN1
52.4 | SN1
52.2 | SN1
52.3 | SN1
52.4 | SN1
52.1 | SN1
52.4 | SN1
52.3 | SN1
52.2 | SN1
52 | SN1
52.1 | SN1
52.3 | SN1
51.9 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.4 | SN1
52.5 | SN1
52.2 | SN1
52.5 | SN1
52.6 | SN1
52.7 | SN1
52.6 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.8 | SN1
52.5 | SN1
52.7 | SN1
53 | SN1
52.9 | SN1
53.3 | SN1
53.4 | SN1
53.2 | SN1
53.2 | SN1
53 | SN1
53 | SN1
52.7 | SN1
51.8 | SN1
51.5 | SN1
51.5 | SN1
51.6 | SN1
51.6 | SN1
51.7 | SN1
51.5 | SN1
51.3 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.2 | SN1
51.9 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.8 | SN1
53.3 | SN1
53.5 | SN1
53.7 | SN1
53.7 | SN1
53.7 | SN1
53.4 | SN1
53.2 | SN1
53.1 | SN1
53.1 | SN1
52.9 | SN1
53.1 | SN1
53.1 | SN1
53 | SN1
53.3 | SN1
53.4 | SN1
53.4 | SN1
53.9 | SN1
53.7 | SN1
53.9 | SN1
53.6 | SN1
53.7 | SN1
53.4 | SN1
53.6 | SN1
53.4 | SN1
53.4 | SN1
53.1 | SN1
53 | SN1
52.6 | SN1
52.4 | SN1
51.9 | SN1
51.5 | SN1
51.5 | SN1
51.4 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.5 | SN1
51.5 | SN1
51.8 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
52.1 | SN1
51.9 | SN1
52.2 | SN1
52.4 | SN1
52.7 | SN1
52.9 | SN1
53.1 | SN1
52.7 | SN1
53 | SN1
53.1 | SN1
52.8 | SN1
53 | SN1
52.9 | SN1
53.2 | SN1
53.3 | SN1
53.6 | SN1
53.6 | SN1
53.8 | SN1
53.9 | SN1
53.9 | SN1
53.7 | SN1
53.7 | SN1
53.7 | SN1
53.5 | SN1
53.6 | SN1
53.7 | SN1
53.6 | SN1
54 | SN1
53.8 | SN1
53.7 | SN1
53.2 | SN1
52.7 | SN1
52.2 | SN1
51.9 | SN1
51.8 | SN1
51.4 | SN1
51.4 | SN1
51.2 | SN1
51.6 | SN1
51.4 | SN1
51.3 | SN1
51.5 | SN1
51.4 | SN1
51.6 | SN1
51.5 | SN1
51.7 | SN1
51.9 | SN1
52.1 | SN1
52.2 | SN1
52.1 | SN1
52.2 | SN1
52.3 | SN1
52.3 | SN1
52.2 | SN1
52.4 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.7 | SN1
52.9 | SN1
53 | SN1
52.9 | SN1
52.9 | SN1
52.9 | SN1
53 | SN1
53 | SN1
52.9 | SN1
53.1 | SN1
53.1 | SN1
52.9 | SN1
53.4 | SN1
53.2 | SN1
53.3 | SN1
53.1 | SN1
52.8 | SN1
52.6 | SN1
52.6 | SN1
52.1 | SN1
51.5 | SN1
51.6 | SN1
51.5 | SN1
51.5 | SN1
51.4 | SN1
51.3 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.4 | SN1
51.5 | SN1
51.5 | SN1
51.5 | SN1
51.4 | SN1
52 | SN1
52.3 | SN1
52.4 | SN1
52.3 | SN1
52.4 | SN1
52.4 | SN1
52.5 | SN1
52.7 | SN1
52.9 | SN1
52.7 | SN1
52.9 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
53.1 | SN1
52.7 | SN1
52.8 | SN1
52.9 | SN1
52.9 | SN1
53.1 | SN1
52.8 | SN1
52.9 | SN1
53.1 | SN1
52.9 | SN1
53.1 | SN1
52.9 | SN1
53.2 | SN1
52.9 | SN1
52.8 | SN1
52.4 | SN1
52.1 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.5 | SN1
51.6 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
52.4 | SN1
52.5 | SN1
52.3 | SN1
52.7 | SN1
52.7 | SN1
52.5 | SN1
52.8 | SN1
52.6 | SN1
52.9 | SN1
52.9 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
52.8 | SN1
53 | SN1
52.9 | SN1
53 | SN1
53.1 | SN1
53.2 | SN1
53.5 | SN1
53.4 | SN1
53.6 | SN1
53.5 | SN1
53.3 | SN1
53.5 | SN1
53.1 | SN1
52.9 | SN1
52.7 | SN1
52.6 | SN1
52.2 | SN1
52.1 | SN1
52 | SN1
51.6 | SN1
51.6 | SN1
51.4 | SN1
51.6 | SN1
51.3 | SN1
51.4 | SN1
51.2 | SN1
51.3 | SN1
51.5 | SN1
51.3 | SN1
51.6 | SN1
51.2 | SN1
51.2 | SN1
51.5 | SN1
52 | SN1
52.5 | SN1
52.9 | SN1
52.5 | SN1
52.9 | SN1
52.6 | SN1
52.8 | SN1
52.7 | SN1
53.2 | SN1
53.1 | SN1
52.9 | SN1
53 | SN1
52.9 | SN1
53.1 | SN1
53.1 | SN1
53.1 | SN1
53.4 | SN1
53.4 | SN1
53.2 | SN1
53.3 | SN1
53.4 | SN1
53.4 | SN1
53.7 | SN1
53.5 | SN1
53.6 | SN1
53.9 | SN1
53.7 | SN1
53.5 | SN1
53 | SN1
52.9 | SN1
52.4 | SN1
51.9 | SN1
51.8 | SN1
51.5 | SN1
51.4 | SN1
51.5 | SN1
51.6 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.5 | SN1
51.4 | SN1
51.5 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
52.4 | SN1
52.4 | SN1
52.5 | SN1
52.4 | SN1
52.7 | SN1
52.3 | SN1
52.7 | SN1
52.8 | SN1
53.1 | SN1
53.1 | SN1
53 | SN1
53.2 | SN1
53.1 | SN1
53.1 | SN1
53 | SN1
53.2 | SN1
53.2 | SN1
53.3 | SN1
53.4 | SN1
53.6 | SN1
53.7 | SN1
53.9 | SN1
53.7 | SN1
53.6 | SN1
53.5 | SN1
53.4 | SN1
53.1 | SN1
53 | SN1
52.6 | SN1
52.1 | SN1
51.8 | SN1
51.6 | SN1
51.5 | SN1
51.6 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51.2 | SN1
51.2 | SN1
51.6 | SN1
51.4 | SN1
51.5 | SN1
51.5 | SN1
51.4 | SN1
51.8 | SN1
52 | SN1
52.3 | SN1
52.4 | SN1
52.7 | SN1
52.6 | SN1
52.7 | SN1
53 | SN1
52.7 | SN1
53.2 | SN1
53 | SN1
53 | SN1
53.2 | SN1
53 | SN1
53.4 | SN1
53.4 | SN1
53.5 | SN1
53.7 | SN1
53.5 | SN1
53.8 | SN1
53.7 | SN1
53.8 | SN1
53.8 | SN1
53.8 | SN1
53.7 | SN1
53.6 | SN1
53.4 | SN1
53.3 | SN1
53 | SN1
52.4 | SN1
52.5 | SN1
51.6 | SN1
51.5 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.5 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.4 | SN1
51.2 | SN1
51.3 | SN1
51.5 | SN1
51.9 | SN1
52.2 | SN1
52.3 | SN1
52.4 | SN1
52.2 | SN1
52.4 | SN1
52.5 | SN1
52.9 | SN1
52.7 | SN1
53 | SN1
52.8 | SN1
53 | SN1
53 | SN1
52.9 | SN1
52.9 | SN1
52.8 | SN1
53 | SN1
53 | SN1
53.2 | SN1
53.4 | SN1
53.3 | SN1
53 | SN1
53.1 | SN1
52.8 | SN1
53 | SN1
52.9 | SN1
52.4 | SN1
52.6 | SN1
52.1 | SN1
52 | SN1
51.6 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.5 | SN1
51.3 | SN1
51.4 | SN1
51.5 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.5 | SN1
51.7 | SN1
51.6 | SN1
52.3 | SN1
52.1 | SN1
52.4 | SN1
52.4 | SN1
52.1 | SN1
52.4 | SN1
52.3 | SN1
52.8 | SN1
52.6 | SN1
52.7 | SN1
52.9 | SN1
52.8 | SN1
53 | SN1
52.9 | SN1
53.5 | SN1
53.3 | SN1
53.8 | SN1
53.2 | SN1
53.4 | SN1
53.5 | SN1
53.5 | SN1
53.6 | SN1
53.7 | SN1
53.6 | SN1
53.1 | SN1
53 | SN1
52.6 | SN1
52 | SN1
51.8 | SN1
51.7 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.5 | SN1
51.3 | SN1
51.3 | SN1
51.2 | SN1
51 | SN1
51.1 | SN1
51.1 | SN1
51.1 | SN1
51.2 | SN1
51.5 | SN1
51.8 | SN1
52 | SN1
52.4 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
52.3 | SN1
52.4 | SN1
52.7 | SN1
53.2 | SN1
53.1 | SN1
52.9 | SN1
53.3 | SN1
53.5 | SN1
53.9 | SN1
53.6 | SN1
53.8 | SN1
54 | SN1
54.3 | SN1
54.5 | SN1
54.4 | SN1
54.5 | SN1
54.4 | SN1
54.1 | SN1
54 | SN1
53.6 | SN1
53.3 | SN1
52.9 | SN1
52.5 | SN1
52.3 | SN1
51.5 | SN1
51.2 | SN1
51 | SN1
51.2 | SN1
51.1 | SN1
51 | SN1
51 | SN1
51.1 | SN1
51.2 | SN1
51.1 | SN1
51 | SN1
51.2 | SN1
51.1 | SN1
51.1 | SN1
51.2 | SN1
51.5 | SN1
51.5 | SN1
52 | SN1
51.9 | SN1
51.7 | SN1
51.7 | SN1
52.3 | SN1
52.7 | SN1
52.5 | SN1
52.9 | SN1
52.9 | SN1
53.2 | SN1
53 | SN1
53 | SN1
52.9 | SN1
52.9 | SN1
52.9 | SN1
53 | SN1
52.7 | SN1
52.9 | SN1
53.1 | SN1
53.3 | SN1
52.8 | SN1
53.5 | SN1
53.2 | SN1
53.2 | SN1
52.9 | SN1
52.7 | SN1
52.5 | SN1
52 | SN1
51.4 | SN1
51.1 | SN1
50.9 | SN1
51 | SN1
51.2 | SN1
51.1 | SN1
51 | SN1
51.1 | SN1
51 | SN1
51 | SN1
51.2 | SN1
51.1 | SN1
51.1 | SN1
51.2 | SN1
51.1 | SN1
51.1 | SN1
51.2 | SN1
51.6 | SN1
51.2 | SN1
51.7 | SN1
51.6 | SN1
51.9 | SN1
51.9 | SN1
52.2 | SN1
52 | SN1
52.1 | SN1
52.3 | SN1
52.3 | SN1
52.4 | SN1
52.8 | SN1
52.4 | SN1
52.7 | SN1
52.7 | SN1
52.9 | SN1
53 | SN1
53 | SN1
53.3 | SN1
53.2 | SN1
53 | SN1
52.8 | SN1
53 | SN1
52.8 | SN1
52.8 | SN1
52.6 | SN1
52.5 | SN1
52.2 | SN1
51.8 | SN1
51.5 | SN1
51.1 | SN1
51.1 | SN1
50.9 | SN1
51.1 | SN1
51.2 | SN1
51.1 | SN1
51.1 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
51.4 | SN1
51.6 | SN1
51.9 | SN1
51.8 | SN1
51.9 | SN1
52 | SN1
52.3 | SN1
52.3 | SN1
52.4 | SN1
52.2 | SN1
52.1 | SN1
52.4 | SN1
52.7 | SN1
52.4 | SN1
52.4 | SN1
52.7 | SN1
52.5 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
52.7 | SN1
52.9 | SN1
53 | SN1
53.1 | SN1
52.8 | SN1
52.7 | SN1
52.3 | SN1
52 | SN1
52 | SN1
51.6 | SN1
51.5 | SN1
51.3 | SN1
51.5 | SN1
51.3 | SN1
51.2 | SN1
51.1 | SN1
51.1 | SN1
51.2 | SN1
51.1 | SN1
50.9 | SN1
51.2 | SN1
51.2 | SN1
50.9 | SN1
51.3 | SN1
51.3 | SN1
51.6 | SN1
51.5 | SN1
51.9 | SN1
52.2 | SN1
51.8 | SN1
52 | SN1
52.2 | SN1
52.3 | SN1
52 | SN1
52.4 | SN1
52.4 | SN1
52.4 | SN1
52.6 | SN1
52.6 | SN1
52.2 | SN1
52.4 | SN1
52.5 | SN1
52.4 | SN1
52.2 | SN1
52.9 | SN1
52.7 | SN1
52.5 | SN1
52.6 | SN1
52.9 | SN1
52.4 | SN1
52.9 | SN1
0 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
51.7 | SN1
51.6 | SN1
51.5 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.1 | SN1
51.1 | SN1
51.1 | SN1
51.1 | SN1
51 | SN1
51.1 | SN1
50.9 | SN1
51 | SN1
51 | SN1
51.1 | SN1
50.9 | SN1
51.7 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
52 | SN1
52.1 | SN1
52.3 | SN1
52 | SN1
52.2 | SN1
52.2 | SN1
51.8 | SN1
52.1 | SN1
52.2 | SN1
52.3 | SN1
52.4 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.5 | SN1
52.5 | SN1
52.3 | SN1
52.2 | SN1
51.6 | SN1
51.5 | SN1
51 | SN1
50.5 | SN1
50.4 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
51.1 | SN1
50.7 | SN1
50.8 | SN1
50.9 | SN1
50.9 | SN1
51 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
51 | SN1
51.5 | SN1
51.5 | SN1
51.7 | SN1
51.9 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
52.2 | SN1
51.9 | SN1
52.2 | SN1
52.6 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.6 | SN1
52.4 | SN1
52.6 | SN1
52.4 | SN1
52.4 | SN1
52.9 | SN1
52.9 | SN1
52.8 | SN1
52.8 | SN1
52.7 | SN1
52.5 | SN1
52.7 | SN1
52.5 | SN1
52.3 | SN1
46 | SN1
52 | SN1
51.7 | SN1
51.6 | SN1
51.5 | SN1
51.3 | SN1
51.2 | SN1
51.2 | SN1
50.6 | SN1
50.5 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
51.1 | SN1
50.9 | SN1
51.1 | SN1
51.2 | SN1
51.4 | SN1
51.6 | SN1
51.8 | SN1
52 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52.2 | SN1
52.1 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.1 | SN1
52.3 | SN1
52.3 | SN1
52.4 | SN1
52.4 | SN1
52.4 | SN1
52.3 | SN1
52.4 | SN1
52.4 | SN1
52.4 | SN1
52.3 | SN1
52.2 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
51.4 | SN1
21 | SN1
24.7 | SN1
30.9 | SN1
30.8 | SN1
30.5 | SN1
31.4 | SN1
32.4 | SN1
32.9 | SN1
33.1 | SN1
33.3 | SN1
32.9 | SN1
33 | SN1
32.4 | SN1
32.1 | SN1
31.7 | SN1
31 | SN1
31 | SN1
30.4 | SN1
30 | SN1
29.8 | SN1
29.7 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
51.2 | SN1
51.1 | SN1
50.7 | SN1
50.6 | SN1
50.9 | SN1
50.3 | SN1
50.7 | SN1
50.3 | SN1
50.5 | SN1
50.5 | SN1
50.6 | SN1
50.7 | SN1
50.7 | SN1
50.9 | SN1
51.5 | SN1
51.4 | SN1
51.6 | SN1
51.1 | SN1
51.7 | SN1
51.3 | SN1
51.2 | SN1
51.1 | SN1
51.1 | SN1
52.1 | SN1
52 | SN1
51.6 | SN1
51.4 | SN1
51.6 | SN1
51.2 | SN1
51.4 | SN1
51.6 | SN1
51.3 | SN1
51.3 | SN1
51.5 | SN1
51.3 | SN1
51.7 | SN1
51.4 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.4 | SN1
51.4 | SN1
51.2 | SN1
51 | SN1
51.4 | SN1
51.1 | SN1
50.7 | SN1
50.5 | SN1
50.3 | SN1
50.4 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.3 | SN1
50.4 | SN1
50.7 | SN1
50.4 | SN1
51.2 | SN1
51.8 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.6 | SN1
51.6 | SN1
51.7 | SN1
52.3 | SN1
52 | SN1
51.9 | SN1
52.1 | SN1
52.3 | SN1
52.1 | SN1
51.6 | SN1
51.7 | SN1
52.1 | SN1
51.7 | SN1
51.9 | SN1
51.7 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.8 | SN1
51.9 | SN1
52 | SN1
51.8 | SN1
51.4 | SN1
51.2 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.6 | SN1
50.4 | SN1
50.3 | SN1
50.6 | SN1
50.6 | SN1
50.7 | SN1
50.6 | SN1
50.8 | SN1
50.5 | SN1
50.8 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.8 | SN1
51.3 | SN1
51.2 | SN1
51.7 | SN1
51.7 | SN1
51.9 | SN1
52.1 | SN1
51.9 | SN1
52.2 | SN1
51.7 | SN1
51.7 | SN1
51.9 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
51.9 | SN1
52 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
52.2 | SN1
51.9 | SN1
52.1 | SN1
52.1 | SN1
51.9 | SN1
51.7 | SN1
51.7 | SN1
51.4 | SN1
51.3 | SN1
50.8 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
51 | SN1
51.2 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
50.7 | SN1
50.9 | SN1
50.6 | SN1
50.7 | SN1
51.6 | SN1
52.1 | SN1
51.7 | SN1
51.4 | SN1
51.5 | SN1
51.8 | SN1
51.7 | SN1
51.9 | SN1
51.7 | SN1
51.4 | SN1
52 | SN1
51.8 | SN1
51.7 | SN1
52.3 | SN1
52.1 | SN1
52.1 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
52.2 | SN1
52.3 | SN1
52.2 | SN1
52.2 | SN1
51.7 | SN1
51.9 | SN1
51.9 | SN1
51.7 | SN1
51.3 | SN1
51.3 | SN1
51.2 | SN1
51.6 | SN1
51.4 | SN1
50.7 | SN1
50.9 | SN1
50.9 | SN1
50.7 | SN1
51.1 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
51 | SN1
50.7 | SN1
50.9 | SN1
50.7 | SN1
50.6 | SN1
51.1 | SN1
51.3 | SN1
51.7 | SN1
51.6 | SN1
52.2 | SN1
51.9 | SN1
52 | SN1
52 | SN1
52.1 | SN1
52 | SN1
51.8 | SN1
52.1 | SN1
52.1 | SN1
51.9 | SN1
52 | SN1
52.4 | SN1
52.3 | SN1
52.4 | SN1
52.5 | SN1
52.3 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.5 | SN1
52.3 | SN1
52.3 | SN1
52.1 | SN1
52 | SN1
51.7 | SN1
51.3 | SN1
51.1 | SN1
51 | SN1
51.2 | SN1
51.2 | SN1
50.7 | SN1
50.5 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
51.7 | SN1
51.6 | SN1
51 | SN1
50.7 | SN1
50.7 | SN1
51.1 | SN1
51.1 | SN1
51.6 | SN1
51.5 | SN1
51.5 | SN1
51.4 | SN1
51.6 | SN1
51.8 | SN1
52.2 | SN1
52 | SN1
52 | SN1
52 | SN1
52.2 | SN1
52.3 | SN1
52.6 | SN1
52.7 | SN1
53 | SN1
52.8 | SN1
52.6 | SN1
52.6 | SN1
52.4 | SN1
52.2 | SN1
52.3 | SN1
52.3 | SN1
52.2 | SN1
52.3 | SN1
52.2 | SN1
51.8 | SN1
51.6 | SN1
51 | SN1
51.1 | SN1
51.3 | SN1
50.7 | SN1
51.1 | SN1
51.6 | SN1
51 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
51.5 | SN1
51.7 | SN1
51 | SN1
51.3 | SN1
51.6 | SN1
51.8 | SN1
52.4 | SN1
52.6 | SN1
53.1 | SN1
52.9 | SN1
52.9 | SN1
53.1 | SN1
52.7 | SN1
52.6 | SN1
52.5 | SN1
53.4 | SN1
53.1 | SN1
53.1 | SN1
52.9 | SN1
52.9 | SN1
52.9 | SN1
53.2 | SN1
53.3 | SN1
53.2 | SN1
53.4 | SN1
53 | SN1
52.9 | SN1
53.1 | SN1
53.2 | SN1
53.1 | SN1
53.3 | SN1
53.5 | SN1
52.8 | SN1
52.6 | SN1
52.2 | SN1
51.9 | SN1
51.2 | SN1
50.8 | SN1
50.9 | SN1
50.6 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.6 | SN1
51.1 | SN1
51 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
50.6 | SN1
51.1 | SN1
50.9 | SN1
51 | SN1
51.4 | SN1
51.6 | SN1
51.9 | SN1
51.8 | SN1
52 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.6 | SN1
52.4 | SN1
52.4 | SN1
51.9 | SN1
52.2 | SN1
52.3 | SN1
52.4 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.7 | SN1
52.6 | SN1
52.4 | SN1
52.1 | SN1
51.8 | SN1
51.4 | SN1
51.2 | SN1
51.1 | SN1
51 | SN1
51.1 | SN1
50.9 | SN1
50.8 | SN1
51 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
51 | SN1
51.2 | SN1
51.1 | SN1
51.1 | SN1
51.1 | SN1
51.1 | SN1
51.1 | SN1
51.7 | SN1
51.6 | SN1
51.6 | SN1
51.7 | SN1
51.7 | SN1
51.8 | SN1
51.6 | SN1
52 | SN1
52 | SN1
52.3 | SN1
52.3 | SN1
52 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
52.2 | SN1
52.6 | SN1
52.4 | SN1
52.3 | SN1
52 | SN1
51.8 | SN1
51.8 | SN1
51.4 | SN1
51.3 | SN1
51.2 | SN1
51 | SN1
51 | SN1
51 | SN1
51 | SN1
51.1 | SN1
51.1 | SN1
50.9 | SN1
51 | SN1
51 | SN1
51 | SN1
51 | SN1
51.1 | SN1
51 | SN1
51.1 | SN1
51.3 | SN1
51.1 | SN1
51.6 | SN1
51.7 | SN1
51.8 | SN1
51.9 | SN1
52 | SN1
51.6 | SN1
52 | SN1
52 | SN1
52.2 | SN1
52 | SN1
52 | SN1
51.9 | SN1
52.2 | SN1
51.8 | SN1
52 | SN1
52 | SN1
51.8 | SN1
52 | SN1
51.9 | SN1
51.8 | SN1
52.2 | SN1
52.2 | SN1
52.1 | SN1
52.3 | SN1
52 | SN1
51.9 | SN1
51.6 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.6 | SN1
51.4 | SN1
51.3 | SN1
51.4 | SN1
51.4 | SN1
51.2 | SN1
51.3 | SN1
51.2 | SN1
51.2 | SN1
51.4 | SN1
51.6 | SN1
51.5 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
52.1 | SN1
52 | SN1
52.2 | SN1
52.2 | SN1
52.5 | SN1
52.3 | SN1
52.7 | SN1
52.6 | SN1
52.5 | SN1
52.4 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.4 | SN1
52.5 | SN1
52.3 | SN1
52.6 | SN1
52.5 | SN1
52.3 | SN1
51.7 | SN1
51.9 | SN1
51.6 | SN1
51.8 | SN1
51.2 | SN1
51.2 | SN1
51 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
50.7 | SN1
50.8 | SN1
50.5 | SN1
50.9 | SN1
50.7 | SN1
50.9 | SN1
50.8 | SN1
51.1 | SN1
51.7 | SN1
51.5 | SN1
51.7 | SN1
51.9 | SN1
51.7 | SN1
51.6 | SN1
51.6 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
51.6 | SN1
51.9 | SN1
52.1 | SN1
52 | SN1
52.1 | SN1
52.3 | SN1
52.5 | SN1
52.4 | SN1
52.4 | SN1
52.6 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
52.1 | SN1
51.8 | SN1
51.7 | SN1
51.1 | SN1
50.9 | SN1
50.7 | SN1
50.5 | SN1
50.6 | SN1
50.7 | SN1
50.3 | SN1
50.5 | SN1
50.8 | SN1
50.6 | SN1
50.7 | SN1
50.5 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
51 | SN1
50.8 | SN1
51.5 | SN1
51.5 | SN1
51.6 | SN1
52 | SN1
51.5 | SN1
51.6 | SN1
52 | SN1
52.1 | SN1
52 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
52 | SN1
52 | SN1
52.2 | SN1
51.9 | SN1
52.1 | SN1
52.1 | SN1
52.4 | SN1
52 | SN1
52.3 | SN1
52.5 | SN1
52.1 | SN1
52.2 | SN1
52.1 | SN1
51.6 | SN1
51.6 | SN1
51.5 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.2 | SN1
51.5 | SN1
51.2 | SN1
51.1 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.9 | SN1
51.2 | SN1
51.4 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
51.6 | SN1
52.1 | SN1
52 | SN1
52.1 | SN1
52 | SN1
52.4 | SN1
52 | SN1
51.8 | SN1
52.3 | SN1
52 | SN1
52.4 | SN1
52.2 | SN1
52.4 | SN1
52.3 | SN1
52.4 | SN1
52.8 | SN1
52.4 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.2 | SN1
51.8 | SN1
51.8 | SN1
51.6 | SN1
51.4 | SN1
51.5 | SN1
51.3 | SN1
50.7 | SN1
50.9 | SN1
50.5 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
51 | SN1
51.5 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.6 | SN1
51.7 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
52.4 | SN1
52.3 | SN1
52.4 | SN1
52 | SN1
52.1 | SN1
52.2 | SN1
52 | SN1
52.1 | SN1
52.2 | SN1
52.6 | SN1
52.4 | SN1
52.3 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.5 | SN1
51.4 | SN1
51.2 | SN1
50.7 | SN1
50.7 | SN1
50.5 | SN1
50.6 | SN1
50.7 | SN1
50.5 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.5 | SN1
50.8 | SN1
50.6 | SN1
50.8 | SN1
50.6 | SN1
50.8 | SN1
51.1 | SN1
51.6 | SN1
51.3 | SN1
51.9 | SN1
52 | SN1
52.1 | SN1
52 | SN1
51.9 | SN1
52.2 | SN1
52.2 | SN1
52 | SN1
52.3 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.6 | SN1
52.7 | SN1
53.1 | SN1
52.7 | SN1
53.1 | SN1
53 | SN1
52.9 | SN1
52.7 | SN1
52.6 | SN1
52 | SN1
51.7 | SN1
51.5 | SN1
51.2 | SN1
51.3 | SN1
51 | SN1
50.8 | SN1
50.2 | SN1
50.6 | SN1
50.3 | SN1
50.4 | SN1
50.6 | SN1
50.4 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.3 | SN1
50.1 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.8 | SN1
51.5 | SN1
51.2 | SN1
51.5 | SN1
51.7 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
51.8 | SN1
52.3 | SN1
52.2 | SN1
52.7 | SN1
52.5 | SN1
52.1 | SN1
52.4 | SN1
52 | SN1
52.3 | SN1
52.4 | SN1
52 | SN1
52.2 | SN1
52.2 | SN1
52.5 | SN1
52.3 | SN1
52.2 | SN1
52.4 | SN1
52 | SN1
51.7 | SN1
51.1 | SN1
51.1 | SN1
51 | SN1
50.7 | SN1
50.3 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.5 | SN1
50.2 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
50.3 | SN1
50.5 | SN1
50.4 | SN1
50.2 | SN1
50.5 | SN1
50.7 | SN1
51.3 | SN1
51.3 | SN1
51.7 | SN1
51.4 | SN1
51.9 | SN1
51.8 | SN1
52 | SN1
52 | SN1
51.7 | SN1
51.9 | SN1
52.4 | SN1
52.2 | SN1
52.1 | SN1
52.3 | SN1
52.1 | SN1
52.5 | SN1
52.2 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.6 | SN1
52.9 | SN1
52.8 | SN1
52.5 | SN1
52.2 | SN1
52.1 | SN1
51.8 | SN1
51.4 | SN1
51.1 | SN1
50.7 | SN1
50.3 | SN1
50.2 | SN1
50.5 | SN1
50.4 | SN1
50.9 | SN1
50.3 | SN1
50.6 | SN1
50.5 | SN1
50.7 | SN1
51.1 | SN1
50.4 | SN1
50.3 | SN1
50.1 | SN1
50.1 | SN1
50.1 | SN1
50.3 | SN1
50.6 | SN1
50.8 | SN1
51.2 | SN1
51.4 | SN1
51.3 | SN1
51.4 | SN1
51.2 | SN1
51.6 | SN1
52 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
52.1 | SN1
52.1 | SN1
51.8 | SN1
51.9 | SN1
52.1 | SN1
51.9 | SN1
52.2 | SN1
51.8 | SN1
52.1 | SN1
51.9 | SN1
52.1 | SN1
51.8 | SN1
51.9 | SN1
51.4 | SN1
51.1 | SN1
51.1 | SN1
50.9 | SN1
50.4 | SN1
50.5 | SN1
50.7 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.5 | SN1
50.5 | SN1
50.6 | SN1
50.5 | SN1
50.4 | SN1
50.6 | SN1
50.8 | SN1
50.9 | SN1
51.5 | SN1
51.5 | SN1
51.6 | SN1
51.8 | SN1
51.6 | SN1
51.8 | SN1
51.8 | SN1
52.2 | SN1
51.8 | SN1
51.7 | SN1
52.1 | SN1
52 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
52.2 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.4 | SN1
51.1 | SN1
50.7 | SN1
50.8 | SN1
50.6 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.9 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.5 | SN1
50.9 | SN1
51.1 | SN1
51 | SN1
51.3 | SN1
51.5 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.9 | SN1
51.7 | SN1
51.6 | SN1
51.4 | SN1
51.7 | SN1
52.2 | SN1
52 | SN1
51.9 | SN1
52.3 | SN1
52 | SN1
51.9 | SN1
51.9 | SN1
52.3 | SN1
52.2 | SN1
52.3 | SN1
52.3 | SN1
52.1 | SN1
51.9 | SN1
51.7 | SN1
51.5 | SN1
51.5 | SN1
51.3 | SN1
51 | SN1
50.7 | SN1
51 | SN1
50.5 | SN1
50.8 | SN1
51.1 | SN1
50.9 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.6 | SN1
50.5 | SN1
50.8 | SN1
50.7 | SN1
51.2 | SN1
51.1 | SN1
51.3 | SN1
51.2 | SN1
51.6 | SN1
51.8 | SN1
51.7 | SN1
52 | SN1
51.8 | SN1
51.9 | SN1
51.8 | SN1
51.9 | SN1
52.1 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
52.2 | SN1
52.2 | SN1
52.2 | SN1
51.8 | SN1
52.2 | SN1
52.3 | SN1
52 | SN1
51.7 | SN1
51.6 | SN1
51.3 | SN1
51.3 | SN1
51.1 | SN1
51 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.9 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.9 | SN1
51.1 | SN1
50.9 | SN1
51.4 | SN1
51.7 | SN1
51.7 | SN1
51.3 | SN1
51.7 | SN1
51.7 | SN1
51.5 | SN1
51.5 | SN1
51.4 | SN1
51.8 | SN1
51.9 | SN1
52.2 | SN1
51.9 | SN1
52 | SN1
52.1 | SN1
52.2 | SN1
52.2 | SN1
52 | SN1
52 | SN1
52.2 | SN1
52.1 | SN1
52.4 | SN1
52.2 | SN1
52 | SN1
52 | SN1
51.7 | SN1
51.6 | SN1
51.1 | SN1
51.3 | SN1
51 | SN1
51 | SN1
50.5 | SN1
50.8 | SN1
50.8 | SN1
51 | SN1
50.9 | SN1
51 | SN1
51 | SN1
50.9 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.6 | SN1
50.8 | SN1
50.8 | SN1
51.2 | SN1
51.3 | SN1
51.4 | SN1
51.5 | SN1
51.8 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.6 | SN1
51.8 | SN1
51.8 | SN1
52 | SN1
51.8 | SN1
51.8 | SN1
52 | SN1
51.9 | SN1
52 | SN1
52 | SN1
52.2 | SN1
51.9 | SN1
52.1 | SN1
52 | SN1
52.2 | SN1
51.6 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.7 | SN1
51.5 | SN1
51.2 | SN1
50.9 | SN1
50.5 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
50.7 | SN1
50.9 | SN1
51 | SN1
50.7 | SN1
51.1 | SN1
51 | SN1
51.1 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.1 | SN1
51.3 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.5 | SN1
51.6 | SN1
51.6 | SN1
51.9 | SN1
52 | SN1
51.9 | SN1
51.9 | SN1
52 | SN1
52 | SN1
51.9 | SN1
51.9 | SN1
52 | SN1
51.9 | SN1
52.1 | SN1
51.5 | SN1
51.9 | SN1
52.1 | SN1
51.6 | SN1
51.9 | SN1
51.3 | SN1
51.4 | SN1
51.2 | SN1
51.3 | SN1
51.2 | SN1
51.2 | SN1
50.9 | SN1
50.8 | SN1
50.9 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
51 | SN1
51 | SN1
51.2 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.7 | SN1
51.7 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
52.3 | SN1
52.2 | SN1
52 | SN1
52.3 | SN1
52.3 | SN1
52.1 | SN1
52.5 | SN1
52.1 | SN1
52.2 | SN1
52 | SN1
52.4 | SN1
52 | SN1
51.8 | SN1
51.7 | SN1
51.7 | SN1
51.2 | SN1
51.1 | SN1
51 | SN1
51 | SN1
50.8 | SN1
50.6 | SN1
50.5 | SN1
50.5 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.9 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
51.4 | SN1
51.3 | SN1
51.4 | SN1
51.6 | SN1
51.3 | SN1
51.7 | SN1
51.6 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.5 | SN1
52.5 | SN1
51.4 | SN1
51.5 | SN1
51.8 | SN1
51.7 | SN1
51.9 | SN1
52 | SN1
52.2 | SN1
52.1 | SN1
52.2 | SN1
52 | SN1
52.2 | SN1
52.3 | SN1
52.3 | SN1
52.1 | SN1
52.2 | SN1
51.8 | SN1
51.9 | SN1
51.6 | SN1
51.6 | SN1
51.4 | SN1
51.3 | SN1
51.1 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.9 | SN1
51 | SN1
50.7 | SN1
50.5 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
51.4 | SN1
51.4 | SN1
51.7 | SN1
51.6 | SN1
51.8 | SN1
51.6 | SN1
51.9 | SN1
51.8 | SN1
51.9 | SN1
52 | SN1
52 | SN1
51.9 | SN1
51.8 | SN1
52.1 | SN1
51.9 | SN1
52.3 | SN1
52 | SN1
52.3 | SN1
52.1 | SN1
52.3 | SN1
52.2 | SN1
52.2 | SN1
52.4 | SN1
52.3 | SN1
52.6 | SN1
52.3 | SN1
52.2 | SN1
52.1 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
52 | SN1
51.6 | SN1
51.9 | SN1
51.2 | SN1
51 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
50.7 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.6 | SN1
51.1 | SN1
50.9 | SN1
51.5 | SN1
51.4 | SN1
51.7 | SN1
51.6 | SN1
52.1 | SN1
52 | SN1
52 | SN1
52 | SN1
51.9 | SN1
52.1 | SN1
52.3 | SN1
52.2 | SN1
52.2 | SN1
52.2 | SN1
52.5 | SN1
52.3 | SN1
52.3 | SN1
52.1 | SN1
52.4 | SN1
52.5 | SN1
52.4 | SN1
52.6 | SN1
52.3 | SN1
52.2 | SN1
51.8 | SN1
51.8 | SN1
51.5 | SN1
51.4 | SN1
51.5 | SN1
51.4 | SN1
51.2 | SN1
50.9 | SN1
51 | SN1
50.8 | SN1
50.9 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.6 | SN1
50.5 | SN1
51 | SN1
50.8 | SN1
51 | SN1
51.5 | SN1
51.2 | SN1
51.5 | SN1
51.6 | SN1
51.8 | SN1
51.9 | SN1
52.1 | SN1
52 | SN1
52.2 | SN1
51.9 | SN1
51.9 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.5 | SN1
52.3 | SN1
52.1 | SN1
51.7 | SN1
51.9 | SN1
51.8 | SN1
51.4 | SN1
51.5 | SN1
51.4 | SN1
51.1 | SN1
51.1 | SN1
51 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
50.7 | SN1
50.8 | SN1
50.6 | SN1
50.9 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.9 | SN1
50.9 | SN1
51.5 | SN1
51.6 | SN1
51.7 | SN1
51.9 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
52.1 | SN1
51.6 | SN1
51.9 | SN1
51.7 | SN1
52 | SN1
52.1 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
52.1 | SN1
52.3 | SN1
52.2 | SN1
52.1 | SN1
52.3 | SN1
52.2 | SN1
51.9 | SN1
51.5 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.7 | SN1
51.4 | SN1
51.2 | SN1
51.2 | SN1
51.1 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.5 | SN1
50.8 | SN1
50.6 | SN1
50.4 | SN1
50.7 | SN1
51.1 | SN1
51.1 | SN1
50.9 | SN1
51.3 | SN1
51.3 | SN1
51.6 | SN1
51.5 | SN1
51.7 | SN1
51.6 | SN1
51.7 | SN1
51.8 | SN1
52 | SN1
51.9 | SN1
52.1 | SN1
51.7 | SN1
51.9 | SN1
52.3 | SN1
51.9 | SN1
52 | SN1
52 | SN1
52 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
51.5 | SN1
51.7 | SN1
51.3 | SN1
51.5 | SN1
51.2 | SN1
51.3 | SN1
51.3 | SN1
51.2 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.6 | SN1
50.9 | SN1
50.7 | SN1
50.8 | SN1
50.6 | SN1
50.8 | SN1
50.6 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
51 | SN1
50.9 | SN1
51 | SN1
51.2 | SN1
51.2 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.5 | SN1
51.6 | SN1
51.7 | SN1
51.2 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
51.8 | SN1
52.1 | SN1
52.1 | SN1
51.7 | SN1
51.8 | SN1
52 | SN1
51.6 | SN1
51.2 | SN1
51.2 | SN1
51.3 | SN1
51 | SN1
51.1 | SN1
51 | SN1
51 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.9 | SN1
50.7 | SN1
51.3 | SN1
51 | SN1
51.3 | SN1
51 | SN1
51.5 | SN1
51.3 | SN1
51.3 | SN1
51.2 | SN1
51.4 | SN1
51.6 | SN1
51.5 | SN1
51.6 | SN1
51.5 | SN1
51.4 | SN1
51.3 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
51.5 | SN1
51.7 | SN1
51.6 | SN1
51.7 | SN1
51.5 | SN1
51.8 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.4 | SN1
50.8 | SN1
50.6 | SN1
50.5 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.8 | SN1
50.9 | SN1
50.9 | SN1
51.2 | SN1
51.2 | SN1
51.5 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.5 | SN1
51.5 | SN1
51.5 | SN1
52 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
52.1 | SN1
51.7 | SN1
51.7 | SN1
51.6 | SN1
51.5 | SN1
51.8 | SN1
51.5 | SN1
51.9 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.4 | SN1
51.3 | SN1
51.2 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.6 | SN1
51 | SN1
50.9 | SN1
50.6 | SN1
50.9 | SN1
50.9 | SN1
51.1 | SN1
51.5 | SN1
51.2 | SN1
51.1 | SN1
51.5 | SN1
51.4 | SN1
51.6 | SN1
51.5 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.5 | SN1
51.6 | SN1
51.4 | SN1
51.5 | SN1
51.5 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
51.9 | SN1
52.1 | SN1
51.9 | SN1
52.1 | SN1
52.2 | SN1
52.1 | SN1
52 | SN1
51.7 | SN1
51.5 | SN1
51.1 | SN1
51.1 | SN1
50.9 | SN1
50.9 | SN1
51 | SN1
50.8 | SN1
50.6 | SN1
50.7 | SN1
50.9 | SN1
50.7 | SN1
51 | SN1
51 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
51.1 | SN1
51.4 | SN1
51.5 | SN1
52.1 | SN1
52.2 | SN1
52.1 | SN1
51.9 | SN1
51.7 | SN1
51.4 | SN1
51.7 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51.6 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
51.9 | SN1
52.1 | SN1
52.1 | SN1
52.3 | SN1
52.1 | SN1
52.2 | SN1
52 | SN1
52.2 | SN1
52.1 | SN1
52 | SN1
51.6 | SN1
51.7 | SN1
51.2 | SN1
51.2 | SN1
51.1 | SN1
51.1 | SN1
50.8 | SN1
50.6 | SN1
50.8 | SN1
50.8 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
50.3 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.7 | SN1
50.5 | SN1
50.6 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
51.3 | SN1
51.4 | SN1
51.4 | SN1
51.2 | SN1
51.7 | SN1
51.6 | SN1
51.8 | SN1
52.1 | SN1
51.8 | SN1
52.2 | SN1
52 | SN1
52 | SN1
52.4 | SN1
52.2 | SN1
52.6 | SN1
52.2 | SN1
52.4 | SN1
52.2 | SN1
52.1 | SN1
51.9 | SN1
51.7 | SN1
51.9 | SN1
51.5 | SN1
51.4 | SN1
51.7 | SN1
51 | SN1
50.9 | SN1
51 | SN1
51 | SN1
50.9 | SN1
51.1 | SN1
51 | SN1
51 | SN1
51 | SN1
51 | SN1
51 | SN1
51 | SN1
50.9 | SN1
51.4 | SN1
51.2 | SN1
51.8 | SN1
52 | SN1
52 | SN1
52.1 | SN1
52.3 | SN1
52.4 | SN1
52.3 | SN1
52.3 | SN1
52.4 | SN1
52.7 | SN1
52.7 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
52.7 | SN1
52.9 | SN1
52.7 | SN1
52.5 | SN1
52.1 | SN1
51.9 | SN1
51.8 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51 | SN1
51.2 | SN1
51.2 | SN1
51 | SN1
51 | SN1
51.1 | SN1
51.2 | SN1
51 | SN1
51.2 | SN1
51.4 | SN1
51.6 | SN1
51.5 | SN1
51.8 | SN1
51.7 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
52 | SN1
52.1 | SN1
52 | SN1
51.9 | SN1
52 | SN1
52 | SN1
52.2 | SN1
52.3 | SN1
52.1 | SN1
52.2 | SN1
52.4 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.4 | SN1
52.1 | SN1
52.2 | SN1
52.3 | SN1
52.2 | SN1
52.3 | SN1
51.7 | SN1
51.5 | SN1
51.4 | SN1
51.1 | SN1
51.2 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
50.9 | SN1
50.8 | SN1
50.6 | SN1
50.4 | SN1
50.2 | SN1
50.2 | SN1
50.3 | SN1
50.2 | SN1
50.2 | SN1
50.4 | SN1
50.5 | SN1
50.8 | SN1
51.1 | SN1
51 | SN1
51.6 | SN1
51.3 | SN1
51.5 | SN1
51.3 | SN1
51.5 | SN1
51.5 | SN1
51.7 | SN1
51.7 | SN1
51.6 | SN1
51.9 | SN1
51.6 | SN1
51.8 | SN1
51.9 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
52 | SN1
51.9 | SN1
52 | SN1
52.2 | SN1
51.9 | SN1
52.3 | SN1
51.7 | SN1
51.6 | SN1
51.2 | SN1
51.3 | SN1
51.5 | SN1
51.7 | SN1
51.5 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51 | SN1
50.7 | SN1
50.7 | SN1
50.5 | SN1
50.5 | SN1
50.2 | SN1
50.5 | SN1
50.3 | SN1
50.3 | SN1
50.2 | SN1
50.4 | SN1
50.7 | SN1
50.9 | SN1
51 | SN1
51.3 | SN1
51.9 | SN1
51.7 | SN1
51.5 | SN1
51.7 | SN1
51.9 | SN1
51.8 | SN1
51.7 | SN1
51.9 | SN1
51.9 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
52 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.2 | SN1
52.2 | SN1
52.2 | SN1
52.1 | SN1
52.3 | SN1
52 | SN1
51.8 | SN1
51.6 | SN1
51.5 | SN1
51.4 | SN1
51.5 | SN1
51.5 | SN1
51.6 | SN1
51.2 | SN1
51.1 | SN1
51.1 | SN1
50.5 | SN1
50.5 | SN1
50.6 | SN1
50.4 | SN1
50.3 | SN1
50.6 | SN1
50.4 | SN1
50.5 | SN1
50.6 | SN1
51.4 | SN1
51.6 | SN1
51.5 | SN1
51.8 | SN1
52 | SN1
51.9 | SN1
51.8 | SN1
51.6 | SN1
51.7 | SN1
51.9 | SN1
52.2 | SN1
51.9 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
52.3 | SN1
52.2 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.4 | SN1
52.6 | SN1
52.9 | SN1
52.8 | SN1
52.8 | SN1
52.4 | SN1
52 | SN1
51.8 | SN1
51.3 | SN1
51.4 | SN1
51.6 | SN1
51.6 | SN1
51.4 | SN1
51.5 | SN1
51.4 | SN1
51.1 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.6 | SN1
50.4 | SN1
50.5 | SN1
50.4 | SN1
50.2 | SN1
50.4 | SN1
50.3 | SN1
50.5 | SN1
50.6 | SN1
51.2 | SN1
51.7 | SN1
51.9 | SN1
51.9 | SN1
52 | SN1
51.9 | SN1
52 | SN1
52 | SN1
51.9 | SN1
52.2 | SN1
51.8 | SN1
52.1 | SN1
52.2 | SN1
52.1 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52.5 | SN1
52.2 | SN1
52.3 | SN1
52.2 | SN1
52.6 | SN1
52.4 | SN1
52.1 | SN1
51.9 | SN1
51.3 | SN1
51.2 | SN1
51.3 | SN1
51.4 | SN1
51.6 | SN1
51.3 | SN1
51.4 | SN1
51.1 | SN1
50.8 | SN1
50.6 | SN1
50.4 | SN1
50.4 | SN1
50.7 | SN1
50.4 | SN1
50.3 | SN1
50.2 | SN1
50.4 | SN1
50.4 | SN1
50.2 | SN1
50.2 | SN1
50.3 | SN1
50.4 | SN1
50.7 | SN1
50.6 | SN1
51.1 | SN1
51.5 | SN1
51.4 | SN1
51.7 | SN1
52 | SN1
51.7 | SN1
51.8 | SN1
51.7 | SN1
52 | SN1
51.9 | SN1
51.9 | SN1
52.2 | SN1
52.1 | SN1
52 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.3 | SN1
52.2 | SN1
52.1 | SN1
51.9 | SN1
51.7 | SN1
51.3 | SN1
51.3 | SN1
51.4 | SN1
51.6 | SN1
51.4 | SN1
51.5 | SN1
51.3 | SN1
51.3 | SN1
50.9 | SN1
50.8 | SN1
50.5 | SN1
50.5 | SN1
50.3 | SN1
50.3 | SN1
50.4 | SN1
50.3 | SN1
50.3 | SN1
50.2 | SN1
50.2 | SN1
50.1 | SN1
50.3 | SN1
50.5 | SN1
50.7 | SN1
51.2 | SN1
51.1 | SN1
51.4 | SN1
51.4 | SN1
51.4 | SN1
51.7 | SN1
52.1 | SN1
52 | SN1
52.2 | SN1
51.9 | SN1
52.2 | SN1
52 | SN1
52.2 | SN1
52.2 | SN1
52.1 | SN1
51.8 | SN1
52.1 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
51.9 | SN1
52 | SN1
51.3 | SN1
51.5 | SN1
51.5 | SN1
51.3 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.2 | SN1
51 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.3 | SN1
50.4 | SN1
50.4 | SN1
50.3 | SN1
50.4 | SN1
50.5 | SN1
50.9 | SN1
51 | SN1
51.2 | SN1
51.4 | SN1
51.5 | SN1
51.3 | SN1
51.7 | SN1
51.7 | SN1
51.7 | SN1
51.7 | SN1
51.6 | SN1
51.7 | SN1
52 | SN1
51.8 | SN1
51.6 | SN1
51.9 | SN1
51.7 | SN1
51.9 | SN1
51.8 | SN1
51.7 | SN1
51.9 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
51.8 | SN1
51.4 | SN1
51.4 | SN1
51.2 | SN1
51.3 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.2 | SN1
50.9 | SN1
50.8 | SN1
50.7 | SN1
50.5 | SN1
50.6 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.2 | SN1
50.2 | SN1
50.3 | SN1
50.2 | SN1
50.6 | SN1
50.6 | SN1
51 | SN1
51.2 | SN1
51.1 | SN1
51.4 | SN1
51.7 | SN1
51.7 | SN1
51.6 | SN1
52.4 | SN1
52.4 | SN1
52 | SN1
52.3 | SN1
52.5 | SN1
51.9 | SN1
52.5 | SN1
52.4 | SN1
52.6 | SN1
52.3 | SN1
52.5 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
51.6 | SN1
51.6 | SN1
51.7 | SN1
51.2 | SN1
51.4 | SN1
51.2 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.5 | SN1
50.5 | SN1
50.3 | SN1
50.2 | SN1
50.1 | SN1
50.2 | SN1
50.1 | SN1
50.3 | SN1
50 | SN1
50.2 | SN1
50.2 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.9 | SN1
50.8 | SN1
51 | SN1
51 | SN1
51 | SN1
51.4 | SN1
51.6 | SN1
51.5 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
51.7 | SN1
51.8 | SN1
52 | SN1
51.6 | SN1
51.6 | SN1
51.9 | SN1
51.7 | SN1
51.9 | SN1
52 | SN1
51.7 | SN1
51.8 | SN1
51.2 | SN1
51 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
51.1 | SN1
50.8 | SN1
51.1 | SN1
50.9 | SN1
50.8 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
50.3 | SN1
50.2 | SN1
50.3 | SN1
51 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
51 | SN1
51.1 | SN1
51.1 | SN1
51.3 | SN1
51.2 | SN1
51.1 | SN1
51.1 | SN1
51.3 | SN1
51.3 | SN1
51.5 | SN1
51.4 | SN1
52.1 | SN1
51.7 | SN1
51.7 | SN1
51.9 | SN1
51.7 | SN1
51.5 | SN1
51.3 | SN1
51.4 | SN1
51.2 | SN1
51 | SN1
51.1 | SN1
50.8 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.1 | SN1
51.1 | SN1
50.7 | SN1
50.4 | SN1
50.3 | SN1
50.3 | SN1
50.4 | SN1
50.3 | SN1
50.4 | SN1
50.2 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.5 | SN1
50.6 | SN1
50.8 | SN1
51.1 | SN1
51.2 | SN1
51.4 | SN1
51.1 | SN1
51.2 | SN1
51.4 | SN1
51.4 | SN1
51.5 | SN1
51.4 | SN1
51.5 | SN1
51.6 | SN1
51.6 | SN1
51.4 | SN1
51.6 | SN1
51.3 | SN1
51.4 | SN1
51.8 | SN1
51.7 | SN1
52 | SN1
51.7 | SN1
51.5 | SN1
51.4 | SN1
51.3 | SN1
50.8 | SN1
50.9 | SN1
51.1 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.9 | SN1
50.9 | SN1
50.5 | SN1
50.7 | SN1
50.9 | SN1
51 | SN1
50.7 | SN1
50.8 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
51 | SN1
50.9 | SN1
51.1 | SN1
51.1 | SN1
50.9 | SN1
51 | SN1
51.1 | SN1
51.1 | SN1
51.1 | SN1
51.2 | SN1
51 | SN1
51.2 | SN1
51.3 | SN1
51.4 | SN1
51.5 | SN1
51.2 | SN1
51.3 | SN1
51.3 | SN1
50.9 | SN1
51.1 | SN1
50.7 | SN1
50.4 | SN1
51.3 | SN1
51.2 | SN1
50.9 | SN1
51.1 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.6 | SN1
50.4 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.8 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
51 | SN1
51.1 | SN1
51 | SN1
50.9 | SN1
51.1 | SN1
51 | SN1
50.9 | SN1
51 | SN1
51.3 | SN1
50.9 | SN1
51 | SN1
51.3 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
51.3 | SN1
51.2 | SN1
51.1 | SN1
51 | SN1
51.3 | SN1
51.1 | SN1
50.9 | SN1
51.1 | SN1
50.8 | SN1
51 | SN1
51 | SN1
51 | SN1
50.9 | SN1
50.7 | SN1
50.5 | SN1
50.7 | SN1
50.4 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.1 | SN1
50.4 | SN1
50.3 | SN1
50.3 | SN1
50.6 | SN1
50.4 | SN1
50.6 | SN1
50.6 | SN1
50.8 | SN1
50.8 | SN1
51.1 | SN1
51.3 | SN1
50.8 | SN1
51.1 | SN1
51.2 | SN1
50.9 | SN1
51.1 | SN1
51.4 | SN1
51.2 | SN1
51.3 | SN1
51.4 | SN1
51.2 | SN1
51.3 | SN1
51.2 | SN1
51.4 | SN1
51.4 | SN1
51.5 | SN1
51.5 | SN1
51.3 | SN1
51 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.7 | SN1
51 | SN1
51 | SN1
51 | SN1
51 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.6 | SN1
50.7 | SN1
50.8 | SN1
50.6 | SN1
50.5 | SN1
50.3 | SN1
50.2 | SN1
50.4 | SN1
50.9 | SN1
50.9 | SN1
51.1 | SN1
51 | SN1
51.2 | SN1
51.3 | SN1
50.9 | SN1
51.1 | SN1
51.2 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.2 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.7 | SN1
51.5 | SN1
51.9 | SN1
51.6 | SN1
51.6 | SN1
51.4 | SN1
51.1 | SN1
50.8 | SN1
51.2 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.5 | SN1
50.6 | SN1
50.5 | SN1
50.8 | SN1
50.5 | SN1
50.4 | SN1
50.6 | SN1
50.2 | SN1
50.1 | SN1
50.4 | SN1
50.2 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.7 | SN1
50.6 | SN1
51 | SN1
51 | SN1
50.8 | SN1
51.2 | SN1
51 | SN1
51 | SN1
51.2 | SN1
51.2 | SN1
51 | SN1
50.8 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.5 | SN1
51.4 | SN1
51.1 | SN1
50.9 | SN1
51 | SN1
50.8 | SN1
50.4 | SN1
50.7 | SN1
51 | SN1
50.5 | SN1
50.3 | SN1
50.3 | SN1
50.4 | SN1
50.5 | SN1
50.7 | SN1
50.7 | SN1
50.5 | SN1
50.8 | SN1
50.3 | SN1
50.2 | SN1
50.3 | SN1
50.2 | SN1
50.2 | SN1
50.1 | SN1
49.9 | SN1
50.1 | SN1
50.2 | SN1
50.2 | SN1
50.3 | SN1
50.3 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.6 | SN1
50.8 | SN1
50.8 | SN1
50.4 | SN1
50.5 | SN1
50.4 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
51.2 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.1 | SN1
50.9 | SN1
50.9 | SN1
50.6 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.8 | SN1
50.6 | SN1
50.3 | SN1
50.1 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.6 | SN1
50.5 | SN1
50.2 | SN1
50.4 | SN1
50.2 | SN1
50.4 | SN1
50.2 | SN1
50.2 | SN1
50.2 | SN1
50.4 | SN1
50.5 | SN1
50.9 | SN1
50.7 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
51.3 | SN1
51 | SN1
51.3 | SN1
51.1 | SN1
51.3 | SN1
51.2 | SN1
51.3 | SN1
51.1 | SN1
51.2 | SN1
51.3 | SN1
51.2 | SN1
51.2 | SN1
51.2 | SN1
51.2 | SN1
51.2 | SN1
51 | SN1
50.8 | SN1
50.8 | SN1
50.6 | SN1
50.4 | SN1
50.5 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.7 | SN1
51.3 | SN1
50.6 | SN1
50.4 | SN1
50.6 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.5 | SN1
50.7 | SN1
50.2 | SN1
50.3 | SN1
50.1 | SN1
49.9 | SN1
50.5 | SN1
50.5 | SN1
50.3 | SN1
50.5 | SN1
50.5 | SN1
50.9 | SN1
51 | SN1
51.1 | SN1
50.7 | SN1
50.9 | SN1
51.2 | SN1
51.2 | SN1
51 | SN1
51.1 | SN1
50.9 | SN1
51.3 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
51.1 | SN1
51.2 | SN1
51.1 | SN1
51.4 | SN1
51.2 | SN1
50.8 | SN1
50.5 | SN1
50.5 | SN1
50.3 | SN1
50.4 | SN1
50.2 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.5 | SN1
50.7 | SN1
50.6 | SN1
50.8 | SN1
50.4 | SN1
50.8 | SN1
50.6 | SN1
50.8 | SN1
50.8 | SN1
50.6 | SN1
50.4 | SN1
50.3 | SN1
50.5 | SN1
50.7 | SN1
50.6 | SN1
51 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
51 | SN1
51.1 | SN1
51.1 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.2 | SN1
51.5 | SN1
51.5 | SN1
51.4 | SN1
51.5 | SN1
51.5 | SN1
51.6 | SN1
51.7 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
51 | SN1
51 | SN1
50.8 | SN1
50.8 | SN1
51.2 | SN1
51.2 | SN1
50.8 | SN1
12.4 | SN1
51.1 | SN1
50.9 | SN1
50.8 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.4 | SN1
50.3 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
51 | SN1
51.1 | SN1
51.2 | SN1
51.1 | SN1
51 | SN1
51.3 | SN1
51.3 | SN1
51 | SN1
51.2 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.5 | SN1
51.3 | SN1
51.7 | SN1
51.5 | SN1
51.3 | SN1
51.5 | SN1
51.6 | SN1
51.3 | SN1
51 | SN1
51 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.1 | SN1
50.5 | SN1
50.4 | SN1
50.6 | SN1
50.8 | SN1
50.4 | SN1
50.4 | SN1
50.5 | SN1
50.7 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
50.6 | SN1
50.3 | SN1
50.3 | SN1
50.1 | SN1
50.8 | SN1
50.6 | SN1
50.9 | SN1
50.3 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
51.1 | SN1
51 | SN1
50.9 | SN1
51.2 | SN1
50.9 | SN1
51.3 | SN1
51.2 | SN1
51.4 | SN1
51.4 | SN1
51.5 | SN1
51.5 | SN1
51.2 | SN1
51.4 | SN1
51.2 | SN1
51.2 | SN1
50.8 | SN1
50.6 | SN1
50.2 | SN1
50.6 | SN1
50.3 | SN1
50.3 | SN1
50.4 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.4 | SN1
50.6 | SN1
50.4 | SN1
50.4 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.3 | SN1
50.3 | SN1
50.4 | SN1
50.3 | SN1
50.5 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
51.3 | SN1
51.2 | SN1
51.3 | SN1
51.4 | SN1
51.1 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
51.2 | SN1
51.2 | SN1
51.2 | SN1
51.3 | SN1
51.3 | SN1
51.2 | SN1
51.1 | SN1
51.3 | SN1
50.9 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.6 | SN1
50.4 | SN1
50.6 | SN1
50.8 | SN1
51 | SN1
50.5 | SN1
50.6 | SN1
50.8 | SN1
50.8 | SN1
50.6 | SN1
50.6 | SN1
50.7 | SN1
50.6 | SN1
50.8 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.2 | SN1
50.2 | SN1
50.2 | SN1
50.1 | SN1
50.6 | SN1
51 | SN1
51 | SN1
51.1 | SN1
51.1 | SN1
51 | SN1
51 | SN1
51.4 | SN1
51.2 | SN1
51 | SN1
51.1 | SN1
51.2 | SN1
51.5 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.2 | SN1
51.3 | SN1
51.5 | SN1
51.1 | SN1
51 | SN1
50.4 | SN1
50.5 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.8 | SN1
50.6 | SN1
50.4 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.6 | SN1
50.3 | SN1
50.5 | SN1
50.2 | SN1
50.4 | SN1
50.2 | SN1
50.1 | SN1
50.1 | SN1
50.3 | SN1
50.5 | SN1
50.5 | SN1
50.8 | SN1
50.8 | SN1
50.5 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
51.1 | SN1
51.3 | SN1
51.1 | SN1
51.6 | SN1
51.1 | SN1
51.3 | SN1
51.4 | SN1
51.5 | SN1
51.2 | SN1
51.3 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51.5 | SN1
51.3 | SN1
51 | SN1
50.7 | SN1
50.2 | SN1
50.5 | SN1
50.9 | SN1
50.6 | SN1
50.7 | SN1
50.5 | SN1
50.5 | SN1
50.6 | SN1
50.2 | SN1
50.5 | SN1
50.6 | SN1
50.7 | SN1
50.6 | SN1
50.4 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.4 | SN1
50.2 | SN1
50.1 | SN1
50.1 | SN1
50.2 | SN1
50.5 | SN1
50.6 | SN1
50.8 | SN1
50.4 | SN1
50.7 | SN1
50.9 | SN1
50.9 | SN1
50.8 | SN1
50.9 | SN1
51.1 | SN1
51.3 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.6 | SN1
51.6 | SN1
51.5 | SN1
51.4 | SN1
50.9 | SN1
50.6 | SN1
50.2 | SN1
50 | SN1
50.6 | SN1
50.5 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.6 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.4 | SN1
50.6 | SN1
50.4 | SN1
50.7 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.2 | SN1
50.4 | SN1
50.1 | SN1
50.1 | SN1
50.2 | SN1
50.4 | SN1
50.6 | SN1
50.6 | SN1
51.2 | SN1
51.1 | SN1
50.8 | SN1
51.5 | SN1
51.1 | SN1
51 | SN1
51.1 | SN1
51 | SN1
51 | SN1
51.4 | SN1
51.1 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
50.9 | SN1
51.2 | SN1
51.1 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
49.9 | SN1
49.8 | SN1
50 | SN1
50.2 | SN1
50.4 | SN1
50.6 | SN1
50.4 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.3 | SN1
50.2 | SN1
50.3 | SN1
50.2 | SN1
50 | SN1
50.4 | SN1
50.2 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
51 | SN1
51.1 | SN1
50.8 | SN1
50.9 | SN1
51 | SN1
51 | SN1
51.1 | SN1
51.2 | SN1
51 | SN1
51.3 | SN1
51 | SN1
51.2 | SN1
51.2 | SN1
51 | SN1
50.8 | SN1
50.4 | SN1
50.8 | SN1
50.5 | SN1
50.6 | SN1
50.4 | SN1
50.5 | SN1
50.6 | SN1
50.8 | SN1
50.9 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
50.3 | SN1
50.5 | SN1
50.2 | SN1
50.4 | SN1
50 | SN1
50 | SN1
50.2 | SN1
50.3 | SN1
50.5 | SN1
50.8 | SN1
50.5 | SN1
50.8 | SN1
51 | SN1
50.8 | SN1
50.5 | SN1
51.2 | SN1
51.1 | SN1
50.9 | SN1
50.8 | SN1
51 | SN1
51.2 | SN1
51.3 | SN1
51.4 | SN1
50.9 | SN1
51.1 | SN1
51.1 | SN1
51.3 | SN1
51.2 | SN1
51.1 | SN1
50.9 | SN1
51.1 | SN1
50.8 | SN1
50.9 | SN1
50.7 | SN1
50.8 | SN1
50.4 | SN1
50.4 | SN1
50.6 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.3 | SN1
50.5 | SN1
50.3 | SN1
50.5 | SN1
50.6 | SN1
50.5 | SN1
50.7 | SN1
50.4 | SN1
50.3 | SN1
50.2 | SN1
50.2 | SN1
50.2 | SN1
50 | SN1
50.1 | SN1
50.4 | SN1
50.5 | SN1
50.4 | SN1
50.8 | SN1
50.8 | SN1
50.5 | SN1
50.8 | SN1
50.6 | SN1
50.7 | SN1
51 | SN1
51 | SN1
50.8 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
51.1 | SN1
51 | SN1
50.8 | SN1
50.8 | SN1
50.6 | SN1
50.5 | SN1
50.3 | SN1
50.2 | SN1
50.2 | SN1
50.3 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.7 | SN1
50.5 | SN1
50.7 | SN1
50.7 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
50.3 | SN1
50.2 | SN1
50 | SN1
50.2 | SN1
50.4 | SN1
50.2 | SN1
50.7 | SN1
50.5 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.5 | SN1
50.6 | SN1
50.5 | SN1
50.8 | SN1
50.6 | SN1
50.8 | SN1
50.9 | SN1
51.3 | SN1
50.9 | SN1
51 | SN1
51 | SN1
50.7 | SN1
51.2 | SN1
51.1 | SN1
50.9 | SN1
50.9 | SN1
50.6 | SN1
50.4 | SN1
50.2 | SN1
50.4 | SN1
50.2 | SN1
50.5 | SN1
50.3 | SN1
50.4 | SN1
50.5 | SN1
50.7 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.2 | SN1
50.1 | SN1
50 | SN1
50.1 | SN1
50.1 | SN1
49.9 | SN1
50.5 | SN1
50.3 | SN1
50.4 | SN1
50.7 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.9 | SN1
50.8 | SN1
51 | SN1
51.2 | SN1
51 | SN1
51.2 | SN1
51.2 | SN1
51.2 | SN1
51.1 | SN1
51.1 | SN1
51.1 | SN1
51.2 | SN1
51 | SN1
50.9 | SN1
50.4 | SN1
50.3 | SN1
50 | SN1
50.2 | SN1
50.4 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.5 | SN1
50.3 | SN1
50.4 | SN1
50.6 | SN1
50.5 | SN1
50.9 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
51.1 | SN1
50.9 | SN1
51.2 | SN1
51 | SN1
51.1 | SN1
51.2 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.1 | SN1
51.3 | SN1
51.3 | SN1
51.1 | SN1
50.9 | SN1
51.2 | SN1
51.2 | SN1
51 | SN1
51 | SN1
50.3 | SN1
50.3 | SN1
50.4 | SN1
50.4 | SN1
50.6 | SN1
50.7 | SN1
50.6 | SN1
50.8 | SN1
50.6 | SN1
50.7 | SN1
50.8 | SN1
50.2 | SN1
50.6 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.2 | SN1
50 | SN1
50.2 | SN1
50.1 | SN1
50.3 | SN1
50.3 | SN1
50.5 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.9 | SN1
50.8 | SN1
51 | SN1
50.8 | SN1
51 | SN1
50.9 | SN1
51.3 | SN1
51 | SN1
51.2 | SN1
51.1 | SN1
51.2 | SN1
51.3 | SN1
51.1 | SN1
51.1 | SN1
51.1 | SN1
51 | SN1
50.9 | SN1
50.7 | SN1
50.4 | SN1
50.3 | SN1
50.4 | SN1
50.5 | SN1
50.6 | SN1
50.6 | SN1
50.8 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.7 | SN1
50.4 | SN1
50.7 | SN1
50.7 | SN1
50.3 | SN1
50.3 | SN1
50.4 | SN1
50.4 | SN1
50.2 | SN1
50.3 | SN1
50.4 | SN1
50.3 | SN1
50.3 | SN1
50.2 | SN1
50.4 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.8 | SN1
51 | SN1
51.3 | SN1
51.1 | SN1
51.2 | SN1
51 | SN1
50.8 | SN1
51.1 | SN1
51.1 | SN1
51.3 | SN1
51.2 | SN1
51.2 | SN1
51.2 | SN1
51.2 | SN1
51.5 | SN1
51.6 | SN1
51.4 | SN1
50.9 | SN1
50.6 | SN1
50.3 | SN1
50.4 | SN1
50.3 | SN1
50.2 | SN1
50.2 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.5 | SN1
50.5 | SN1
50.1 | SN1
50.3 | SN1
50.4 | SN1
50 | SN1
50.1 | SN1
50.1 | SN1
50.2 | SN1
50.1 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.8 | SN1
50.4 | SN1
50.6 | SN1
51.1 | SN1
50.9 | SN1
50.9 | SN1
51.1 | SN1
50.9 | SN1
51.2 | SN1
51.2 | SN1
51.3 | SN1
51.3 | SN1
51.1 | SN1
51.2 | SN1
51.1 | SN1
51 | SN1
50.7 | SN1
50.3 | SN1
50.2 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.5 | SN1
50.6 | SN1
50.5 | SN1
50.7 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.6 | SN1
50.7 | SN1
50.5 | SN1
50.3 | SN1
50.5 | SN1
50.2 | SN1
50.3 | SN1
50 | SN1
50.2 | SN1
50.4 | SN1
50.3 | SN1
50.4 | SN1
50.6 | SN1
50.5 | SN1
50.4 | SN1
50.9 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.9 | SN1
50.8 | SN1
50.7 | SN1
50.9 | SN1
50.9 | SN1
50.8 | SN1
50.7 | SN1
50.9 | SN1
51.1 | SN1
51.4 | SN1
51.1 | SN1
51.1 | SN1
50.7 | SN1
50.5 | SN1
50.5 | SN1
50.2 | SN1
50.3 | SN1
50.7 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.4 | SN1
50.6 | SN1
50.2 | SN1
49.8 | SN1
50 | SN1
49.9 | SN1
50.2 | SN1
50.3 | SN1
49.9 | SN1
50.2 | SN1
49.9 | SN1
50.2 | SN1
49.8 | SN1
49.7 | SN1
49.7 | SN1
50 | SN1
50.3 | SN1
50.2 | SN1
50.2 | SN1
50.8 | SN1
50.3 | SN1
50.5 | SN1
50.2 | SN1
50.3 | SN1
50.5 | SN1
50.4 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.9 | SN1
50.6 | SN1
50.9 | SN1
51 | SN1
50.7 | SN1
50.8 | SN1
51 | SN1
51 | SN1
50.5 | SN1
50.6 | SN1
50.4 | SN1
50.2 | SN1
49.9 | SN1
49.8 | SN1
50.1 | SN1
49.7 | SN1
50.1 | SN1
50 | SN1
50.4 | SN1
50.5 | SN1
50.3 | SN1
50.4 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.9 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.5 | SN1
50.6 | SN1
50.4 | SN1
50.2 | SN1
50.1 | SN1
50 | SN1
50.4 | SN1
50.3 | SN1
50.4 | SN1
50.7 | SN1
50.4 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
51 | SN1
51.2 | SN1
50.7 | SN1
51.3 | SN1
51 | SN1
51 | SN1
51.1 | SN1
51 | SN1
51.6 | SN1
51.4 | SN1
51.4 | SN1
51.2 | SN1
51 | SN1
50.7 | SN1
50.6 | SN1
50.5 | SN1
50.3 | SN1
50.3 | SN1
50.3 | SN1
50.3 | SN1
50.5 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.4 | SN1
50.6 | SN1
50.4 | SN1
50.3 | SN1
50.2 | SN1
50.4 | SN1
50.6 | SN1
50.5 | SN1
50.7 | SN1
50.5 | SN1
51 | SN1
51.2 | SN1
51.2 | SN1
51.3 | SN1
51 | SN1
50.9 | SN1
51 | SN1
51.2 | SN1
51.3 | SN1
51.5 | SN1
51.1 | SN1
51.3 | SN1
51.1 | SN1
51.2 | SN1
50.7 | SN1
50.9 | SN1
50.2 | SN1
50.2 | SN1
50.6 | SN1
49.8 | SN1
50.2 | SN1
50.4 | SN1
50 | SN1
49.9 | SN1
50 | SN1
50 | SN1
50 | SN1
50.2 | SN1
50.1 | SN1
50.2 | SN1
50 | SN1
50.3 | SN1
50.2 | SN1
50.2 | SN1
50.2 | SN1
50 | SN1
49.9 | SN1
50.1 | SN1
50 | SN1
50 | SN1
49.8 | SN1
49.8 | SN1
49.9 | SN1
50.2 | SN1
50 | SN1
50.7 | SN1
50.2 | SN1
51 | SN1
50.8 | SN1
51.1 | SN1
51.3 | SN1
51.1 | SN1
51.1 | SN1
51 | SN1
51.3 | SN1
51.2 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.1 | SN1
50.8 | SN1
50.6 | SN1
50 | SN1
50 | SN1
49.7 | SN1
50 | SN1
50.2 | SN1
50.3 | SN1
50.3 | SN1
50.2 | SN1
50.5 | SN1
50.6 | SN1
50.6 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.5 | SN1
50.3 | SN1
50.2 | SN1
50.2 | SN1
50.3 | SN1
50.3 | SN1
50.4 | SN1
50.2 | SN1
50.5 | SN1
50.5 | SN1
50.8 | SN1
50.8 | SN1
51 | SN1
51 | SN1
51 | SN1
50.9 | SN1
51.1 | SN1
51.3 | SN1
51.3 | SN1
51.5 | SN1
51.3 | SN1
51 | SN1
51.4 | SN1
51 | SN1
50.8 | SN1
50.7 | SN1
50.4 | SN1
50.4 | SN1
50.3 | SN1
50.4 | SN1
50.5 | SN1
50.6 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.5 | SN1
50.5 | SN1
50.2 | SN1
50.3 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
51 | SN1
51 | SN1
51 | SN1
51.1 | SN1
50.8 | SN1
51 | SN1
50.8 | SN1
51.2 | SN1
51 | SN1
51.1 | SN1
51 | SN1
51.2 | SN1
51.2 | SN1
51 | SN1
51.1 | SN1
50.8 | SN1
50.7 | SN1
50.3 | SN1
50.4 | SN1
50.3 | SN1
50.2 | SN1
50.3 | SN1
50.6 | SN1
50.6 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
51 | SN1
50.8 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.7 | SN1
50.7 | SN1
50.6 | SN1
50.9 | SN1
50.6 | SN1
50.9 | SN1
50.6 | SN1
50.6 | SN1
51.1 | SN1
50.6 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
51.2 | SN1
51 | SN1
51.2 | SN1
51.3 | SN1
50.8 | SN1
50.2 | SN1
50.3 | SN1
50.3 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.8 | SN1
50.5 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.8 | SN1
50.5 | SN1
50.5 | SN1
50.3 | SN1
50.3 | SN1
50.3 | SN1
50.4 | SN1
50.6 | SN1
50.7 | SN1
51 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.5 | SN1
51.1 | SN1
51 | SN1
50.9 | SN1
51 | SN1
50.7 | SN1
51 | SN1
51 | SN1
50.8 | SN1
51 | SN1
50.9 | SN1
51.1 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.5 | SN1
50.4 | SN1
50.2 | SN1
50.2 | SN1
50.2 | SN1
50.5 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.8 | SN1
50.6 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.5 | SN1
50.5 | SN1
50.3 | SN1
50.1 | SN1
50.3 | SN1
50.3 | SN1
50.3 | SN1
50.5 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.6 | SN1
50.7 | SN1
50.7 | SN1
51.1 | SN1
50.5 | SN1
50.8 | SN1
51 | SN1
51 | SN1
50.9 | SN1
51.1 | SN1
50.8 | SN1
50.7 | SN1
51.1 | SN1
51.1 | SN1
51.1 | SN1
50.6 | SN1
50.5 | SN1
50.4 | SN1
50.1 | SN1
50.1 | SN1
50.4 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.8 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
50.9 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.6 | SN1
50.8 | SN1
50.5 | SN1
50.5 | SN1
50.3 | SN1
50.2 | SN1
50.2 | SN1
50.3 | SN1
50.1 | SN1
50.4 | SN1
50.4 | SN1
50.7 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.5 | SN1
50.3 | SN1
50.5 | SN1
50.9 | SN1
50.6 | SN1
50.8 | SN1
51.1 | SN1
51 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
51.4 | SN1
51 | SN1
50.7 | SN1
50.2 | SN1
50 | SN1
50.3 | SN1
50.3 | SN1
50.5 | SN1
50.7 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
50.6 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.6 | SN1
50.4 | SN1
50.2 | SN1
50.1 | SN1
50 | SN1
50.3 | SN1
50.7 | SN1
50.5 | SN1
50.8 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.9 | SN1
50.9 | SN1
50.8 | SN1
50.9 | SN1
50.9 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.7 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
51.1 | SN1
50.6 | SN1
50.5 | SN1
50.7 | SN1
50.6 | SN1
50.5 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.9 | SN1
51 | SN1
51.3 | SN1
51.1 | SN1
50.9 | SN1
50.8 | SN1
50.6 | SN1
50.6 | SN1
51 | SN1
51.6 | SN1
51.6 | SN1
52.1 | SN1
51.8 | SN1
51.6 | SN1
51.6 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.2 | SN1
51.2 | SN1
51.3 | SN1
51.2 | SN1
51.4 | SN1
51.1 | SN1
51.3 | SN1
51.1 | SN1
51.2 | SN1
51.3 | SN1
51.2 | SN1
51.4 | SN1
51.3 | SN1
51.5 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51 | SN1
51 | SN1
51 | SN1
50.7 | SN1
50.9 | SN1
50.9 | SN1
50.8 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
51 | SN1
51 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
50.8 | SN1
51 | SN1
51 | SN1
50.8 | SN1
51.2 | SN1
51.2 | SN1
51.2 | SN1
51.3 | SN1
51.2 | SN1
51.3 | SN1
51.2 | SN1
51.1 | SN1
51.3 | SN1
51.5 | SN1
51.2 | SN1
51.2 | SN1
51.2 | SN1
50.9 | SN1
51.1 | SN1
51.2 | SN1
51 | SN1
51.2 | SN1
51 | SN1
51.1 | SN1
51.5 | SN1
51.2 | SN1
51.1 | SN1
51 | SN1
50.7 | SN1
50.9 | SN1
50.9 | SN1
50.8 | SN1
50.9 | SN1
50.9 | SN1
51.1 | SN1
50.9 | SN1
51.1 | SN1
51 | SN1
50.9 | SN1
51 | SN1
51 | SN1
51 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.7 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
51 | SN1
51.1 | SN1
51 | SN1
51.2 | SN1
51 | SN1
51.3 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.5 | SN1
51.3 | SN1
51.3 | SN1
51.2 | SN1
51.1 | SN1
51 | SN1
51.1 | SN1
51 | SN1
50.9 | SN1
50.8 | SN1
51 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
51 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.4 | SN1
50.9 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
51 | SN1
51.2 | SN1
51.1 | SN1
51 | SN1
50.6 | SN1
50.4 | SN1
50.6 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.6 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.9 | SN1
50.8 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.1 | SN1
50.3 | SN1
50.3 | SN1
50.1 | SN1
50.4 | SN1
50.2 | SN1
50.4 | SN1
50.5 | SN1
50.8 | SN1
51 | SN1
51.1 | SN1
51.2 | SN1
50.9 | SN1
51 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.6 | SN1
50.8 | SN1
51.3 | SN1
51.2 | SN1
50.8 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
50.7 | SN1
50.7 | SN1
50.3 | SN1
50.3 | SN1
50.4 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.3 | SN1
50 | SN1
50.6 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
50.7 | SN1
50.8 | SN1
50.4 | SN1
50.2 | SN1
51 | SN1
51 | SN1
51 | SN1
51.1 | SN1
50.8 | SN1
50.7 | SN1
51.1 | SN1
50.9 | SN1
51.2 | SN1
51.1 | SN1
50.9 | SN1
50.9 | SN1
51.1 | SN1
51 | SN1
51.3 | SN1
51.2 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.4 | SN1
51.5 | SN1
51.5 | SN1
51.6 | SN1
51.4 | SN1
51.3 | SN1
50.8 | SN1
50.8 | SN1
50.6 | SN1
50.5 | SN1
50 | SN1
50.2 | SN1
50.4 | SN1
50.7 | SN1
50.7 | SN1
50.6 | SN1
50.5 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
51.1 | SN1
50.9 | SN1
51 | SN1
51.1 | SN1
50.8 | SN1
50.7 | SN1
50.6 | SN1
50.8 | SN1
50.6 | SN1
50.2 | SN1
50.3 | SN1
50.2 | SN1
50.6 | SN1
50.5 | SN1
50.7 | SN1
51.3 | SN1
51 | SN1
51.1 | SN1
51 | SN1
51.3 | SN1
50.9 | SN1
51.2 | SN1
51.3 | SN1
51.4 | SN1
51.2 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.6 | SN1
51.7 | SN1
51.4 | SN1
51.1 | SN1
51.2 | SN1
50.7 | SN1
50.5 | SN1
50.3 | SN1
50.4 | SN1
50.7 | SN1
50.6 | SN1
50.9 | SN1
50.7 | SN1
50.8 | SN1
50.9 | SN1
51.1 | SN1
50.8 | SN1
50.9 | SN1
51 | SN1
51 | SN1
50.9 | SN1
51 | SN1
51.2 | SN1
50.9 | SN1
50.8 | SN1
50.5 | SN1
50.5 | SN1
50.7 | SN1
50.1 | SN1
50.3 | SN1
50.2 | SN1
50.6 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
51 | SN1
51 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.5 | SN1
51.3 | SN1
51.3 | SN1
51.6 | SN1
51.5 | SN1
51.4 | SN1
51.3 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.9 | SN1
50.9 | SN1
51 | SN1
51 | SN1
50.9 | SN1
51 | SN1
51.1 | SN1
51 | SN1
50.9 | SN1
50.6 | SN1
50.7 | SN1
50.7 | SN1
50.4 | SN1
50.4 | SN1
50.3 | SN1
50.3 | SN1
50.3 | SN1
50.2 | SN1
50.2 | SN1
50.2 | SN1
50.3 | SN1
50.6 | SN1
50.8 | SN1
51 | SN1
51.1 | SN1
50.7 | SN1
50.9 | SN1
50.8 | SN1
50.6 | SN1
51 | SN1
51.2 | SN1
51.1 | SN1
51.1 | SN1
51 | SN1
51 | SN1
50.7 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.7 | SN1
50.9 | SN1
50.9 | SN1
51 | SN1
50.8 | SN1
50.9 | SN1
50.9 | SN1
51.1 | SN1
51.1 | SN1
51.1 | SN1
50.9 | SN1
50.8 | SN1
50.9 | SN1
50.7 | SN1
50.5 | SN1
50.5 | SN1
51 | SN1
51.3 | SN1
51 | SN1
51.3 | SN1
51.2 | SN1
51.4 | SN1
51.5 | SN1
51.1 | SN1
51.2 | SN1
51.3 | SN1
51.1 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
51.2 | SN1
51.3 | SN1
51.1 | SN1
51.1 | SN1
51 | SN1
51.3 | SN1
51.1 | SN1
51.2 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
50.6 | SN1
50.2 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
50.7 | SN1
50.9 | SN1
50.8 | SN1
51 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
50.8 | SN1
50.7 | SN1
50.9 | SN1
50.6 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
52.3 | SN1
52.4 | SN1
52.3 | SN1
52.4 | SN1
52 | SN1
51.3 | SN1
51.5 | SN1
51.2 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51 | SN1
51 | SN1
51.2 | SN1
50.9 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
50.4 | SN1
50.5 | SN1
50.7 | SN1
50.2 | SN1
50.5 | SN1
50.3 | SN1
50.4 | SN1
50.4 | SN1
50.8 | SN1
51.6 | SN1
51.8 | SN1
51.9 | SN1
52.8 | SN1
53.4 | SN1
53.5 | SN1
53.5 | SN1
54.1 | SN1
55 | SN1
54.5 | SN1
55.8 | SN1
55.4 | SN1
55.4 | SN1
55.4 | SN1
55.3 | SN1
55.3 | SN1
54.9 | SN1
54.6 | SN1
55 | SN1
54.7 | SN1
53.9 | SN1
53.5 | SN1
53 | SN1
52.7 | SN1
52.6 | SN1
52.2 | SN1
52 | SN1
51.4 | SN1
51.7 | SN1
51.4 | SN1
51.6 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.3 | SN1
51.3 | SN1
51.4 | SN1
51.2 | SN1
51.1 | SN1
51.3 | SN1
50.9 | SN1
50.8 | SN1
50.8 | SN1
51.3 | SN1
51.5 | SN1
52.1 | SN1
52.3 | SN1
53.3 | SN1
53.4 | SN1
53.7 | SN1
54.4 | SN1
54.3 | SN1
55.2 | SN1
55.3 | SN1
55.1 | SN1
55.3 | SN1
54.8 | SN1
55 | SN1
55.7 | SN1
55.2 | SN1
55.1 | SN1
55.1 | SN1
54.6 | SN1
54.8 | SN1
54.5 | SN1
53.8 | SN1
54.1 | SN1
53.9 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
49.8 | SN1
50.2 | SN1
50.3 | SN1
50.2 | SN1
50.4 | SN1
50.4 | SN1
50.3 | SN1
50.5 | SN1
50.2 | SN1
50 | SN1
50.6 | SN1
50.5 | SN1
51 | SN1
51.5 | SN1
51.9 | SN1
52 | SN1
52.7 | SN1
52.3 | SN1
53.2 | SN1
53.2 | SN1
53.9 | SN1
54 | SN1
53.7 | SN1
54.2 | SN1
54.2 | SN1
54.3 | SN1
54 | SN1
53.9 | SN1
53.2 | SN1
53.4 | SN1
53.1 | SN1
52.9 | SN1
52.6 | SN1
51.7 | SN1
51.5 | SN1
51.3 | SN1
51.2 | SN1
51 | SN1
50.8 | SN1
50.4 | SN1
50.5 | SN1
50.7 | SN1
50.9 | SN1
51.1 | SN1
50.7 | SN1
50.8 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.6 | SN1
50.7 | SN1
50.3 | SN1
50.5 | SN1
50.7 | SN1
50.2 | SN1
50 | SN1
50.2 | SN1
50.2 | SN1
51 | SN1
51.4 | SN1
52 | SN1
52.3 | SN1
52.5 | SN1
53.1 | SN1
53.1 | SN1
53.3 | SN1
53.7 | SN1
53.9 | SN1
53 | SN1
53.1 | SN1
53.4 | SN1
53.1 | SN1
52.9 | SN1
53 | SN1
53 | SN1
53 | SN1
52.4 | SN1
52.4 | SN1
52 | SN1
52.4 | SN1
52.2 | SN1
51.9 | SN1
51.7 | SN1
51.4 | SN1
51.2 | SN1
50.8 | SN1
50.9 | SN1
50.6 | SN1
50.5 | SN1
50.8 | SN1
50.2 | SN1
51 | SN1
50.8 | SN1
51 | SN1
50.6 | SN1
51 | SN1
51 | SN1
50.7 | SN1
50.5 | SN1
50.6 | SN1
50.5 | SN1
50.2 | SN1
50.2 | SN1
50.1 | SN1
49.9 | SN1
51.7 | SN1
51.5 | SN1
52.6 | SN1
53 | SN1
53.2 | SN1
53.4 | SN1
53.5 | SN1
53.3 | SN1
53.9 | SN1
54.1 | SN1
54.7 | SN1
54 | SN1
54.5 | SN1
53.8 | SN1
54.1 | SN1
53.9 | SN1
53.8 | SN1
54 | SN1
53.5 | SN1
54 | SN1
53.6 | SN1
52.9 | SN1
53 | SN1
52.8 | SN1
53 | SN1
53.2 | SN1
15.3 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
53 | SN1
58.1 | SN1
56.4 | SN1
55.5 | SN1
55.3 | SN1
54.5 | SN1
54.5 | SN1
54.5 | SN1
54.3 | SN1
53.8 | SN1
53.5 | SN1
53.4 | SN1
53.1 | SN1
52.5 | SN1
52.8 | SN1
52.9 | SN1
52.5 | SN1
52.4 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.4 | SN1
52.7 | SN1
52.6 | SN1
52.7 | SN1
52.8 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
52.7 | SN1
52.7 | SN1
52.5 | SN1
52.8 | SN1
52.7 | SN1
52.8 | SN1
52.9 | SN1
52.6 | SN1
52.7 | SN1
53 | SN1
52.9 | SN1
53.1 | SN1
53.2 | SN1
57 | SN1
54 | SN1
52.8 | SN1
52.7 | SN1
52.3 | SN1
52.5 | SN1
52.3 | SN1
52.2 | SN1
52.1 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.4 | SN1
52 | SN1
52.4 | SN1
51.9 | SN1
52.2 | SN1
51.5 | SN1
51 | SN1
50.7 | SN1
50.3 | SN1
49.9 | SN1
49.7 | SN1
49.5 | SN1
49.1 | SN1
49.2 | SN1
49.1 | SN1
48.9 | SN1
48.7 | SN1
49 | SN1
49.2 | SN1
49.2 | SN1
49.5 | SN1
49.6 | SN1
49.6 | SN1
49.7 | SN1
49.8 | SN1
49.9 | SN1
49.5 | SN1
49.8 | SN1
50 | SN1
49.8 | SN1
49.9 | SN1
50 | SN1
50 | SN1
50.6 | SN1
50.6 | SN1
51.1 | SN1
51.2 | SN1
51.6 | SN1
52 | SN1
52.6 | SN1
53.1 | SN1
53.4 | SN1
54 | SN1
54.3 | SN1
53.5 | SN1
53.6 | SN1
52.9 | SN1
53 | SN1
53.5 | SN1
54 | SN1
53.9 | SN1
52.7 | SN1
52.6 | SN1
51.5 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.4 | SN1
51.3 | SN1
52.5 | SN1
52.4 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.5 | SN1
52.7 | SN1
52.6 | SN1
52.3 | SN1
52.5 | SN1
52 | SN1
52 | SN1
52.1 | SN1
52.4 | SN1
52 | SN1
52.8 | SN1
53.7 | SN1
54.1 | SN1
54 | SN1
54.2 | SN1
54.4 | SN1
54.7 | SN1
55 | SN1
55.1 | SN1
55.3 | SN1
55.5 | SN1
55.7 | SN1
55.7 | SN1
55.8 | SN1
56 | SN1
57.9 | SN1
56.8 | SN1
56.6 | SN1
55.9 | SN1
55.3 | SN1
55.2 | SN1
55.2 | SN1
54.9 | SN1
54.7 | SN1
54.7 | SN1
54.3 | SN1
54.2 | SN1
53.7 | SN1
53.5 | SN1
53.1 | SN1
53.5 | SN1
53.1 | SN1
52.9 | SN1
52.9 | SN1
53.2 | SN1
53.3 | SN1
53.4 | SN1
53.4 | SN1
53.1 | SN1
53.2 | SN1
53.2 | SN1
52.9 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
52.6 | SN1
53.8 | SN1
53.7 | SN1
53.7 | SN1
54.1 | SN1
54.2 | SN1
53.9 | SN1
54.3 | SN1
54.8 | SN1
54.7 | SN1
55.5 | SN1
55.2 | SN1
55.4 | SN1
55.6 | SN1
55.6 | SN1
56 | SN1
56.2 | SN1
55.9 | SN1
56.1 | SN1
56.2 | SN1
55.8 | SN1
55.6 | SN1
55.3 | SN1
55.2 | SN1
55.3 | SN1
54.9 | SN1
54.7 | SN1
54.3 | SN1
53.8 | SN1
53.9 | SN1
53.5 | SN1
53.4 | SN1
53.4 | SN1
53.4 | SN1
53.4 | SN1
53 | SN1
53.4 | SN1
52.8 | SN1
53.1 | SN1
53 | SN1
53 | SN1
53.1 | SN1
53 | SN1
53.2 | SN1
52.8 | SN1
52.9 | SN1
54 | SN1
54.1 | SN1
54 | SN1
55.2 | SN1
55.9 | SN1
56.1 | SN1
56 | SN1
56.3 | SN1
56.6 | SN1
56.5 | SN1
56.7 | SN1
56.9 | SN1
57 | SN1
57.4 | SN1
57.6 | SN1
57.6 | SN1
57.2 | SN1
57.2 | SN1
57.9 | SN1
57.5 | SN1
57.6 | SN1
57.1 | SN1
56.9 | SN1
56.2 | SN1
55.7 | SN1
55.5 | SN1
55.1 | SN1
54.7 | SN1
54.6 | SN1
54.4 | SN1
54.1 | SN1
53.7 | SN1
54.2 | SN1
54.7 | SN1
55.3 | SN1
55.1 | SN1
55.8 | SN1
55.6 | SN1
55.3 | SN1
55.5 | SN1
55.5 | SN1
55.6 | SN1
55.6 | SN1
55.5 | SN1
55.7 | SN1
55.3 | SN1
55.1 | SN1
55.3 | SN1
55.3 | SN1
55.2 | SN1
55.4 | SN1
55.8 | SN1
55.6 | SN1
56.1 | SN1
55.7 | SN1
56 | SN1
55.9 | SN1
56 | SN1
56.6 | SN1
56.3 | SN1
56.3 | SN1
56.6 | SN1
56.6 | SN1
56.5 | SN1
56.8 | SN1
56.5 | SN1
56.3 | SN1
56.8 | SN1
55.8 | SN1
56.2 | SN1
55.9 | SN1
55.1 | SN1
55.1 | SN1
54.7 | SN1
54 | SN1
53.9 | SN1
53.7 | SN1
53.4 | SN1
53.5 | SN1
53.7 | SN1
53.5 | SN1
53.3 | SN1
53.4 | SN1
53.4 | SN1
53.4 | SN1
53.4 | SN1
53.1 | SN1
53.2 | SN1
53.1 | SN1
53.4 | SN1
54.6 | SN1
55.6 | SN1
55.8 | SN1
56.3 | SN1
56.4 | SN1
56.4 | SN1
56.4 | SN1
56 | SN1
56.4 | SN1
56.6 | SN1
56.5 | SN1
56.7 | SN1
57.2 | SN1
57.2 | SN1
57.3 | SN1
56.9 | SN1
57.5 | SN1
57.4 | SN1
57.8 | SN1
58.5 | SN1
57.3 | SN1
57.5 | SN1
57.3 | SN1
55 | SN1
53.6 | SN1
53.1 | SN1
53.5 | SN1
53.5 | SN1
53.5 | SN1
53.2 | SN1
53.1 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.5 | SN1
52.2 | SN1
52.5 | SN1
52.4 | SN1
52.5 | SN1
52.3 | SN1
52.1 | SN1
52.2 | SN1
52.6 | SN1
53 | SN1
54.2 | SN1
55.6 | SN1
56.6 | SN1
56.9 | SN1
57.4 | SN1
57.7 | SN1
58 | SN1
58.5 | SN1
58.2 | SN1
57.9 | SN1
58.2 | SN1
57.6 | SN1
57.5 | SN1
57.6 | SN1
57.8 | SN1
57.8 | SN1
57.9 | SN1
57.5 | SN1
58.4 | SN1
59.2 | SN1
59 | SN1
58.9 | SN1
59.5 | SN1
60.6 | SN1
60.6 | SN1
60.1 | SN1
60.3 | SN1
60.4 | SN1
60.1 | SN1
59.2 | SN1
58.6 | SN1
58.2 | SN1
57.9 | SN1
57.8 | SN1
57.5 | SN1
57.3 | SN1
57.6 | SN1
57.6 | SN1
56.9 | SN1
57.6 | SN1
59 | SN1
59.6 | SN1
59.6 | SN1
59.8 | SN1
59.8 | SN1
59.8 | SN1
59.8 | SN1
59.9 | SN1
59.8 | SN1
59.9 | SN1
59.7 | SN1
60 | SN1
59.6 | SN1
59.4 | SN1
59.4 | SN1
59.3 | SN1
59.4 | SN1
59.5 | SN1
59 | SN1
59.7 | SN1
59.7 | SN1
60 | SN1
60.4 | SN1
60.5 | SN1
60.5 | SN1
61.2 | SN1
61.4 | SN1
61.3 | SN1
61 | SN1
60.4 | SN1
59.9 | SN1
59.7 | SN1
58.7 | SN1
58 | SN1
57.6 | SN1
57.5 | SN1
56.9 | SN1
56.9 | SN1
56.6 | SN1
56.3 | SN1
56.2 | SN1
56.2 | SN1
56 | SN1
56.2 | SN1
56.1 | SN1
55.8 | SN1
55.6 | SN1
55.4 | SN1
55.4 | SN1
55.4 | SN1
55.5 | SN1
55.7 | SN1
55.8 | SN1
55.5 | SN1
55.5 | SN1
55.3 | SN1
55.5 | SN1
55.6 | SN1
55.5 | SN1
55.3 | SN1
55.2 | SN1
55.4 | SN1
55.5 | SN1
55.7 | SN1
55.7 | SN1
55.9 | SN1
55.9 | SN1
56.1 | SN1
56.4 | SN1
57.1 | SN1
56.5 | SN1
56.7 | SN1
56.9 | SN1
57 | SN1
57 | SN1
56.8 | SN1
56.8 | SN1
56.8 | SN1
56.4 | SN1
55.6 | SN1
55.8 | SN1
55.6 | SN1
55.4 | SN1
54.8 | SN1
54.8 | SN1
54.9 | SN1
54.5 | SN1
54.6 | SN1
54.7 | SN1
54.4 | SN1
54.3 | SN1
54.4 | SN1
54.2 | SN1
54.1 | SN1
54.2 | SN1
54.2 | SN1
54.1 | SN1
53.8 | SN1
53.8 | SN1
53.8 | SN1
53.7 | SN1
53.9 | SN1
54 | SN1
53.6 | SN1
53.6 | SN1
53.5 | SN1
53.5 | SN1
53.4 | SN1
53.6 | SN1
53.7 | SN1
53.9 | SN1
54.2 | SN1
54.6 | SN1
54.8 | SN1
54.7 | SN1
55.1 | SN1
55.3 | SN1
56.3 | SN1
55.8 | SN1
56 | SN1
55.7 | SN1
55.5 | SN1
55.6 | SN1
55.4 | SN1
55.2 | SN1
55.3 | SN1
54.8 | SN1
54.3 | SN1
53.8 | SN1
53.5 | SN1
53.2 | SN1
53.1 | SN1
53.2 | SN1
53.1 | SN1
52.8 | SN1
52.7 | SN1
52.8 | SN1
53 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.2 | SN1
51.9 | SN1
52 | SN1
52 | SN1
50.8 | SN1
50.5 | SN1
50.3 | SN1
50.2 | SN1
50 | SN1
49.7 | SN1
49.3 | SN1
49.8 | SN1
49.6 | SN1
49.3 | SN1
49.2 | SN1
49.6 | SN1
49.9 | SN1
50 | SN1
49.9 | SN1
50.5 | SN1
50.9 | SN1
51.1 | SN1
51 | SN1
50.4 | SN1
50.5 | SN1
51 | SN1
50.6 | SN1
50.5 | SN1
49.9 | SN1
50.3 | SN1
50.7 | SN1
50.5 | SN1
49.8 | SN1
49.2 | SN1
48.6 | SN1
48.6 | SN1
48.5 | SN1
48.3 | SN1
47.9 | SN1
48 | SN1
47.9 | SN1
47.8 | SN1
47.6 | SN1
47.8 | SN1
47.9 | SN1
47.8 | SN1
47.9 | SN1
48 | SN1
47.8 | SN1
47.7 | SN1
47.7 | SN1
47.9 | SN1
47.4 | SN1
47.5 | SN1
48.1 | SN1
47.6 | SN1
47.7 | SN1
47.4 | SN1
47.2 | SN1
46.9 | SN1
48.2 | SN1
52.5 | SN1
53.1 | SN1
52.8 | SN1
52.9 | SN1
52.9 | SN1
53.1 | SN1
53.2 | SN1
53.3 | SN1
53.8 | SN1
53.9 | SN1
53.7 | SN1
53.4 | SN1
53.3 | SN1
53 | SN1
53.2 | SN1
53.3 | SN1
52.8 | SN1
52.3 | SN1
51.4 | SN1
51.1 | SN1
51.2 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
50.6 | SN1
51.1 | SN1
51 | SN1
51 | SN1
51.3 | SN1
51 | SN1
51.1 | SN1
51.2 | SN1
51.3 | SN1
51.2 | SN1
51.2 | SN1
51.3 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.4 | SN1
51.6 | SN1
51.7 | SN1
51.7 | SN1
52 | SN1
52.2 | SN1
52.5 | SN1
52.5 | SN1
52.9 | SN1
53.4 | SN1
53.5 | SN1
53.7 | SN1
53.7 | SN1
53.9 | SN1
53.6 | SN1
54.4 | SN1
53.9 | SN1
54.1 | SN1
53.7 | SN1
53.9 | SN1
52.4 | SN1
52.1 | SN1
52 | SN1
51.8 | SN1
51.7 | SN1
51.5 | SN1
51.4 | SN1
51.2 | SN1
51.9 | SN1
51.6 | SN1
51.3 | SN1
51.3 | SN1
50.7 | SN1
53.3 | SN1
54.8 | SN1
55.8 | SN1
56 | SN1
56.1 | SN1
56 | SN1
56 | SN1
56.1 | SN1
55.8 | SN1
55.9 | SN1
55.6 | SN1
55.5 | SN1
55.5 | SN1
55.4 | SN1
55 | SN1
55.1 | SN1
54.9 | SN1
55.4 | SN1
55.4 | SN1
55.7 | SN1
55.7 | SN1
56.9 | SN1
56.3 | SN1
56.2 | SN1
56.4 | SN1
56.1 | SN1
55.9 | SN1
55.4 | SN1
55.6 | SN1
55.8 | SN1
55.5 | SN1
55.5 | SN1
55.2 | SN1
55.2 | SN1
53.2 | SN1
52.8 | SN1
53 | SN1
52.7 | SN1
53.1 | SN1
53.8 | SN1
53.7 | SN1
53.6 | SN1
54.1 | SN1
54.5 | SN1
54.9 | SN1
55 | SN1
55.3 | SN1
55.2 | SN1
55 | SN1
55.2 | SN1
55.1 | SN1
55.1 | SN1
55.2 | SN1
55 | SN1
55 | SN1
54.7 | SN1
54.8 | SN1
54.5 | SN1
54.4 | SN1
54.8 | SN1
54.8 | SN1
54.6 | SN1
54.9 | SN1
55.2 | SN1
55.5 | SN1
55.4 | SN1
55.9 | SN1
56.5 | SN1
56.6 | SN1
56.7 | SN1
56.6 | SN1
56.3 | SN1
55.6 | SN1
54.9 | SN1
54.7 | SN1
54.9 | SN1
55.4 | SN1
55.6 | SN1
55.4 | SN1
55.5 | SN1
54.4 | SN1
52.5 | SN1
52.8 | SN1
53 | SN1
52.9 | SN1
52.9 | SN1
52.9 | SN1
52.8 | SN1
53.1 | SN1
52.7 | SN1
52.8 | SN1
52.7 | SN1
52.7 | SN1
52.9 | SN1
52.6 | SN1
53.1 | SN1
55.4 | SN1
56.3 | SN1
56.5 | SN1
57.2 | SN1
57.1 | SN1
57.2 | SN1
57.1 | SN1
57 | SN1
56.7 | SN1
56.8 | SN1
56.8 | SN1
56.7 | SN1
56.4 | SN1
56.7 | SN1
56.6 | SN1
56.9 | SN1
56.9 | SN1
57 | SN1
57.2 | SN1
57.3 | SN1
57.5 | SN1
56.9 | SN1
1.2 | SN1
61.2 | SN1
61.6 | SN1
61.6 | SN1
58 | SN1
56.3 | SN1
55.4 | SN1
55.3 | SN1
54.7 | SN1
54.2 | SN1
53.7 | SN1
52.8 | SN1
52.2 | SN1
52.6 | SN1
52.2 | SN1
52.3 | SN1
52.1 | SN1
52.2 | SN1
53.9 | SN1
55.5 | SN1
56 | SN1
57 | SN1
57 | SN1
57.1 | SN1
57.2 | SN1
57.6 | SN1
58 | SN1
57.8 | SN1
58.3 | SN1
57.8 | SN1
57.8 | SN1
57.6 | SN1
57.5 | SN1
57.4 | SN1
57.1 | SN1
57.2 | SN1
57.3 | SN1
57 | SN1
57.3 | SN1
56.9 | SN1
57.5 | SN1
57.6 | SN1
57.4 | SN1
57.5 | SN1
57.3 | SN1
56.9 | SN1
57 | SN1
56.3 | SN1
56.6 | SN1
56.3 | SN1
56 | SN1
56.3 | SN1
55.8 | SN1
55.3 | SN1
54.9 | SN1
54.7 | SN1
54.4 | SN1
54.1 | SN1
54.4 | SN1
54 | SN1
54.1 | SN1
53.9 | SN1
53.9 | SN1
53.8 | SN1
53.6 | SN1
53.5 | SN1
53.3 | SN1
53.6 | SN1
53.5 | SN1
53.4 | SN1
53.6 | SN1
53.6 | SN1
53.4 | SN1
53.5 | SN1
53.2 | SN1
53.3 | SN1
53 | SN1
53.2 | SN1
53.4 | SN1
53.3 | SN1
53.3 | SN1
53.4 | SN1
53.4 | SN1
53.8 | SN1
53.8 | SN1
53.4 | SN1
53.8 | SN1
54 | SN1
53.7 | SN1
54.1 | SN1
54 | SN1
53.5 | SN1
53.8 | SN1
53.5 | SN1
54.3 | SN1
54 | SN1
53.8 | SN1
54.1 | SN1
52.8 | SN1
52.4 | SN1
51.9 | SN1
51.8 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
51.1 | SN1
51.1 | SN1
50.7 | SN1
50.6 | SN1
50.4 | SN1
50.2 | SN1
50.7 | SN1
49.7 | SN1
49.7 | SN1
50 | SN1
50 | SN1
49.7 | SN1
50 | SN1
49.2 | SN1
49.6 | SN1
48.8 | SN1
49.5 | SN1
49.3 | SN1
49.3 | SN1
48.6 | SN1
48.9 | SN1
49.3 | SN1
49.1 | SN1
48.9 | SN1
48.9 | SN1
48.4 | SN1
49 | SN1
48.5 | SN1
49 | SN1
48.7 | SN1
56.8 | SN1
53.8 | SN1
53 | SN1
53.4 | SN1
53.6 | SN1
54.4 | SN1
54.1 | SN1
53.7 | SN1
52.5 | SN1
52.4 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
51.6 | SN1
51.2 | SN1
51.5 | SN1
51 | SN1
51.4 | SN1
51.2 | SN1
51.5 | SN1
51.5 | SN1
51.8 | SN1
51.5 | SN1
51.3 | SN1
51.4 | SN1
51.5 | SN1
51.3 | SN1
51.7 | SN1
51.4 | SN1
51.6 | SN1
51.3 | SN1
51.8 | SN1
51.4 | SN1
51.3 | SN1
51.5 | SN1
51.7 | SN1
51.2 | SN1
51.7 | SN1
51.6 | SN1
51.8 | SN1
51.3 | SN1
52 | SN1
52.2 | SN1
52.1 | SN1
52.4 | SN1
52.6 | SN1
52.9 | SN1
53.1 | SN1
53.1 | SN1
52.9 | SN1
53 | SN1
53.4 | SN1
53.1 | SN1
53 | SN1
51.9 | SN1
52.5 | SN1
51 | SN1
51.2 | SN1
51.3 | SN1
51.5 | SN1
51.7 | SN1
51.6 | SN1
51.3 | SN1
51.2 | SN1
51.2 | SN1
50.8 | SN1
50.7 | SN1
50.9 | SN1
50.9 | SN1
51.1 | SN1
51 | SN1
51 | SN1
50.8 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.7 | SN1
50.8 | SN1
50.6 | SN1
50.8 | SN1
50.6 | SN1
50.7 | SN1
50.8 | SN1
50.6 | SN1
50.9 | SN1
50.5 | SN1
50.7 | SN1
51.1 | SN1
51.4 | SN1
51.8 | SN1
51.6 | SN1
52 | SN1
51.8 | SN1
52 | SN1
52.7 | SN1
53 | SN1
52.8 | SN1
53 | SN1
53.8 | SN1
53.2 | SN1
53.2 | SN1
52.6 | SN1
52.4 | SN1
51.9 | SN1
52.1 | SN1
52.9 | SN1
53 | SN1
53 | SN1
53.2 | SN1
52.5 | SN1
52.7 | SN1
52.8 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.6 | SN1
52.4 | SN1
52.4 | SN1
52.4 | SN1
52.4 | SN1
52.3 | SN1
51.9 | SN1
52.4 | SN1
52.1 | SN1
51.9 | SN1
52.4 | SN1
52.3 | SN1
52.5 | SN1
52.4 | SN1
51.9 | SN1
52 | SN1
51.7 | SN1
53.8 | SN1
57.1 | SN1
58.5 | SN1
59.4 | SN1
59.1 | SN1
59.2 | SN1
59.4 | SN1
59.6 | SN1
59.7 | SN1
59.5 | SN1
59.8 | SN1
59.7 | SN1
59.5 | SN1
59.5 | SN1
58.2 | SN1
54.3 | SN1
53.5 | SN1
52.9 | SN1
52.7 | SN1
52.2 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
51.7 | SN1
51.6 | SN1
51.3 | SN1
51.3 | SN1
51.4 | SN1
51.8 | SN1
52 | SN1
54.3 | SN1
54.7 | SN1
55.6 | SN1
55.5 | SN1
56 | SN1
56.6 | SN1
56.5 | SN1
56.4 | SN1
56.2 | SN1
56.2 | SN1
55.8 | SN1
55.6 | SN1
55.9 | SN1
55.9 | SN1
55.5 | SN1
55.6 | SN1
55.7 | SN1
55.5 | SN1
55.8 | SN1
57.6 | SN1
58.6 | SN1
58.9 | SN1
59.2 | SN1
56.8 | SN1
55.8 | SN1
55.9 | SN1
55.6 | SN1
55.8 | SN1
55.5 | SN1
55.6 | SN1
55.1 | SN1
55.4 | SN1
55.1 | SN1
54.8 | SN1
54.7 | SN1
54.6 | SN1
53.3 | SN1
52.6 | SN1
52.9 | SN1
53.1 | SN1
52.7 | SN1
52.3 | SN1
52.2 | SN1
52.3 | SN1
52.4 | SN1
52.1 | SN1
52.5 | SN1
52.4 | SN1
52.5 | SN1
52.5 | SN1
52.1 | SN1
52.4 | SN1
52.8 | SN1
52.6 | SN1
52.5 | SN1
52.6 | SN1
52.5 | SN1
52.7 | SN1
52.3 | SN1
52.6 | SN1
52.3 | SN1
52.7 | SN1
52.5 | SN1
52.9 | SN1
52.9 | SN1
53 | SN1
53.1 | SN1
53.8 | SN1
53.6 | SN1
53.4 | SN1
54.1 | SN1
54.1 | SN1
53.9 | SN1
54.3 | SN1
54.4 | SN1
54 | SN1
54 | SN1
53.8 | SN1
53.8 | SN1
53.4 | SN1
53.1 | SN1
53.4 | SN1
53.1 | SN1
53.1 | SN1
52.6 | SN1
52.2 | SN1
51.9 | SN1
51.6 | SN1
52.2 | SN1
52.1 | SN1
51.8 | SN1
52.5 | SN1
54 | SN1
54.4 | SN1
54.7 | SN1
54.9 | SN1
54.5 | SN1
54.4 | SN1
54.5 | SN1
54.4 | SN1
54.4 | SN1
54.4 | SN1
54.2 | SN1
54.1 | SN1
54.1 | SN1
53.6 | SN1
53.9 | SN1
53.6 | SN1
53.8 | SN1
54 | SN1
54.2 | SN1
54.3 | SN1
54.7 | SN1
55.2 | SN1
55 | SN1
54.7 | SN1
54.6 | SN1
54.7 | SN1
55 | SN1
55.5 | SN1
55.2 | SN1
54.9 | SN1
54.9 | SN1
54.9 | SN1
54.7 | SN1
54.9 | SN1
54 | SN1
53.8 | SN1
53.4 | SN1
52.7 | SN1
52.7 | SN1
52.3 | SN1
53.8 | SN1
54.8 | SN1
55 | SN1
55 | SN1
55.2 | SN1
54.8 | SN1
55.2 | SN1
54.9 | SN1
54.6 | SN1
54.5 | SN1
54.4 | SN1
54.4 | SN1
54.4 | SN1
54.3 | SN1
54.1 | SN1
53.9 | SN1
54.1 | SN1
54 | SN1
53.9 | SN1
54 | SN1
54.1 | SN1
53.9 | SN1
54.1 | SN1
54.3 | SN1
54.4 | SN1
54.6 | SN1
54.7 | SN1
55 | SN1
55 | SN1
55 | SN1
55 | SN1
55.4 | SN1
54.6 | SN1
54.7 | SN1
55.1 | SN1
54.8 | SN1
55 | SN1
54.6 | SN1
54.7 | SN1
54.3 | SN1
54.1 | SN1
53.6 | SN1
52.6 | SN1
52.4 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.2 | SN1
52 | SN1
52 | SN1
52 | SN1
52 | SN1
51.8 | SN1
51.7 | SN1
51.5 | SN1
51.8 | SN1
51.5 | SN1
51.4 | SN1
51.5 | SN1
51.6 | SN1
51.3 | SN1
51.7 | SN1
51.6 | SN1
51.3 | SN1
51.4 | SN1
51.3 | SN1
51.4 | SN1
51.2 | SN1
51.1 | SN1
51.5 | SN1
52.7 | SN1
54.5 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
0 | SN1
55.5 | SN1
54.6 | SN1
54.1 | SN1
53.4 | SN1
53.6 | SN1
53.3 | SN1
53.2 | SN1
53.1 | SN1
52.5 | SN1
51.9 | SN1
51.3 | SN1
51.3 | SN1
51.5 | SN1
50.8 | SN1
50.9 | SN1
50.9 | SN1
50.9 | SN1
50.7 | SN1
50.9 | SN1
50.6 | SN1
50.7 | SN1
50.7 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.4 | SN1
50.7 | SN1
50.3 | SN1
50.3 | SN1
50.4 | SN1
50.5 | SN1
50.2 | SN1
50.1 | SN1
50.2 | SN1
50.2 | SN1
50.3 | SN1
50.5 | SN1
50.5 | SN1
50.6 | SN1
50.6 | SN1
51.1 | SN1
51.5 | SN1
51.6 | SN1
51.6 | SN1
51.9 | SN1
51.9 | SN1
52.4 | SN1
51.8 | SN1
52.2 | SN1
52.2 | SN1
52 | SN1
52.5 | SN1
52.3 | SN1
51.9 | SN1
51.6 | SN1
51.9 | SN1
51.6 | SN1
51 | SN1
50.5 | SN1
50.3 | SN1
50.6 | SN1
50.3 | SN1
50.5 | SN1
50.1 | SN1
50.1 | SN1
49.9 | SN1
49.9 | SN1
49.8 | SN1
50 | SN1
50.1 | SN1
49.8 | SN1
50.3 | SN1
49.9 | SN1
50 | SN1
49.9 | SN1
50.1 | SN1
49.8 | SN1
49.6 | SN1
49.9 | SN1
49.4 | SN1
49.5 | SN1
49.3 | SN1
49.5 | SN1
49.6 | SN1
49.9 | SN1
50 | SN1
50.3 | SN1
51.1 | SN1
51.1 | SN1
51.6 | SN1
51.1 | SN1
51.4 | SN1
51.6 | SN1
52.6 | SN1
52.1 | SN1
52 | SN1
52.4 | SN1
51.8 | SN1
51.8 | SN1
51.3 | SN1
51.5 | SN1
51.5 | SN1
50.8 | SN1
50.7 | SN1
50.6 | SN1
50.4 | SN1
50.2 | SN1
50.6 | SN1
50 | SN1
50.2 | SN1
50.3 | SN1
50 | SN1
50.1 | SN1
50.1 | SN1
50.1 | SN1
49.8 | SN1
49.8 | SN1
49.6 | SN1
49.9 | SN1
50 | SN1
49.6 | SN1
49.6 | SN1
49.2 | SN1
49.5 | SN1
49.9 | SN1
49.6 | SN1
49.4 | SN1
49.5 | SN1
49.5 | SN1
49.5 | SN1
49.6 | SN1
50.3 | SN1
50.5 | SN1
51.2 | SN1
51.8 | SN1
51.8 | SN1
51.6 | SN1
52 | SN1
52.2 | SN1
52.6 | SN1
52.3 | SN1
52.4 | SN1
52.7 | SN1
52.6 | SN1
52.3 | SN1
52.8 | SN1
51.9 | SN1
51.7 | SN1
51.5 | SN1
51.3 | SN1
51.2 | SN1
50.3 | SN1
50.1 | SN1
50.1 | SN1
50 | SN1
50 | SN1
50.2 | SN1
49.7 | SN1
49.7 | SN1
49.5 | SN1
49.7 | SN1
49.8 | SN1
49.5 | SN1
49.7 | SN1
49.2 | SN1
49.4 | SN1
49.4 | SN1
49.5 | SN1
49.2 | SN1
49.1 | SN1
49.2 | SN1
49 | SN1
49.6 | SN1
49.2 | SN1
49.1 | SN1
49.2 | SN1
49.4 | SN1
49.7 | SN1
50.4 | SN1
50.4 | SN1
51.1 | SN1
50.9 | SN1
51.4 | SN1
51.7 | SN1
52 | SN1
51.8 | SN1
52.1 | SN1
52.1 | SN1
52.5 | SN1
52.3 | SN1
51.9 | SN1
52.1 | SN1
51.9 | SN1
51.5 | SN1
51.2 | SN1
51 | SN1
51 | SN1
50.3 | SN1
50 | SN1
49.7 | SN1
49.7 | SN1
49.7 | SN1
49.9 | SN1
49.6 | SN1
49.7 | SN1
49.6 | SN1
49.7 | SN1
49.5 | SN1
49.6 | SN1
49.3 | SN1
49.1 | SN1
49.3 | SN1
49.3 | SN1
49.2 | SN1
49.2 | SN1
49 | SN1
49 | SN1
49.1 | SN1
48.8 | SN1
48.9 | SN1
49.2 | SN1
49 | SN1
49.4 | SN1
49.3 | SN1
49.5 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.9 | SN1
51.2 | SN1
51.1 | SN1
51.4 | SN1
51.4 | SN1
51.8 | SN1
52 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
51.8 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.1 | SN1
50.7 | SN1
50.6 | SN1
49.7 | SN1
49.8 | SN1
49.8 | SN1
49.8 | SN1
49.6 | SN1
49.8 | SN1
49.9 | SN1
49.4 | SN1
49.5 | SN1
49.5 | SN1
49.4 | SN1
49.3 | SN1
49.2 | SN1
49.1 | SN1
49.3 | SN1
49.3 | SN1
49.1 | SN1
49.2 | SN1
49 | SN1
49.3 | SN1
49.2 | SN1
49.2 | SN1
49.3 | SN1
49.4 | SN1
49.7 | SN1
50 | SN1
50.2 | SN1
50.2 | SN1
50.5 | SN1
50.6 | SN1
50.8 | SN1
49.3 | SN1
49.4 | SN1
49.9 | SN1
49.9 | SN1
49.6 | SN1
50 | SN1
49.5 | SN1
50.3 | SN1
49.8 | SN1
49.9 | SN1
49.1 | SN1
49.4 | SN1
49.4 | SN1
48.9 | SN1
48.6 | SN1
48.4 | SN1
48.4 | SN1
47.8 | SN1
47.5 | SN1
47.6 | SN1
48.2 | SN1
48.9 | SN1
49.2 | SN1
48.9 | SN1
48.9 | SN1
48.7 | SN1
48.8 | SN1
48.6 | SN1
48.7 | SN1
48.9 | SN1
48.6 | SN1
48.3 | SN1
48.4 | SN1
48.3 | SN1
48.1 | SN1
48.3 | SN1
48.2 | SN1
48.5 | SN1
48.8 | SN1
48.5 | SN1
49.3 | SN1
49 | SN1
49.4 | SN1
49.2 | SN1
49.4 | SN1
49.1 | SN1
51.4 | SN1
51.8 | SN1
51.8 | SN1
51.4 | SN1
51.6 | SN1
52.1 | SN1
51.7 | SN1
51.2 | SN1
51.4 | SN1
51.2 | SN1
51.2 | SN1
50.7 | SN1
50.7 | SN1
49.8 | SN1
50 | SN1
49.8 | SN1
49.7 | SN1
49.5 | SN1
49.4 | SN1
49.6 | SN1
49.6 | SN1
49.5 | SN1
49.5 | SN1
49.6 | SN1
49.3 | SN1
49.4 | SN1
49.5 | SN1
49.1 | SN1
49 | SN1
48.9 | SN1
49.2 | SN1
49.3 | SN1
49.1 | SN1
49.3 | SN1
49 | SN1
49.1 | SN1
49.4 | SN1
49.3 | SN1
49.4 | SN1
49.5 | SN1
49.6 | SN1
50.7 | SN1
50.2 | SN1
50.4 | SN1
50.3 | SN1
50.5 | SN1
50.6 | SN1
50.7 | SN1
50.4 | SN1
50.9 | SN1
51.2 | SN1
51.1 | SN1
50.7 | SN1
50.5 | SN1
49.9 | SN1
50.2 | SN1
49.9 | SN1
49.6 | SN1
49.5 | SN1
49.6 | SN1
49.3 | SN1
49.3 | SN1
49.3 | SN1
49.4 | SN1
49.3 | SN1
49.1 | SN1
48.8 | SN1
49.1 | SN1
49.1 | SN1
49 | SN1
49 | SN1
48.7 | SN1
48.8 | SN1
48.7 | SN1
48.9 | SN1
48.9 | SN1
49 | SN1
48.6 | SN1
48.7 | SN1
48.7 | SN1
49 | SN1
49 | SN1
48.9 | SN1
48.9 | SN1
49 | SN1
48.7 | SN1
49.8 | SN1
49.4 | SN1
49.6 | SN1
49.9 | SN1
49.8 | SN1
50.2 | SN1
48.2 | SN1
48.7 | SN1
49.2 | SN1
49 | SN1
49.4 | SN1
49.3 | SN1
49.2 | SN1
48.9 | SN1
48.9 | SN1
48.6 | SN1
48.7 | SN1
48.2 | SN1
48.2 | SN1
48.1 | SN1
48 | SN1
47.5 | SN1
47.6 | SN1
47.4 | SN1
47.2 | SN1
47.6 | SN1
47.3 | SN1
47.2 | SN1
47.1 | SN1
47 | SN1
47.1 | SN1
47.1 | SN1
47.3 | SN1
47.3 | SN1
47.1 | SN1
47.1 | SN1
47 | SN1
47 | SN1
47 | SN1
46.8 | SN1
47 | SN1
47 | SN1
47 | SN1
46.9 | SN1
47.6 | SN1
47.4 | SN1
47.7 | SN1
48.3 | SN1
48.8 | SN1
49.3 | SN1
49.7 | SN1
49.7 | SN1
51.6 | SN1
51.6 | SN1
51.5 | SN1
51.7 | SN1
52.4 | SN1
52 | SN1
52.5 | SN1
52.1 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
51.6 | SN1
51 | SN1
51.3 | SN1
50.8 | SN1
50.5 | SN1
49.9 | SN1
50.4 | SN1
50.1 | SN1
49.7 | SN1
49.5 | SN1
49.8 | SN1
49.7 | SN1
49.9 | SN1
50 | SN1
49.9 | SN1
50.4 | SN1
50 | SN1
50.2 | SN1
50.1 | SN1
50 | SN1
49.6 | SN1
49.6 | SN1
49.8 | SN1
49.6 | SN1
49.7 | SN1
49.4 | SN1
49.4 | SN1
49.9 | SN1
50.1 | SN1
56.1 | SN1
51.8 | SN1
50.9 | SN1
51.3 | SN1
51.2 | SN1
51.1 | SN1
51.4 | SN1
51.3 | SN1
51.7 | SN1
51.9 | SN1
52.1 | SN1
51.9 | SN1
52.5 | SN1
51.9 | SN1
52 | SN1
51.7 | SN1
52.8 | SN1
52.9 | SN1
52.7 | SN1
52.6 | SN1
52.4 | SN1
52.5 | SN1
52.2 | SN1
52.3 | SN1
52.1 | SN1
52 | SN1
51.9 | SN1
52.2 | SN1
51.9 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
51.8 | SN1
51.6 | SN1
51.8 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
51.6 | SN1
51.3 | SN1
51.3 | SN1
51.6 | SN1
51.8 | SN1
51.9 | SN1
51.8 | SN1
52 | SN1
52 | SN1
52 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.6 | SN1
52.1 | SN1
51.7 | SN1
52.5 | SN1
52.1 | SN1
52.3 | SN1
51.8 | SN1
51.2 | SN1
51.2 | SN1
51.4 | SN1
50.8 | SN1
50.6 | SN1
50.7 | SN1
50.7 | SN1
50.3 | SN1
50.8 | SN1
50.5 | SN1
50.3 | SN1
50.2 | SN1
50.3 | SN1
49.9 | SN1
50.6 | SN1
50.6 | SN1
50.7 | SN1
50.6 | SN1
50.4 | SN1
51.1 | SN1
50.8 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.2 | SN1
50.5 | SN1
50.5 | SN1
50.2 | SN1
49.9 | SN1
50.3 | SN1
50 | SN1
50.2 | SN1
51.1 | SN1
51.4 | SN1
51.1 | SN1
51.1 | SN1
51.3 | SN1
51.7 | SN1
52 | SN1
52.3 | SN1
52 | SN1
51.9 | SN1
51.8 | SN1
52.2 | SN1
52.3 | SN1
52 | SN1
51.3 | SN1
51.1 | SN1
51.2 | SN1
51.2 | SN1
50.6 | SN1
50.6 | SN1
50.4 | SN1
50.2 | SN1
50 | SN1
50.3 | SN1
50.1 | SN1
50.2 | SN1
50 | SN1
50.1 | SN1
50.3 | SN1
50 | SN1
49.9 | SN1
50.2 | SN1
49.6 | SN1
50 | SN1
49.9 | SN1
50 | SN1
50 | SN1
49.9 | SN1
49.7 | SN1
49.8 | SN1
49.8 | SN1
49.8 | SN1
49.9 | SN1
49.5 | SN1
49.7 | SN1
50 | SN1
50.4 | SN1
50.7 | SN1
51.3 | SN1
50.7 | SN1
51 | SN1
51.3 | SN1
52.2 | SN1
52 | SN1
52.1 | SN1
52.2 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
52.3 | SN1
51.8 | SN1
51.7 | SN1
51.2 | SN1
51.3 | SN1
51 | SN1
50.1 | SN1
50 | SN1
50.1 | SN1
49.7 | SN1
49.3 | SN1
49.4 | SN1
49.5 | SN1
49.6 | SN1
49.6 | SN1
50 | SN1
50 | SN1
50.1 | SN1
50.3 | SN1
50 | SN1
50.2 | SN1
50.4 | SN1
50.1 | SN1
50.2 | SN1
49.9 | SN1
50.1 | SN1
49.8 | SN1
49.8 | SN1
49.9 | SN1
49.7 | SN1
49.8 | SN1
49.9 | SN1
50.4 | SN1
50.2 | SN1
50.9 | SN1
51.3 | SN1
51 | SN1
51.4 | SN1
51 | SN1
51.9 | SN1
51.3 | SN1
51.1 | SN1
51.4 | SN1
52 | SN1
51.7 | SN1
50.9 | SN1
50.4 | SN1
50.3 | SN1
50.3 | SN1
50.3 | SN1
49.8 | SN1
49.6 | SN1
49.6 | SN1
49.3 | SN1
48.9 | SN1
48.9 | SN1
48.8 | SN1
49 | SN1
48.8 | SN1
48.8 | SN1
49.2 | SN1
49 | SN1
49.4 | SN1
49.3 | SN1
49.1 | SN1
49.3 | SN1
48.8 | SN1
49 | SN1
49 | SN1
49 | SN1
49.1 | SN1
48.9 | SN1
48.9 | SN1
48.8 | SN1
48.8 | SN1
48.9 | SN1
49 | SN1
48.8 | SN1
48.9 | SN1
49.2 | SN1
49.2 | SN1
49.2 | SN1
50 | SN1
50.4 | SN1
50.9 | SN1
51 | SN1
50.8 | SN1
51.2 | SN1
51.5 | SN1
51.3 | SN1
51.3 | SN1
50.4 | SN1
50.4 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
49.5 | SN1
50 | SN1
50.1 | SN1
50.2 | SN1
50.2 | SN1
50.2 | SN1
50.3 | SN1
49.8 | SN1
50 | SN1
49.9 | SN1
49.8 | SN1
49.9 | SN1
49.9 | SN1
49.9 | SN1
49.9 | SN1
50 | SN1
49.8 | SN1
49.9 | SN1
49.7 | SN1
49.7 | SN1
49.8 | SN1
49.8 | SN1
49.5 | SN1
49.5 | SN1
49.4 | SN1
49.3 | SN1
49.4 | SN1
49.5 | SN1
49.4 | SN1
49.7 | SN1
49.3 | SN1
50 | SN1
50.1 | SN1
50.6 | SN1
50.3 | SN1
50.9 | SN1
51.2 | SN1
51.5 | SN1
51.4 | SN1
51.5 | SN1
51.2 | SN1
50.9 | SN1
51.2 | SN1
50.2 | SN1
50.3 | SN1
50.1 | SN1
50.2 | SN1
50 | SN1
49.5 | SN1
49.4 | SN1
49.2 | SN1
49.3 | SN1
49 | SN1
49 | SN1
49.1 | SN1
48.9 | SN1
49.2 | SN1
48.9 | SN1
49.2 | SN1
48.6 | SN1
49 | SN1
48.9 | SN1
49.3 | SN1
49.1 | SN1
49 | SN1
48.9 | SN1
48.9 | SN1
48.9 | SN1
48.8 | SN1
48.8 | SN1
50 | SN1
50.7 | SN1
50.4 | SN1
50.6 | SN1
50.7 | SN1
50.7 | SN1
50.9 | SN1
51.1 | SN1
51 | SN1
50.9 | SN1
50.9 | SN1
51.2 | SN1
51.4 | SN1
51.4 | SN1
51.7 | SN1
51.4 | SN1
51 | SN1
51.1 | SN1
50.5 | SN1
50.4 | SN1
50 | SN1
50.1 | SN1
50 | SN1
50.1 | SN1
49.5 | SN1
49.4 | SN1
49.8 | SN1
50.1 | SN1
50.2 | SN1
50.5 | SN1
50.2 | SN1
50.3 | SN1
50.3 | SN1
50.7 | SN1
50.6 | SN1
50.4 | SN1
50.5 | SN1
50.2 | SN1
50.3 | SN1
50 | SN1
50.1 | SN1
50.2 | SN1
50.1 | SN1
50.2 | SN1
50.1 | SN1
50.2 | SN1
50.5 | SN1
50.9 | SN1
50.6 | SN1
50.6 | SN1
50.7 | SN1
50.8 | SN1
51 | SN1
50.9 | SN1
51.1 | SN1
51 | SN1
51.3 | SN1
51.4 | SN1
51.4 | SN1
51.2 | SN1
51.6 | SN1
51.6 | SN1
51.4 | SN1
51.2 | SN1
50.4 | SN1
49.9 | SN1
49.9 | SN1
50 | SN1
50.4 | SN1
50.4 | SN1
50 | SN1
49.6 | SN1
49.4 | SN1
49.3 | SN1
49.5 | SN1
49.3 | SN1
49.4 | SN1
49.4 | SN1
49.3 | SN1
49.5 | SN1
49.6 | SN1
49.6 | SN1
49.6 | SN1
49.6 | SN1
49.6 | SN1
49.5 | SN1
49.5 | SN1
49.3 | SN1
49.5 | SN1
49.5 | SN1
49.4 | SN1
49.6 | SN1
49.7 | SN1
49.6 | SN1
49.6 | SN1
49.8 | SN1
50 | SN1
49.9 | SN1
58.6 | SN1
52.4 | SN1
51 | SN1
50.8 | SN1
50.2 | SN1
49.9 | SN1
49.8 | SN1
49.7 | SN1
49.6 | SN1
49.7 | SN1
49.2 | SN1
49.1 | SN1
49 | SN1
48.9 | SN1
48.8 | SN1
48.7 | SN1
48.4 | SN1
48.2 | SN1
48.1 | SN1
47.7 | SN1
47.1 | SN1
47.1 | SN1
47.2 | SN1
47.3 | SN1
47.5 | SN1
47.4 | SN1
47.5 | SN1
47.7 | SN1
47.4 | SN1
47.4 | SN1
47.2 | SN1
49 | SN1
49.9 | SN1
49.7 | SN1
49.8 | SN1
50.3 | SN1
50.5 | SN1
50.2 | SN1
50.3 | SN1
49.9 | SN1
50.2 | SN1
49.9 | SN1
49.8 | SN1
49.9 | SN1
49.8 | SN1
49.9 | SN1
50 | SN1
50.1 | SN1
50.9 | SN1
51.3 | SN1
50.9 | SN1
50.9 | SN1
51.2 | SN1
51.2 | SN1
51.6 | SN1
51.5 | SN1
51.5 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51.1 | SN1
51.2 | SN1
50.7 | SN1
50.5 | SN1
50.3 | SN1
49.8 | SN1
49.7 | SN1
49.8 | SN1
49.6 | SN1
52.5 | SN1
52.5 | SN1
52.3 | SN1
52.3 | SN1
52.4 | SN1
52.8 | SN1
53.6 | SN1
53.4 | SN1
53.2 | SN1
53.2 | SN1
53 | SN1
52.6 | SN1
52.6 | SN1
52.7 | SN1
52.5 | SN1
52.3 | SN1
52.1 | SN1
52.2 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
51.9 | SN1
52.1 | SN1
52.4 | SN1
52.8 | SN1
52.6 | SN1
52.3 | SN1
52.2 | SN1
52.3 | SN1
52.8 | SN1
52.5 | SN1
52.5 | SN1
52 | SN1
52.4 | SN1
52.5 | SN1
52.8 | SN1
52.4 | SN1
52 | SN1
52.3 | SN1
51.6 | SN1
51.2 | SN1
51.1 | SN1
50.8 | SN1
50.4 | SN1
50 | SN1
50.1 | SN1
49.8 | SN1
50.1 | SN1
49.9 | SN1
50.3 | SN1
50 | SN1
49.9 | SN1
49.9 | SN1
49.7 | SN1
50.1 | SN1
49.6 | SN1
49.8 | SN1
49.8 | SN1
49.9 | SN1
49.9 | SN1
49.7 | SN1
49.6 | SN1
49.4 | SN1
49.3 | SN1
49.4 | SN1
49.2 | SN1
49.2 | SN1
49.4 | SN1
49.5 | SN1
49.5 | SN1
50.3 | SN1
50.6 | SN1
50.8 | SN1
50.8 | SN1
51.1 | SN1
51.2 | SN1
51.6 | SN1
51.5 | SN1
52.2 | SN1
51.6 | SN1
51.8 | SN1
51.9 | SN1
52.2 | SN1
51.4 | SN1
51.2 | SN1
51.1 | SN1
50.3 | SN1
50.4 | SN1
50.1 | SN1
49.6 | SN1
49.7 | SN1
49.5 | SN1
49.5 | SN1
49.5 | SN1
49.4 | SN1
49.3 | SN1
49.3 | SN1
49.6 | SN1
49.6 | SN1
49.4 | SN1
49.4 | SN1
49 | SN1
48.9 | SN1
49 | SN1
49.2 | SN1
48.8 | SN1
49.1 | SN1
49.2 | SN1
49 | SN1
49.1 | SN1
48.8 | SN1
48.4 | SN1
48.5 | SN1
48.6 | SN1
49.2 | SN1
49.4 | SN1
50.1 | SN1
50.3 | SN1
50.3 | SN1
51 | SN1
51.3 | SN1
52.1 | SN1
52.3 | SN1
52.4 | SN1
52.6 | SN1
53.1 | SN1
53 | SN1
52.5 | SN1
52.2 | SN1
52.9 | SN1
52.5 | SN1
51.8 | SN1
52 | SN1
51.9 | SN1
50.9 | SN1
50.9 | SN1
50.4 | SN1
50.1 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.3 | SN1
50.1 | SN1
50 | SN1
50.2 | SN1
50.1 | SN1
50.1 | SN1
50.1 | SN1
50.4 | SN1
49.7 | SN1
49.8 | SN1
49.9 | SN1
49.5 | SN1
49.3 | SN1
49.1 | SN1
49.3 | SN1
48.5 | SN1
48.6 | SN1
48.1 | SN1
48.2 | SN1
49 | SN1
49.1 | SN1
48.9 | SN1
51.9 | SN1
50.6 | SN1
50.4 | SN1
50.2 | SN1
50.9 | SN1
50.4 | SN1
51.5 | SN1
50.8 | SN1
50.9 | SN1
51.1 | SN1
50.6 | SN1
50.3 | SN1
50.2 | SN1
50.2 | SN1
49.3 | SN1
49.2 | SN1
49.1 | SN1
49.1 | SN1
48.7 | SN1
48.6 | SN1
48.7 | SN1
48.6 | SN1
48.6 | SN1
48.3 | SN1
48.2 | SN1
48.3 | SN1
48.1 | SN1
48.1 | SN1
47.5 | SN1
48 | SN1
48.2 | SN1
48 | SN1
48 | SN1
48 | SN1
48.2 | SN1
47.9 | SN1
47.9 | SN1
47.9 | SN1
47.8 | SN1
47.9 | SN1
47.8 | SN1
48 | SN1
48.1 | SN1
48.9 | SN1
50 | SN1
49.1 | SN1
50 | SN1
50.3 | SN1
50 | SN1
50.3 | SN1
50.5 | SN1
51.3 | SN1
52 | SN1
52 | SN1
52 | SN1
52.1 | SN1
51.9 | SN1
51.2 | SN1
51.2 | SN1
51.7 | SN1
51.1 | SN1
50.7 | SN1
50 | SN1
50.1 | SN1
49.8 | SN1
49.5 | SN1
49.3 | SN1
49 | SN1
49.1 | SN1
49.3 | SN1
49.4 | SN1
49.1 | SN1
48.9 | SN1
48.7 | SN1
48.9 | SN1
48.5 | SN1
48.5 | SN1
48.1 | SN1
47.7 | SN1
47.7 | SN1
47.8 | SN1
47.8 | SN1
47 | SN1
47.8 | SN1
46.7 | SN1
46.7 | SN1
47 | SN1
46.4 | SN1
46.1 | SN1
47 | SN1
47.6 | SN1
47.5 | SN1
49.4 | SN1
50.8 | SN1
50 | SN1
50.6 | SN1
50.5 | SN1
51 | SN1
50.9 | SN1
50.7 | SN1
50.7 | SN1
50.3 | SN1
49.8 | SN1
49.8 | SN1
49.9 | SN1
49.4 | SN1
49.5 | SN1
48.7 | SN1
48.4 | SN1
47.7 | SN1
47.4 | SN1
47.2 | SN1
46.8 | SN1
46.5 | SN1
46.7 | SN1
46.5 | SN1
46.4 | SN1
46.6 | SN1
46.5 | SN1
46.4 | SN1
46.5 | SN1
46.4 | SN1
46.5 | SN1
46.5 | SN1
46.2 | SN1
46.5 | SN1
46.2 | SN1
46 | SN1
46 | SN1
46.1 | SN1
46.1 | SN1
46.3 | SN1
46.3 | SN1
46.6 | SN1
46.7 | SN1
46.9 | SN1
47.2 | SN1
47 | SN1
47.2 | SN1
48.4 | SN1
48.3 | SN1
48.6 | SN1
48.7 | SN1
48.7 | SN1
48.6 | SN1
48.8 | SN1
48.7 | SN1
49.1 | SN1
49 | SN1
49.4 | SN1
48.8 | SN1
48.8 | SN1
48.4 | SN1
48.1 | SN1
47.7 | SN1
47.5 | SN1
47.2 | SN1
47.1 | SN1
47.3 | SN1
47.1 | SN1
47 | SN1
47.3 | SN1
46.9 | SN1
47.1 | SN1
47 | SN1
46.8 | SN1
47 | SN1
47.1 | SN1
46.9 | SN1
47 | SN1
46.9 | SN1
46.8 | SN1
47 | SN1
46.7 | SN1
46.5 | SN1
46.7 | SN1
46.6 | SN1
46.5 | SN1
46.6 | SN1
46.5 | SN1
46.8 | SN1
47.5 | SN1
47.6 | SN1
47.7 | SN1
47.9 | SN1
48.4 | SN1
48.1 | SN1
48.3 | SN1
48.3 | SN1
48 | SN1
48.2 | SN1
53 | SN1
50 | SN1
49.2 | SN1
48.8 | SN1
48.6 | SN1
48.2 | SN1
47.5 | SN1
47.6 | SN1
47.2 | SN1
46.8 | SN1
46.2 | SN1
46.3 | SN1
46.1 | SN1
47.2 | SN1
47.4 | SN1
47.3 | SN1
47.1 | SN1
47.3 | SN1
46.9 | SN1
47.3 | SN1
47.3 | SN1
47.5 | SN1
47.4 | SN1
47.1 | SN1
47.2 | SN1
47 | SN1
46.9 | SN1
46.8 | SN1
47.2 | SN1
47.1 | SN1
46.7 | SN1
46.6 | SN1
46.6 | SN1
47 | SN1
47 | SN1
47.1 | SN1
47.5 | SN1
47.8 | SN1
47.8 | SN1
48.2 | SN1
49 | SN1
48.8 | SN1
49 | SN1
49.3 | SN1
49.1 | SN1
49.5 | SN1
49.2 | SN1
48.6 | SN1
49.1 | SN1
49.4 | SN1
49.2 | SN1
48.9 | SN1
48.9 | SN1
48.3 | SN1
48.3 | SN1
48 | SN1
48.1 | SN1
47.9 | SN1
47.4 | SN1
47.4 | SN1
47.4 | SN1
47.5 | SN1
47.6 | SN1
47.7 | SN1
47.5 | SN1
47.3 | SN1
47.8 | SN1
47.7 | SN1
47.5 | SN1
47.2 | SN1
47 | SN1
46.8 | SN1
46.5 | SN1
46.4 | SN1
46.3 | SN1
46.1 | SN1
46.3 | SN1
45.8 | SN1
45.8 | SN1
45.9 | SN1
45.8 | SN1
45.9 | SN1
46.7 | SN1
47 | SN1
47.1 | SN1
47.4 | SN1
47.3 | SN1
47.9 | SN1
47.8 | SN1
47.9 | SN1
47.6 | SN1
48.2 | SN1
48 | SN1
48.1 | SN1
48.6 | SN1
48.5 | SN1
47.9 | SN1
47.6 | SN1
47.4 | SN1
47 | SN1
46.7 | SN1
46.6 | SN1
46.1 | SN1
46 | SN1
45.8 | SN1
46 | SN1
45.9 | SN1
45.6 | SN1
45.4 | SN1
45.4 | SN1
45.4 | SN1
45.1 | SN1
45.2 | SN1
45.2 | SN1
45.4 | SN1
45.3 | SN1
45.3 | SN1
45.2 | SN1
44.9 | SN1
44.9 | SN1
45.1 | SN1
44.6 | SN1
44.6 | SN1
44.5 | SN1
44.7 | SN1
44.7 | SN1
44.6 | SN1
44.5 | SN1
44.8 | SN1
45.3 | SN1
46 | SN1
46.2 | SN1
46.8 | SN1
47.1 | SN1
47.2 | SN1
47.8 | SN1
47.4 | SN1
47 | SN1
47.6 | SN1
47.3 | SN1
46.5 | SN1
46.9 | SN1
46.6 | SN1
46.3 | SN1
45.9 | SN1
45.7 | SN1
45.6 | SN1
44.9 | SN1
45 | SN1
44.7 | SN1
44.8 | SN1
44.5 | SN1
44.4 | SN1
44.3 | SN1
44.3 | SN1
44.2 | SN1
44 | SN1
44.3 | SN1
43.9 | SN1
43.9 | SN1
44.1 | SN1
43.6 | SN1
44.1 | SN1
43.5 | SN1
43.8 | SN1
43.7 | SN1
43.6 | SN1
43.9 | SN1
43.6 | SN1
43.5 | SN1
43.5 | SN1
43.4 | SN1
43.5 | SN1
43.6 | SN1
43.7 | SN1
43.9 | SN1
44.4 | SN1
44.2 | SN1
44.6 | SN1
45.5 | SN1
45.4 | SN1
45.7 | SN1
45.5 | SN1
45.8 | SN1
45.4 | SN1
45.2 | SN1
45.9 | SN1
45.7 | SN1
45.7 | SN1
45.7 | SN1
45.3 | SN1
45 | SN1
44.7 | SN1
44.4 | SN1
44.7 | SN1
44.2 | SN1
44.2 | SN1
44.1 | SN1
43.6 | SN1
43.7 | SN1
43.5 | SN1
43.8 | SN1
43.8 | SN1
43.9 | SN1
43.8 | SN1
43.5 | SN1
43.6 | SN1
43.3 | SN1
43.4 | SN1
43.5 | SN1
43.6 | SN1
43 | SN1
43.1 | SN1
42.9 | SN1
43.1 | SN1
42.8 | SN1
42.9 | SN1
43 | SN1
43 | SN1
43.1 | SN1
43.6 | SN1
43.9 | SN1
43.9 | SN1
44.5 | SN1
44.2 | SN1
44.9 | SN1
45.2 | SN1
45.1 | SN1
45.8 | SN1
46.2 | SN1
46.2 | SN1
46.4 | SN1
46.4 | SN1
46.1 | SN1
45.2 | SN1
45.8 | SN1
45.3 | SN1
45.3 | SN1
44.8 | SN1
44.3 | SN1
44.1 | SN1
44 | SN1
43.6 | SN1
43.6 | SN1
43.8 | SN1
43.7 | SN1
43.5 | SN1
43.4 | SN1
43.6 | SN1
43.4 | SN1
43.3 | SN1
43.2 | SN1
43.3 | SN1
43.6 | SN1
43.5 | SN1
43.6 | SN1
43.1 | SN1
43.1 | SN1
42.8 | SN1
43 | SN1
42.8 | SN1
42.5 | SN1
42.6 | SN1
42.5 | SN1
42.7 | SN1
42.7 | SN1
42.9 | SN1
43.2 | SN1
43.2 | SN1
44 | SN1
44.2 | SN1
44.8 | SN1
45.4 | SN1
45.8 | SN1
46 | SN1
46.6 | SN1
47.2 | SN1
47.4 | SN1
47 | SN1
47.7 | SN1
46.8 | SN1
47.2 | SN1
46.9 | SN1
46.6 | SN1
46.1 | SN1
45.8 | SN1
45.9 | SN1
45.9 | SN1
45.7 | SN1
45.3 | SN1
45.3 | SN1
45.4 | SN1
45 | SN1
45.1 | SN1
45.4 | SN1
45.4 | SN1
45.5 | SN1
45.4 | SN1
45.6 | SN1
45.4 | SN1
45.3 | SN1
45.2 | SN1
44.9 | SN1
45 | SN1
44.8 | SN1
44.8 | SN1
44.6 | SN1
44.5 | SN1
44.6 | SN1
44.9 | SN1
44.5 | SN1
44.7 | SN1
44.8 | SN1
45 | SN1
45.2 | SN1
46 | SN1
46.1 | SN1
46.2 | SN1
46.8 | SN1
47.2 | SN1
48 | SN1
47.9 | SN1
48.4 | SN1
49.3 | SN1
49.2 | SN1
48.5 | SN1
47.8 | SN1
48.4 | SN1
47.8 | SN1
47.2 | SN1
47.2 | SN1
47.4 | SN1
47 | SN1
47 | SN1
47 | SN1
46.7 | SN1
47 | SN1
46.7 | SN1
46.8 | SN1
46.6 | SN1
46.7 | SN1
46.8 | SN1
46.8 | SN1
46.6 | SN1
46.4 | SN1
46.5 | SN1
46.5 | SN1
46.5 | SN1
46.5 | SN1
46.1 | SN1
46.2 | SN1
46 | SN1
46.2 | SN1
46.4 | SN1
45.9 | SN1
46.3 | SN1
46.1 | SN1
46 | SN1
46.2 | SN1
46.6 | SN1
47 | SN1
47.8 | SN1
48 | SN1
48.2 | SN1
48.4 | SN1
48.5 | SN1
48.6 | SN1
48.4 | SN1
48.8 | SN1
49.4 | SN1
49 | SN1
49 | SN1
49 | SN1
48.7 | SN1
48.8 | SN1
48.3 | SN1
48.1 | SN1
48.2 | SN1
47.8 | SN1
47.8 | SN1
47.6 | SN1
47.7 | SN1
47.7 | SN1
47.5 | SN1
47.1 | SN1
47.3 | SN1
47.5 | SN1
47.4 | SN1
47.4 | SN1
47.1 | SN1
47.3 | SN1
46.8 | SN1
47.4 | SN1
46.8 | SN1
46.8 | SN1
46.9 | SN1
46.7 | SN1
46.8 | SN1
46.6 | SN1
46.7 | SN1
46.5 | SN1
46.7 | SN1
46.8 | SN1
47 | SN1
46.7 | SN1
46.6 | SN1
47.7 | SN1
48 | SN1
48.7 | SN1
48.4 | SN1
49.8 | SN1
50.4 | SN1
50.7 | SN1
50.2 | SN1
50.7 | SN1
50.3 | SN1
50.2 | SN1
49.9 | SN1
50.2 | SN1
50.2 | SN1
50.1 | SN1
50 | SN1
50 | SN1
48.7 | SN1
48.4 | SN1
48.5 | SN1
48.5 | SN1
48.7 | SN1
48.8 | SN1
48.9 | SN1
48.7 | SN1
48.6 | SN1
48.6 | SN1
48.5 | SN1
48.5 | SN1
48.5 | SN1
48.6 | SN1
48.6 | SN1
48.7 | SN1
48.8 | SN1
48.8 | SN1
48.6 | SN1
48.7 | SN1
48.7 | SN1
49 | SN1
48.2 | SN1
48.6 | SN1
48.3 | SN1
48.4 | SN1
48.6 | SN1
48.3 | SN1
48.6 | SN1
49.1 | SN1
49.1 | SN1
49.5 | SN1
49.6 | SN1
49.7 | SN1
49.5 | SN1
49.7 | SN1
49.7 | SN1
49.9 | SN1
50.1 | SN1
49.7 | SN1
51 | SN1
51.3 | SN1
51.4 | SN1
51 | SN1
50.6 | SN1
50.6 | SN1
50.6 | SN1
50.3 | SN1
50.2 | SN1
49.6 | SN1
50 | SN1
49.8 | SN1
49.8 | SN1
50.2 | SN1
50.1 | SN1
50.1 | SN1
50.1 | SN1
50.1 | SN1
50 | SN1
50.2 | SN1
50.2 | SN1
50.1 | SN1
49.9 | SN1
49.9 | SN1
49.9 | SN1
49.6 | SN1
49.8 | SN1
49.8 | SN1
49.5 | SN1
49.5 | SN1
49.8 | SN1
49.8 | SN1
49.7 | SN1
50.3 | SN1
50.4 | SN1
50.1 | SN1
50.4 | SN1
50.1 | SN1
50.6 | SN1
50 | SN1
51 | SN1
51.2 | SN1
51.3 | SN1
50.7 | SN1
50.9 | SN1
51.1 | SN1
51.7 | SN1
51.7 | SN1
51.8 | SN1
51.1 | SN1
50.6 | SN1
50.4 | SN1
50.6 | SN1
50.2 | SN1
49.9 | SN1
49.7 | SN1
49.9 | SN1
49.9 | SN1
49.5 | SN1
49.5 | SN1
49.3 | SN1
49.5 | SN1
49.3 | SN1
49.1 | SN1
49.2 | SN1
49.3 | SN1
49.2 | SN1
49.1 | SN1
48.9 | SN1
49 | SN1
49.2 | SN1
49.1 | SN1
49 | SN1
49.2 | SN1
49.3 | SN1
49.2 | SN1
48.9 | SN1
49.1 | SN1
49.3 | SN1
49.4 | SN1
49.6 | SN1
49.2 | SN1
49.6 | SN1
49.6 | SN1
50.3 | SN1
50.4 | SN1
51.1 | SN1
50.2 | SN1
50.5 | SN1
51 | SN1
51.2 | SN1
51.4 | SN1
51.3 | SN1
50.7 | SN1
50.5 | SN1
49.5 | SN1
49 | SN1
48.2 | SN1
48.5 | SN1
47.9 | SN1
48.1 | SN1
48.3 | SN1
48.2 | SN1
48.2 | SN1
48.4 | SN1
48.1 | SN1
48.2 | SN1
48 | SN1
48 | SN1
48 | SN1
48.1 | SN1
47.8 | SN1
47.8 | SN1
48.2 | SN1
48.2 | SN1
47.9 | SN1
48 | SN1
47.6 | SN1
47.7 | SN1
47.8 | SN1
47.6 | SN1
47.7 | SN1
47.6 | SN1
47.6 | SN1
47.6 | SN1
48 | SN1
48 | SN1
48.3 | SN1
48.6 | SN1
49 | SN1
47.3 | SN1
47.5 | SN1
48.1 | SN1
48.1 | SN1
51 | SN1
48.4 | SN1
47.2 | SN1
52.3 | SN1
49.9 | SN1
48.9 | SN1
51.3 | SN1
51.6 | SN1
51.7 | SN1
51.8 | SN1
51.5 | SN1
51.2 | SN1
51.1 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
50.4 | SN1
50.3 | SN1
50.2 | SN1
50.3 | SN1
49.9 | SN1
50.1 | SN1
50.2 | SN1
49.9 | SN1
49.7 | SN1
49.7 | SN1
49.8 | SN1
49.6 | SN1
49.8 | SN1
49.4 | SN1
49.3 | SN1
49.3 | SN1
49.1 | SN1
49.2 | SN1
49.1 | SN1
49.3 | SN1
49.5 | SN1
49.4 | SN1
49.9 | SN1
49.8 | SN1
49.9 | SN1
50.3 | SN1
50.1 | SN1
51.4 | SN1
51.7 | SN1
52.2 | SN1
51.6 | SN1
51.7 | SN1
52 | SN1
51.7 | SN1
51.2 | SN1
51.3 | SN1
51.3 | SN1
51 | SN1
50.9 | SN1
51.1 | SN1
51 | SN1
50.8 | SN1
50.6 | SN1
50.2 | SN1
50.2 | SN1
50.2 | SN1
50.7 | SN1
50.3 | SN1
50.2 | SN1
50.5 | SN1
50.1 | SN1
50.1 | SN1
50.3 | SN1
50.2 | SN1
50.1 | SN1
49.9 | SN1
50.2 | SN1
49.9 | SN1
50.2 | SN1
50.2 | SN1
50 | SN1
50.1 | SN1
49.9 | SN1
50 | SN1
50.1 | SN1
50.1 | SN1
50.4 | SN1
50.3 | SN1
50.5 | SN1
50.4 | SN1
50.6 | SN1
50.6 | SN1
51.1 | SN1
51.2 | SN1
51.5 | SN1
51.7 | SN1
51.8 | SN1
52 | SN1
52.8 | SN1
52.2 | SN1
52.7 | SN1
52.3 | SN1
52.2 | SN1
51.8 | SN1
54.6 | SN1
52 | SN1
51.3 | SN1
51 | SN1
51 | SN1
50.7 | SN1
50.1 | SN1
50.5 | SN1
50.4 | SN1
50.3 | SN1
50.6 | SN1
50.3 | SN1
50.2 | SN1
50.1 | SN1
50.2 | SN1
50.6 | SN1
50.3 | SN1
50.5 | SN1
50.5 | SN1
50.4 | SN1
50.2 | SN1
50.3 | SN1
50.4 | SN1
50.2 | SN1
50 | SN1
50 | SN1
49.9 | SN1
49.9 | SN1
49.4 | SN1
49.4 | SN1
49.8 | SN1
50.6 | SN1
50.8 | SN1
51.3 | SN1
51.6 | SN1
51.8 | SN1
51.6 | SN1
51.6 | SN1
51.9 | SN1
52.5 | SN1
52.7 | SN1
52.8 | SN1
52.6 | SN1
52.3 | SN1
52.8 | SN1
51.4 | SN1
51.8 | SN1
51.7 | SN1
51.3 | SN1
50.9 | SN1
50.5 | SN1
50.4 | SN1
50.3 | SN1
50.1 | SN1
50 | SN1
49.9 | SN1
49.8 | SN1
49.9 | SN1
50 | SN1
49.9 | SN1
50.3 | SN1
49.8 | SN1
50.2 | SN1
50 | SN1
49.8 | SN1
49.9 | SN1
49.7 | SN1
49.5 | SN1
49.4 | SN1
49 | SN1
49.5 | SN1
49.5 | SN1
49.4 | SN1
49.3 | SN1
49.3 | SN1
49.1 | SN1
49.3 | SN1
49.6 | SN1
50.3 | SN1
50.6 | SN1
50.7 | SN1
51.3 | SN1
51.7 | SN1
51.6 | SN1
52.3 | SN1
51.9 | SN1
52.3 | SN1
52.6 | SN1
52.7 | SN1
51.9 | SN1
51.8 | SN1
52.1 | SN1
51.6 | SN1
51.2 | SN1
51 | SN1
51 | SN1
50.6 | SN1
50.5 | SN1
50.3 | SN1
50.2 | SN1
50.3 | SN1
50.1 | SN1
50.2 | SN1
49.7 | SN1
50.1 | SN1
50 | SN1
50 | SN1
49.8 | SN1
49.7 | SN1
49.8 | SN1
49.7 | SN1
49.8 | SN1
49.6 | SN1
49.7 | SN1
49.5 | SN1
49.8 | SN1
49.7 | SN1
49.6 | SN1
49.4 | SN1
49.6 | SN1
49.5 | SN1
49.5 | SN1
49.4 | SN1
49.9 | SN1
50.2 | SN1
50.8 | SN1
51 | SN1
51 | SN1
51.3 | SN1
51.7 | SN1
51.4 | SN1
51.6 | SN1
51.8 | SN1
52.2 | SN1
51.3 | SN1
51.8 | SN1
52.2 | SN1
51.8 | SN1
51.7 | SN1
51.1 | SN1
51 | SN1
50.7 | SN1
50.1 | SN1
50 | SN1
50 | SN1
50.2 | SN1
49.7 | SN1
49.9 | SN1
50 | SN1
50 | SN1
49.8 | SN1
49.8 | SN1
50.3 | SN1
49.7 | SN1
50.3 | SN1
49.9 | SN1
50.1 | SN1
49.9 | SN1
50 | SN1
50.2 | SN1
49.7 | SN1
49.6 | SN1
49.6 | SN1
49.6 | SN1
49.6 | SN1
49.5 | SN1
49.8 | SN1
49.5 | SN1
50.2 | SN1
50.4 | SN1
50.2 | SN1
51.2 | SN1
50.8 | SN1
51.1 | SN1
51.4 | SN1
51.2 | SN1
51.4 | SN1
51.2 | SN1
50.9 | SN1
51 | SN1
52.4 | SN1
51.8 | SN1
52.2 | SN1
51.9 | SN1
51.6 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.4 | SN1
51 | SN1
50.7 | SN1
50.7 | SN1
50.4 | SN1
50.2 | SN1
50.2 | SN1
50.1 | SN1
50.3 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.5 | SN1
50.6 | SN1
50.1 | SN1
50.2 | SN1
50.4 | SN1
50.4 | SN1
50.7 | SN1
50.5 | SN1
50.1 | SN1
50.3 | SN1
50.1 | SN1
50.1 | SN1
50.1 | SN1
50.2 | SN1
50.4 | SN1
50.3 | SN1
50.1 | SN1
51.1 | SN1
51.6 | SN1
51.8 | SN1
52 | SN1
52 | SN1
51.9 | SN1
52 | SN1
52.5 | SN1
52.6 | SN1
52.8 | SN1
51.9 | SN1
53 | SN1
51.9 | SN1
51.3 | SN1
51 | SN1
50.8 | SN1
50.6 | SN1
50.3 | SN1
50.6 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.6 | SN1
50.4 | SN1
50.6 | SN1
50.5 | SN1
50.9 | SN1
50.7 | SN1
50.6 | SN1
50.8 | SN1
50.7 | SN1
51.1 | SN1
50.5 | SN1
50.3 | SN1
50.1 | SN1
49.9 | SN1
50.2 | SN1
50.1 | SN1
50.3 | SN1
50.3 | SN1
50.3 | SN1
50.7 | SN1
50.8 | SN1
50.6 | SN1
50.9 | SN1
51.9 | SN1
52.6 | SN1
51.5 | SN1
52 | SN1
51.7 | SN1
52 | SN1
52 | SN1
52.1 | SN1
51.6 | SN1
52 | SN1
51.9 | SN1
51.8 | SN1
51.4 | SN1
51.7 | SN1
51.3 | SN1
51.2 | SN1
51.2 | SN1
51 | SN1
50.8 | SN1
50.8 | SN1
50.4 | SN1
50.6 | SN1
50.5 | SN1
50.6 | SN1
50.5 | SN1
50.4 | SN1
50.6 | SN1
50.5 | SN1
50.2 | SN1
50.3 | SN1
50.3 | SN1
50.3 | SN1
50.2 | SN1
50.1 | SN1
49.8 | SN1
50 | SN1
49.9 | SN1
50.2 | SN1
50.3 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.3 | SN1
50.6 | SN1
51.5 | SN1
50.8 | SN1
51.6 | SN1
51.4 | SN1
50.7 | SN1
52.3 | SN1
52.2 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
51.5 | SN1
51.4 | SN1
51.5 | SN1
51.2 | SN1
50.9 | SN1
50.8 | SN1
51 | SN1
50.7 | SN1
50.5 | SN1
50.5 | SN1
50.5 | SN1
50.3 | SN1
50.5 | SN1
50.2 | SN1
50.3 | SN1
50.8 | SN1
50.6 | SN1
50.6 | SN1
50.5 | SN1
50.4 | SN1
50.8 | SN1
50.3 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.4 | SN1
50.2 | SN1
50.1 | SN1
50.2 | SN1
50.4 | SN1
50.3 | SN1
50.5 | SN1
50.8 | SN1
50.6 | SN1
50.8 | SN1
51.5 | SN1
52.4 | SN1
51.5 | SN1
52.3 | SN1
52.2 | SN1
52.6 | SN1
51.6 | SN1
52.5 | SN1
52.3 | SN1
52.2 | SN1
51.6 | SN1
51.4 | SN1
51.7 | SN1
51.7 | SN1
51.1 | SN1
51.4 | SN1
50.8 | SN1
50.5 | SN1
50.5 | SN1
50.7 | SN1
50.2 | SN1
50.2 | SN1
50.2 | SN1
50.2 | SN1
50.5 | SN1
50 | SN1
49.9 | SN1
50.1 | SN1
50 | SN1
50.2 | SN1
50.3 | SN1
50.4 | SN1
50 | SN1
50 | SN1
50.2 | SN1
49.8 | SN1
50.1 | SN1
50.3 | SN1
50.1 | SN1
49.9 | SN1
49.4 | SN1
49.5 | SN1
49.4 | SN1
49.5 | SN1
49.4 | SN1
49.6 | SN1
49.8 | SN1
49.8 | SN1
50.1 | SN1
50.6 | SN1
50.4 | SN1
50.2 | SN1
49.9 | SN1
50.3 | SN1
50.5 | SN1
49.9 | SN1
50.3 | SN1
50.3 | SN1
50 | SN1
49.9 | SN1
49.8 | SN1
49.7 | SN1
49.3 | SN1
49.3 | SN1
49.2 | SN1
49.6 | SN1
49.4 | SN1
49.5 | SN1
49.3 | SN1
49.6 | SN1
49.6 | SN1
49.2 | SN1
49.3 | SN1
49.3 | SN1
49.3 | SN1
49.1 | SN1
49.2 | SN1
49.2 | SN1
49 | SN1
49.1 | SN1
49.2 | SN1
49 | SN1
48.6 | SN1
49.1 | SN1
49.1 | SN1
48.9 | SN1
48.6 | SN1
49 | SN1
49.4 | SN1
49.5 | SN1
49.5 | SN1
49.7 | SN1
49.4 | SN1
49.4 | SN1
50.1 | SN1
50.3 | SN1
50 | SN1
50.1 | SN1
49.9 | SN1
49.8 | SN1
49.7 | SN1
49.7 | SN1
49.8 | SN1
49.4 | SN1
49.1 | SN1
48.9 | SN1
52.4 | SN1
53.4 | SN1
54 | SN1
54.4 | SN1
54.1 | SN1
54.7 | SN1
54.8 | SN1
54.8 | SN1
54.8 | SN1
54.8 | SN1
54.8 | SN1
54.7 | SN1
54.9 | SN1
55.1 | SN1
54.9 | SN1
54.5 | SN1
54.8 | SN1
54.6 | SN1
54.4 | SN1
54.3 | SN1
54.5 | SN1
54.3 | SN1
54.2 | SN1
54.3 | SN1
54.1 | SN1
54.3 | SN1
54.4 | SN1
54.1 | SN1
54.6 | SN1
55.2 | SN1
54.6 | SN1
55.1 | SN1
54.5 | SN1
54.8 | SN1
55.1 | SN1
54.3 | SN1
54.3 | SN1
54 | SN1
53.6 | SN1
53.6 | SN1
53.5 | SN1
53.3 | SN1
53.3 | SN1
52.6 | SN1
52.4 | SN1
52 | SN1
51.9 | SN1
51.6 | SN1
51.5 | SN1
51.3 | SN1
51.2 | SN1
51.9 | SN1
52.1 | SN1
52.6 | SN1
53.1 | SN1
53.4 | SN1
53.7 | SN1
53.9 | SN1
54.5 | SN1
54.6 | SN1
54.5 | SN1
54.3 | SN1
54.3 | SN1
54.3 | SN1
54.4 | SN1
53.9 | SN1
53.9 | SN1
54 | SN1
53.7 | SN1
53.9 | SN1
54 | SN1
53.8 | SN1
53.8 | SN1
54.4 | SN1
53.9 | SN1
54.1 | SN1
53.7 | SN1
53.5 | SN1
53.7 | SN1
54 | SN1
53.9 | SN1
53.7 | SN1
53.6 | SN1
53.6 | SN1
52.8 | SN1
52.8 | SN1
53.6 | SN1
53.2 | SN1
52.6 | SN1
52.1 | SN1
52.4 | SN1
52.5 | SN1
52.2 | SN1
52.3 | SN1
51.9 | SN1
51.4 | SN1
51.5 | SN1
51.1 | SN1
51.6 | SN1
51.6 | SN1
51.4 | SN1
51.4 | SN1
51.3 | SN1
51.3 | SN1
51.3 | SN1
51.4 | SN1
51.4 | SN1
50.7 | SN1
50.8 | SN1
50.9 | SN1
50.8 | SN1
50.7 | SN1
51 | SN1
50.5 | SN1
50.4 | SN1
50.5 | SN1
50.2 | SN1
50.5 | SN1
50.4 | SN1
50.4 | SN1
50.6 | SN1
51.1 | SN1
51.8 | SN1
51.1 | SN1
51.5 | SN1
51.3 | SN1
51.8 | SN1
51.7 | SN1
51.9 | SN1
52.3 | SN1
53.4 | SN1
54 | SN1
53.5 | SN1
52.8 | SN1
52.9 | SN1
52.6 | SN1
52.6 | SN1
52.4 | SN1
51.6 | SN1
50.9 | SN1
51.1 | SN1
50.7 | SN1
50.2 | SN1
49.8 | SN1
50.1 | SN1
49.9 | SN1
50 | SN1
49.8 | SN1
49.9 | SN1
49.7 | SN1
50 | SN1
50.1 | SN1
50 | SN1
49.6 | SN1
49.6 | SN1
49.7 | SN1
49.6 | SN1
49.6 | SN1
49.9 | SN1
49.9 | SN1
49.4 | SN1
49.6 | SN1
49.4 | SN1
49.9 | SN1
49.6 | SN1
49.6 | SN1
49.7 | SN1
50 | SN1
50 | SN1
49.9 | SN1
50.5 | SN1
51.3 | SN1
52.5 | SN1
52.3 | SN1
52.3 | SN1
52.5 | SN1
52.1 | SN1
52.3 | SN1
52.5 | SN1
51.9 | SN1
52.1 | SN1
51.7 | SN1
52.1 | SN1
52.2 | SN1
51.7 | SN1
51.1 | SN1
51.2 | SN1
50.4 | SN1
49.9 | SN1
49.8 | SN1
49.9 | SN1
50 | SN1
49.5 | SN1
49.9 | SN1
50.1 | SN1
49.6 | SN1
49.6 | SN1
49.5 | SN1
49.7 | SN1
49.4 | SN1
49.4 | SN1
49.2 | SN1
49.3 | SN1
49.3 | SN1
49.4 | SN1
49.2 | SN1
49.1 | SN1
49 | SN1
49.2 | SN1
49.1 | SN1
49 | SN1
49.5 | SN1
49.4 | SN1
49.5 | SN1
49.9 | SN1
50.4 | SN1
2.5 | SN1
4.3 | SN1
7.4 | SN1
59.2 | SN1
55 | SN1
53.9 | SN1
52.9 | SN1
52.5 | SN1
52.3 | SN1
52.1 | SN1
52 | SN1
50.5 | SN1
50.1 | SN1
49.8 | SN1
49.6 | SN1
53.2 | SN1
53.2 | SN1
53.3 | SN1
53.3 | SN1
53.2 | SN1
52.5 | SN1
51.9 | SN1
51.6 | SN1
51.8 | SN1
51.5 | SN1
51.5 | SN1
51.4 | SN1
51.8 | SN1
51.6 | SN1
51.7 | SN1
51.9 | SN1
51.7 | SN1
52.2 | SN1
52.5 | SN1
53.1 | SN1
53.8 | SN1
54.7 | SN1
54.5 | SN1
55 | SN1
54.8 | SN1
54.7 | SN1
54.9 | SN1
54.6 | SN1
54.2 | SN1
54.2 | SN1
54.2 | SN1
54.1 | SN1
53.9 | SN1
53.7 | SN1
53.7 | SN1
53.5 | SN1
53.3 | SN1
53.5 | SN1
53.6 | SN1
53.5 | SN1
53 | SN1
53.3 | SN1
53.2 | SN1
53.3 | SN1
53.4 | SN1
53 | SN1
53.2 | SN1
53 | SN1
53.4 | SN1
53.1 | SN1
52.7 | SN1
52.4 | SN1
52.6 | SN1
52.6 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.4 | SN1
52.5 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
51.9 | SN1
52.7 | SN1
53.6 | SN1
53.9 | SN1
54.6 | SN1
55 | SN1
54.9 | SN1
55.1 | SN1
55.2 | SN1
55 | SN1
55.1 | SN1
54.8 | SN1
54.7 | SN1
54.7 | SN1
54.1 | SN1
53.7 | SN1
54 | SN1
54 | SN1
53.7 | SN1
53.7 | SN1
53.9 | SN1
53.6 | SN1
53.5 | SN1
53.8 | SN1
53.4 | SN1
53.3 | SN1
53.2 | SN1
53.5 | SN1
53.7 | SN1
53.5 | SN1
53.3 | SN1
53.3 | SN1
52.9 | SN1
52.6 | SN1
52.7 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.2 | SN1
52.6 | SN1
52.6 | SN1
52.4 | SN1
52.3 | SN1
52.1 | SN1
51.7 | SN1
52.4 | SN1
52.5 | SN1
53.2 | SN1
53.5 | SN1
54.3 | SN1
54.7 | SN1
55 | SN1
55 | SN1
55.1 | SN1
55 | SN1
55.2 | SN1
54.8 | SN1
54.8 | SN1
54.8 | SN1
55 | SN1
55 | SN1
54.8 | SN1
54.5 | SN1
54.7 | SN1
54.6 | SN1
54.2 | SN1
54.2 | SN1
53.7 | SN1
53.4 | SN1
53.3 | SN1
53.4 | SN1
53.2 | SN1
53.2 | SN1
53 | SN1
53 | SN1
53.3 | SN1
53.4 | SN1
53.3 | SN1
53.1 | SN1
53 | SN1
53 | SN1
52.9 | SN1
52.9 | SN1
53.1 | SN1
52.8 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
52 | SN1
52.2 | SN1
52.6 | SN1
52.7 | SN1
53 | SN1
53.8 | SN1
54.2 | SN1
54.4 | SN1
54.6 | SN1
54.4 | SN1
54.5 | SN1
54.4 | SN1
54.4 | SN1
54.4 | SN1
54.6 | SN1
54.7 | SN1
54.7 | SN1
54.7 | SN1
54.7 | SN1
54.9 | SN1
54.7 | SN1
54.6 | SN1
54.8 | SN1
54.3 | SN1
54.5 | SN1
54 | SN1
54.3 | SN1
54.2 | SN1
53.8 | SN1
53.6 | SN1
53.5 | SN1
53.4 | SN1
52.6 | SN1
53.6 | SN1
53.5 | SN1
53.2 | SN1
53.1 | SN1
52.3 | SN1
51.6 | SN1
51.6 | SN1
51.9 | SN1
52.1 | SN1
52.3 | SN1
52.5 | SN1
51.9 | SN1
52.2 | SN1
52.3 | SN1
52.3 | SN1
52.2 | SN1
52.5 | SN1
52.4 | SN1
52.9 | SN1
53.1 | SN1
53.8 | SN1
53.9 | SN1
54 | SN1
54 | SN1
54.2 | SN1
54 | SN1
53.9 | SN1
53.7 | SN1
53.8 | SN1
53.6 | SN1
53.8 | SN1
53.4 | SN1
53.4 | SN1
53.2 | SN1
53.3 | SN1
53.1 | SN1
53.2 | SN1
53 | SN1
53 | SN1
53.3 | SN1
53.2 | SN1
53 | SN1
52.9 | SN1
52.9 | SN1
52.7 | SN1
52.3 | SN1
52.8 | SN1
52.7 | SN1
52.4 | SN1
52.5 | SN1
52.4 | SN1
52.3 | SN1
52.6 | SN1
52.4 | SN1
52.5 | SN1
52.7 | SN1
52.6 | SN1
52.4 | SN1
52.3 | SN1
52.6 | SN1
52.4 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.7 | SN1
52.8 | SN1
53 | SN1
53 | SN1
53 | SN1
53.2 | SN1
53.3 | SN1
53.1 | SN1
52.6 | SN1
53.4 | SN1
53.3 | SN1
53.3 | SN1
53.5 | SN1
53.3 | SN1
53.6 | SN1
53.4 | SN1
53.5 | SN1
53.4 | SN1
53.5 | SN1
53.1 | SN1
53 | SN1
53.1 | SN1
53.1 | SN1
52.7 | SN1
52.9 | SN1
53.2 | SN1
53 | SN1
52.7 | SN1
52.7 | SN1
53.3 | SN1
53 | SN1
53.1 | SN1
53 | SN1
52.9 | SN1
52.8 | SN1
52.8 | SN1
52 | SN1
51.8 | SN1
51.9 | SN1
51.5 | SN1
51.6 | SN1
51.7 | SN1
51.7 | SN1
51.9 | SN1
52.3 | SN1
52.8 | SN1
53.2 | SN1
53.8 | SN1
53.7 | SN1
54.1 | SN1
53.8 | SN1
53.9 | SN1
53.8 | SN1
53.8 | SN1
53.8 | SN1
53.5 | SN1
53.1 | SN1
53 | SN1
52.9 | SN1
53.1 | SN1
53 | SN1
53.2 | SN1
53 | SN1
53.3 | SN1
53.1 | SN1
52.9 | SN1
52.9 | SN1
52.6 | SN1
52.4 | SN1
52.6 | SN1
52.1 | SN1
52.4 | SN1
52.1 | SN1
52.6 | SN1
52.5 | SN1
53.2 | SN1
52.7 | SN1
52.2 | SN1
52.5 | SN1
52.4 | SN1
52.2 | SN1
52.5 | SN1
52.3 | SN1
52.4 | SN1
52.2 | SN1
52.3 | SN1
52 | SN1
52 | SN1
51.6 | SN1
51.6 | SN1
51.6 | SN1
52 | SN1
52.7 | SN1
52.9 | SN1
53.1 | SN1
53.3 | SN1
53.4 | SN1
53.5 | SN1
53.5 | SN1
52.9 | SN1
52.7 | SN1
52.8 | SN1
53.1 | SN1
53.2 | SN1
53 | SN1
53.2 | SN1
53.1 | SN1
53 | SN1
52.9 | SN1
52.8 | SN1
52.6 | SN1
52.7 | SN1
52.6 | SN1
52.5 | SN1
52.9 | SN1
52.6 | SN1
52.4 | SN1
52.7 | SN1
53 | SN1
52.8 | SN1
52.8 | SN1
52.9 | SN1
52.7 | SN1
52.5 | SN1
52.3 | SN1
52.2 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
52.4 | SN1
52.4 | SN1
52 | SN1
51.8 | SN1
51.7 | SN1
51.7 | SN1
52.6 | SN1
52.9 | SN1
52.7 | SN1
53 | SN1
53.2 | SN1
53.3 | SN1
53.4 | SN1
53.2 | SN1
53.2 | SN1
53.2 | SN1
53.3 | SN1
53.2 | SN1
53.3 | SN1
53.2 | SN1
53.1 | SN1
53.3 | SN1
53.1 | SN1
53.3 | SN1
53.1 | SN1
52.8 | SN1
53.3 | SN1
52.8 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
52.9 | SN1
52.9 | SN1
52.5 | SN1
52.5 | SN1
52.3 | SN1
52.3 | SN1
52.2 | SN1
51.8 | SN1
51.6 | SN1
51.7 | SN1
51.8 | SN1
51.4 | SN1
51.5 | SN1
51.6 | SN1
51.5 | SN1
51.8 | SN1
52.3 | SN1
51.6 | SN1
51.8 | SN1
51.8 | SN1
52.3 | SN1
52.5 | SN1
53 | SN1
52.9 | SN1
53 | SN1
53.1 | SN1
53.4 | SN1
53.1 | SN1
53.2 | SN1
53.4 | SN1
53.2 | SN1
53.1 | SN1
53.4 | SN1
53.4 | SN1
53.2 | SN1
53.1 | SN1
53.2 | SN1
53.2 | SN1
53.1 | SN1
52.7 | SN1
52.8 | SN1
52.5 | SN1
52.5 | SN1
52.3 | SN1
51.9 | SN1
52 | SN1
52.1 | SN1
52 | SN1
52.1 | SN1
51.9 | SN1
52.3 | SN1
52.7 | SN1
52.5 | SN1
52.3 | SN1
52 | SN1
52 | SN1
52.2 | SN1
51.9 | SN1
52 | SN1
51.9 | SN1
52.2 | SN1
52.4 | SN1
52 | SN1
52 | SN1
51.6 | SN1
51.7 | SN1
51.8 | SN1
51.9 | SN1
52 | SN1
52.2 | SN1
52.2 | SN1
52.4 | SN1
52.5 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.5 | SN1
52.3 | SN1
52.5 | SN1
52.4 | SN1
52.4 | SN1
52.2 | SN1
52.1 | SN1
52.2 | SN1
52.2 | SN1
51.8 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
52 | SN1
52.2 | SN1
52.4 | SN1
52.6 | SN1
52.4 | SN1
52.2 | SN1
52.3 | SN1
52.6 | SN1
52.5 | SN1
52.1 | SN1
52.3 | SN1
52.1 | SN1
52.1 | SN1
52.3 | SN1
52.1 | SN1
52.3 | SN1
52.2 | SN1
52.1 | SN1
51.8 | SN1
51.5 | SN1
51.8 | SN1
51.9 | SN1
52 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
52.1 | SN1
52.3 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
52.3 | SN1
52.2 | SN1
52.1 | SN1
51.9 | SN1
52 | SN1
52.1 | SN1
52 | SN1
51.8 | SN1
52 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
52.1 | SN1
52.3 | SN1
52.7 | SN1
52.6 | SN1
52.6 | SN1
52.7 | SN1
52.8 | SN1
53 | SN1
52.6 | SN1
52.3 | SN1
52.1 | SN1
52 | SN1
52 | SN1
52 | SN1
52.1 | SN1
52.4 | SN1
52.1 | SN1
51.5 | SN1
51.7 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
52.4 | SN1
52.5 | SN1
52.4 | SN1
52.2 | SN1
51.9 | SN1
52.5 | SN1
52.3 | SN1
52.2 | SN1
52.2 | SN1
52.3 | SN1
52.6 | SN1
52.6 | SN1
52.3 | SN1
52.4 | SN1
51.9 | SN1
52.2 | SN1
52.5 | SN1
52.3 | SN1
52.2 | SN1
52.1 | SN1
51.7 | SN1
51.9 | SN1
51.6 | SN1
51.7 | SN1
51.7 | SN1
51.7 | SN1
51.5 | SN1
51.7 | SN1
51.8 | SN1
51.7 | SN1
51.9 | SN1
51.7 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
52.3 | SN1
52 | SN1
52.2 | SN1
52.2 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
52.4 | SN1
52.5 | SN1
52.4 | SN1
52.7 | SN1
52.5 | SN1
52.5 | SN1
52.7 | SN1
52.3 | SN1
52.6 | SN1
52.7 | SN1
52.8 | SN1
52.4 | SN1
52.5 | SN1
52.2 | SN1
52.4 | SN1
52.2 | SN1
52.4 | SN1
52.5 | SN1
52.1 | SN1
52.4 | SN1
52.4 | SN1
51.9 | SN1
52 | SN1
51.9 | SN1
52.3 | SN1
51.6 | SN1
52 | SN1
51.4 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
52.3 | SN1
52.4 | SN1
52.2 | SN1
52.2 | SN1
52.2 | SN1
52.2 | SN1
52.4 | SN1
52.5 | SN1
52.3 | SN1
52.2 | SN1
52.8 | SN1
52.7 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.4 | SN1
52.4 | SN1
52.7 | SN1
52.6 | SN1
52.5 | SN1
53 | SN1
52.5 | SN1
52.2 | SN1
52.3 | SN1
52.2 | SN1
52.9 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.6 | SN1
52.5 | SN1
52.4 | SN1
51.8 | SN1
51.7 | SN1
51.5 | SN1
51.4 | SN1
51.4 | SN1
51.8 | SN1
51.5 | SN1
51.7 | SN1
51.9 | SN1
51.4 | SN1
51.9 | SN1
51.9 | SN1
51.9 | SN1
51.7 | SN1
51.5 | SN1
51.5 | SN1
51.7 | SN1
51.7 | SN1
52.2 | SN1
52.3 | SN1
52.4 | SN1
52.6 | SN1
52.9 | SN1
52.8 | SN1
52.6 | SN1
52.9 | SN1
52.9 | SN1
52.8 | SN1
52.4 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.6 | SN1
52.4 | SN1
52.5 | SN1
52.6 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
53 | SN1
52.6 | SN1
52.4 | SN1
52.6 | SN1
52.3 | SN1
52.5 | SN1
52.3 | SN1
52 | SN1
51.8 | SN1
51.3 | SN1
51.5 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.7 | SN1
51.7 | SN1
51.5 | SN1
51.6 | SN1
51.4 | SN1
51.6 | SN1
51.6 | SN1
51.7 | SN1
51.6 | SN1
51.8 | SN1
52.2 | SN1
52.5 | SN1
52.9 | SN1
52.8 | SN1
52.9 | SN1
52.8 | SN1
52.8 | SN1
52.6 | SN1
53.2 | SN1
52.9 | SN1
52.8 | SN1
52.9 | SN1
52.7 | SN1
52.8 | SN1
52.7 | SN1
52.3 | SN1
52.6 | SN1
52.7 | SN1
52.6 | SN1
52.3 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.4 | SN1
52.2 | SN1
52.4 | SN1
52.1 | SN1
52.2 | SN1
51.7 | SN1
51.3 | SN1
51.2 | SN1
51.3 | SN1
51.3 | SN1
51.1 | SN1
51.3 | SN1
51.7 | SN1
51.3 | SN1
51.7 | SN1
51.5 | SN1
51.7 | SN1
51.5 | SN1
51.5 | SN1
51.4 | SN1
51.5 | SN1
51.5 | SN1
51.5 | SN1
52.3 | SN1
52.2 | SN1
52.5 | SN1
52.6 | SN1
52.9 | SN1
52.7 | SN1
52.9 | SN1
52.7 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.7 | SN1
52.8 | SN1
52.9 | SN1
52.9 | SN1
52.4 | SN1
52.7 | SN1
52.7 | SN1
52.5 | SN1
52.4 | SN1
52.9 | SN1
52.5 | SN1
52.5 | SN1
52.3 | SN1
52.2 | SN1
52.1 | SN1
52.1 | SN1
51.3 | SN1
51.6 | SN1
51.6 | SN1
51.5 | SN1
51.6 | SN1
51.4 | SN1
51.8 | SN1
51.8 | SN1
51.5 | SN1
52 | SN1
51.9 | SN1
51.8 | SN1
51.9 | SN1
51.7 | SN1
51.9 | SN1
51.6 | SN1
52 | SN1
51.7 | SN1
52.5 | SN1
52.7 | SN1
52.9 | SN1
52.7 | SN1
53.2 | SN1
53 | SN1
52.8 | SN1
52.7 | SN1
52.8 | SN1
52.7 | SN1
52.8 | SN1
52.8 | SN1
52.9 | SN1
52.4 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
52.6 | SN1
52.3 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
52.3 | SN1
52 | SN1
51.9 | SN1
52 | SN1
51.4 | SN1
51.7 | SN1
51.2 | SN1
51.2 | SN1
51.2 | SN1
51.9 | SN1
51.4 | SN1
51.7 | SN1
51.7 | SN1
51.7 | SN1
52 | SN1
51.5 | SN1
51.8 | SN1
51.7 | SN1
51.9 | SN1
52.3 | SN1
52 | SN1
52.1 | SN1
52.2 | SN1
52.8 | SN1
52.6 | SN1
52.9 | SN1
52.5 | SN1
52.5 | SN1
52.5 | SN1
52.4 | SN1
52.6 | SN1
52.4 | SN1
52.3 | SN1
52.3 | SN1
52.3 | SN1
52.6 | SN1
52.2 | SN1
52.4 | SN1
52.5 | SN1
52.3 | SN1
52.5 | SN1
52.3 | SN1
52.4 | SN1
52.2 | SN1
52.6 | SN1
52.4 | SN1
52.3 | SN1
52 | SN1
52 | SN1
51.9 | SN1
51.5 | SN1
51.2 | SN1
51.8 | SN1
51.8 | SN1
51.2 | SN1
51.9 | SN1
51.8 | SN1
51.3 | SN1
52.1 | SN1
51.8 | SN1
51.5 | SN1
51.9 | SN1
51.6 | SN1
51.6 | SN1
51.9 | SN1
51.9 | SN1
52.3 | SN1
52.8 | SN1
52.7 | SN1
52.7 | SN1
52.5 | SN1
52.7 | SN1
52.9 | SN1
52.7 | SN1
52.8 | SN1
52.6 | SN1
52.6 | SN1
52.8 | SN1
52.7 | SN1
52.9 | SN1
52.9 | SN1
52.7 | SN1
52.9 | SN1
52.9 | SN1
52.8 | SN1
52.9 | SN1
52.9 | SN1
52.9 | SN1
52.8 | SN1
52.5 | SN1
52.1 | SN1
52.4 | SN1
52.1 | SN1
52.2 | SN1
51.9 | SN1
52.3 | SN1
51.8 | SN1
52.1 | SN1
51.4 | SN1
51.3 | SN1
51.8 | SN1
51.9 | SN1
51.7 | SN1
51.9 | SN1
52 | SN1
51.6 | SN1
52 | SN1
51.9 | SN1
51.6 | SN1
51.5 | SN1
51.9 | SN1
51.6 | SN1
52 | SN1
52.4 | SN1
52.5 | SN1
52.8 | SN1
53 | SN1
52.9 | SN1
52.8 | SN1
52.8 | SN1
53 | SN1
53.1 | SN1
53 | SN1
52.9 | SN1
53 | SN1
52.8 | SN1
53 | SN1
53 | SN1
52.7 | SN1
53 | SN1
52.6 | SN1
52.8 | SN1
52.6 | SN1
52.7 | SN1
52.6 | SN1
52.8 | SN1
52.3 | SN1
52.8 | SN1
52.7 | SN1
52.3 | SN1
52.4 | SN1
52.1 | SN1
51.5 | SN1
51.6 | SN1
51.6 | SN1
51.4 | SN1
51.7 | SN1
51.3 | SN1
51.5 | SN1
52 | SN1
51.7 | SN1
51.5 | SN1
51.8 | SN1
51.8 | SN1
51.6 | SN1
51.6 | SN1
52 | SN1
51.7 | SN1
52.1 | SN1
52.3 | SN1
52.3 | SN1
52.6 | SN1
52.9 | SN1
53.1 | SN1
52.9 | SN1
52.8 | SN1
53 | SN1
53.2 | SN1
52.6 | SN1
52.9 | SN1
52.9 | SN1
52.8 | SN1
52.7 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
52.8 | SN1
52.7 | SN1
53.1 | SN1
53 | SN1
52.8 | SN1
52.8 | SN1
52.6 | SN1
52.6 | SN1
52.2 | SN1
51.9 | SN1
52 | SN1
51.4 | SN1
51.2 | SN1
51.3 | SN1
51.3 | SN1
52 | SN1
51.4 | SN1
51.7 | SN1
51.7 | SN1
51.9 | SN1
51.8 | SN1
51.6 | SN1
51.5 | SN1
52 | SN1
51.5 | SN1
51.5 | SN1
51.9 | SN1
51.7 | SN1
52.3 | SN1
52.4 | SN1
52.6 | SN1
52.2 | SN1
52.7 | SN1
52.7 | SN1
52.7 | SN1
52.3 | SN1
51.9 | SN1
51.4 | SN1
51.4 | SN1
51.6 | SN1
52 | SN1
51.6 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
52.1 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.7 | SN1
51.6 | SN1
51.7 | SN1
52 | SN1
52.1 | SN1
52.6 | SN1
52.2 | SN1
52.5 | SN1
53 | SN1
52.7 | SN1
52.7 | SN1
52.5 | SN1
52.8 | SN1
52.5 | SN1
52.3 | SN1
52.5 | SN1
52 | SN1
51.7 | SN1
51.5 | SN1
51.6 | SN1
51.5 | SN1
51.7 | SN1
51.9 | SN1
51.8 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.5 | SN1
51.6 | SN1
51.8 | SN1
51.9 | SN1
52.2 | SN1
52.1 | SN1
52.1 | SN1
52.5 | SN1
52.4 | SN1
52.7 | SN1
52.8 | SN1
52.4 | SN1
52.6 | SN1
52.9 | SN1
52.6 | SN1
52.6 | SN1
52.6 | SN1
52.8 | SN1
52.6 | SN1
52.8 | SN1
52.9 | SN1
53 | SN1
53.1 | SN1
52.7 | SN1
52.8 | SN1
52.3 | SN1
52.8 | SN1
53 | SN1
53 | SN1
52.8 | SN1
52.6 | SN1
52.8 | SN1
52.7 | SN1
52.8 | SN1
52.7 | SN1
52.2 | SN1
52 | SN1
51.5 | SN1
51.5 | SN1
51.6 | SN1
51.6 | SN1
51.8 | SN1
51.6 | SN1
51.8 | SN1
51.9 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
51.7 | SN1
51.8 | SN1
52.5 | SN1
52.5 | SN1
52.6 | SN1
52.6 | SN1
52.9 | SN1
52.9 | SN1
53.2 | SN1
52.9 | SN1
52.5 | SN1
53 | SN1
53 | SN1
53 | SN1
52.9 | SN1
52.9 | SN1
53.3 | SN1
53 | SN1
52.8 | SN1
52.8 | SN1
52.7 | SN1
52.8 | SN1
52.6 | SN1
52.8 | SN1
52.7 | SN1
52.8 | SN1
52.6 | SN1
52.8 | SN1
53 | SN1
52.6 | SN1
52.6 | SN1
52.7 | SN1
52.3 | SN1
52.1 | SN1
52 | SN1
52 | SN1
51.3 | SN1
51.5 | SN1
51.7 | SN1
51.3 | SN1
51.8 | SN1
51.8 | SN1
52 | SN1
51.7 | SN1
51.9 | SN1
51.9 | SN1
51.8 | SN1
52.2 | SN1
52.4 | SN1
53.4 | SN1
53.9 | SN1
54 | SN1
53.7 | SN1
54.1 | SN1
54.3 | SN1
54.2 | SN1
54 | SN1
54 | SN1
53.9 | SN1
53.9 | SN1
54.2 | SN1
53.9 | SN1
53.6 | SN1
53 | SN1
53.2 | SN1
52.7 | SN1
53 | SN1
53.2 | SN1
53.3 | SN1
53.3 | SN1
53.1 | SN1
53.5 | SN1
53.1 | SN1
53 | SN1
53.1 | SN1
52.8 | SN1
52.7 | SN1
52.5 | SN1
52.3 | SN1
51.9 | SN1
51.8 | SN1
51.8 | SN1
51.6 | SN1
51.7 | SN1
51.8 | SN1
51.8 | SN1
51.8 | SN1
51.9 | SN1
51.9 | SN1
51.7 | SN1
51.7 | SN1
52.2 | SN1
52.1 | SN1
52.1 | SN1
52.6 | SN1
52.7 | SN1
52.7 | SN1
52.9 | SN1
52.4 | SN1
52.8 | SN1
53 | SN1
53.1 | SN1
53.1 | SN1
53 | SN1
52.9 | SN1
53 | SN1
53 | SN1
52.9 | SN1
53.1 | SN1
53.4 | SN1
53.4 | SN1
53.5 | SN1
53.4 | SN1
53.1 | SN1
53.3 | SN1
53.5 | SN1
53 | SN1
53.4 | SN1
53.1 | SN1
53.3 | SN1
53.3 | SN1
53.2 | SN1
53.2 | SN1
52.9 | SN1
52.7 | SN1
52.3 | SN1
52.2 | SN1
52 | SN1
51.8 | SN1
52.1 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
51.9 | SN1
52 | SN1
52.2 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
52.2 | SN1
52 | SN1
52.4 | SN1
52.7 | SN1
52.6 | SN1
52.9 | SN1
53.1 | SN1
53.1 | SN1
53.1 | SN1
52.7 | SN1
52.9 | SN1
52.9 | SN1
53.2 | SN1
52.8 | SN1
53.1 | SN1
53 | SN1
53 | SN1
53 | SN1
53.3 | SN1
52.7 | SN1
53.1 | SN1
53 | SN1
53.3 | SN1
53 | SN1
53.5 | SN1
53.2 | SN1
53.1 | SN1
53.2 | SN1
53.3 | SN1
53 | SN1
53.1 | SN1
53 | SN1
52.6 | SN1
52.2 | SN1
52.1 | SN1
51.7 | SN1
52 | SN1
51.8 | SN1
52.3 | SN1
52.3 | SN1
52.1 | SN1
52.1 | SN1
52.2 | SN1
46.7 | SN2
47 | SN2
47 | SN2
46.9 | SN2
46.8 | SN2
47 | SN2
47.1 | SN2
46.8 | SN2
46.6 | SN2
46.3 | SN2
46.3 | SN2
46.3 | SN2
46.5 | SN2
46.5 | SN2
46.4 | SN2
46.5 | SN2
46.1 | SN2
46.6 | SN2
46.6 | SN2
47.1 | SN2
47 | SN2
47.1 | SN2
47.4 | SN2
48 | SN2
48.7 | SN2
49.3 | SN2
49 | SN2
49.1 | SN2
48.8 | SN2
49.2 | SN2
49.3 | SN2
48.6 | SN2
48.5 | SN2
47.9 | SN2
47.7 | SN2
48 | SN2
47.3 | SN2
46.8 | SN2
46.5 | SN2
46.6 | SN2
46.5 | SN2
46.4 | SN2
46.3 | SN2
46.6 | SN2
46.3 | SN2
46.1 | SN2
46.2 | SN2
46.1 | SN2
45.8 | SN2
46 | SN2
46.2 | SN2
46.1 | SN2
46 | SN2
45.9 | SN2
45.5 | SN2
46.1 | SN2
45.4 | SN2
45.4 | SN2
45.5 | SN2
45 | SN2
45.5 | SN2
45 | SN2
45.1 | SN2
45.4 | SN2
45.2 | SN2
45.4 | SN2
45.3 | SN2
45.9 | SN2
46 | SN2
46.4 | SN2
46.8 | SN2
47.3 | SN2
47.7 | SN2
48.9 | SN2
48.7 | SN2
48.8 | SN2
48.9 | SN2
48.7 | SN2
48.7 | SN2
48.7 | SN2
48.7 | SN2
48.3 | SN2
47.4 | SN2
56.1 | SN2
49.8 | SN2
48.3 | SN2
48 | SN2
47.9 | SN2
48.1 | SN2
47.6 | SN2
47.9 | SN2
47.6 | SN2
47.6 | SN2
47.7 | SN2
47.3 | SN2
47.5 | SN2
47.3 | SN2
47.2 | SN2
47.2 | SN2
46.8 | SN2
47 | SN2
46.9 | SN2
47 | SN2
46.6 | SN2
46.6 | SN2
46.6 | SN2
46.3 | SN2
46.5 | SN2
46.6 | SN2
46.3 | SN2
46.1 | SN2
46.6 | SN2
46.3 | SN2
47.1 | SN2
47.1 | SN2
47.3 | SN2
48.1 | SN2
49.1 | SN2
49.7 | SN2
49.8 | SN2
49.5 | SN2
49.5 | SN2
49.5 | SN2
49.3 | SN2
49 | SN2
48.8 | SN2
48.4 | SN2
48.1 | SN2
48.3 | SN2
48.2 | SN2
48.2 | SN2
47.6 | SN2
47.5 | SN2
47.3 | SN2
47.1 | SN2
47.5 | SN2
47.4 | SN2
47.2 | SN2
47.4 | SN2
47.4 | SN2
47.2 | SN2
47.1 | SN2
47.1 | SN2
47.2 | SN2
46.9 | SN2
47.4 | SN2
47.1 | SN2
46.8 | SN2
46.8 | SN2
46.9 | SN2
46.8 | SN2
46.8 | SN2
46.8 | SN2
46.8 | SN2
46.8 | SN2
46.7 | SN2
46.8 | SN2
46.4 | SN2
46.5 | SN2
47.1 | SN2
47.1 | SN2
47.2 | SN2
47.2 | SN2
47.6 | SN2
48.3 | SN2
49 | SN2
49.5 | SN2
49.3 | SN2
49 | SN2
49.1 | SN2
49 | SN2
49.6 | SN2
48.6 | SN2
48.9 | SN2
48.8 | SN2
48.1 | SN2
47.5 | SN2
47.1 | SN2
47 | SN2
47 | SN2
47.5 | SN2
47.1 | SN2
47 | SN2
49.7 | SN2
49.6 | SN2
49.8 | SN2
49.9 | SN2
50 | SN2
50.2 | SN2
50 | SN2
49.8 | SN2
49.8 | SN2
49.9 | SN2
49.7 | SN2
49.9 | SN2
49.7 | SN2
49.8 | SN2
49.8 | SN2
49.6 | SN2
49.2 | SN2
49.6 | SN2
49.8 | SN2
49.4 | SN2
49.4 | SN2
49.3 | SN2
49.7 | SN2
49.5 | SN2
49.8 | SN2
50 | SN2
50.5 | SN2
50.2 | SN2
50.4 | SN2
51.1 | SN2
51.3 | SN2
51.2 | SN2
50.6 | SN2
50.4 | SN2
50.7 | SN2
50.2 | SN2
50.1 | SN2
50.3 | SN2
50 | SN2
49.7 | SN2
50 | SN2
49.7 | SN2
49.3 | SN2
48.6 | SN2
50.9 | SN2
50.3 | SN2
50.3 | SN2
49.8 | SN2
50.1 | SN2
49.8 | SN2
49.5 | SN2
49.5 | SN2
50 | SN2
50.2 | SN2
50.5 | SN2
50.2 | SN2
50.8 | SN2
50.6 | SN2
50.5 | SN2
49.9 | SN2
50.2 | SN2
50.3 | SN2
49.9 | SN2
50.2 | SN2
50.1 | SN2
50.2 | SN2
50 | SN2
49.9 | SN2
50.1 | SN2
50.1 | SN2
50 | SN2
49.8 | SN2
49.9 | SN2
50.7 | SN2
50.9 | SN2
50.9 | SN2
51.2 | SN2
51.2 | SN2
51.2 | SN2
51.9 | SN2
51.9 | SN2
52.1 | SN2
52.3 | SN2
52.1 | SN2
52.2 | SN2
51.7 | SN2
51.1 | SN2
50.6 | SN2
50.6 | SN2
50.3 | SN2
50.4 | SN2
50 | SN2
49.6 | SN2
49.4 | SN2
49.4 | SN2
49.1 | SN2
49.3 | SN2
49.2 | SN2
49.2 | SN2
49.2 | SN2
49.6 | SN2
49.1 | SN2
49.4 | SN2
49.2 | SN2
49.3 | SN2
49.1 | SN2
49.6 | SN2
49.4 | SN2
49.3 | SN2
49 | SN2
48.9 | SN2
49.1 | SN2
49.1 | SN2
49.1 | SN2
48.9 | SN2
48.8 | SN2
48.8 | SN2
48.8 | SN2
49 | SN2
49.4 | SN2
49.7 | SN2
50.2 | SN2
51.8 | SN2
52.2 | SN2
52.4 | SN2
52.1 | SN2
52 | SN2
52.5 | SN2
51.8 | SN2
52.2 | SN2
51.5 | SN2
51.3 | SN2
51.5 | SN2
50.7 | SN2
50.4 | SN2
50.8 | SN2
50.6 | SN2
50.8 | SN2
50.3 | SN2
50.3 | SN2
50.4 | SN2
50.4 | SN2
50.1 | SN2
50.4 | SN2
50.1 | SN2
50.2 | SN2
49.9 | SN2
49.8 | SN2
49.8 | SN2
49.6 | SN2
49.7 | SN2
49.7 | SN2
49.5 | SN2
49.4 | SN2
49.4 | SN2
49.7 | SN2
49.5 | SN2
49.3 | SN2
49 | SN2
48.9 | SN2
49 | SN2
49.3 | SN2
49.5 | SN2
49.1 | SN2
49.2 | SN2
49.4 | SN2
49.4 | SN2
49.7 | SN2
50 | SN2
49.8 | SN2
49.6 | SN2
10.2 | SN2
10 | SN2
10.9 | SN2
52.9 | SN2
52.3 | SN2
52.5 | SN2
52 | SN2
51.9 | SN2
50.9 | SN2
50.6 | SN2
50.6 | SN2
50.8 | SN2
51 | SN2
50.8 | SN2
50.3 | SN2
50.2 | SN2
49.6 | SN2
49.7 | SN2
49.3 | SN2
49.6 | SN2
50.1 | SN2
49.1 | SN2
48.8 | SN2
49.2 | SN2
49.1 | SN2
49.4 | SN2
49.5 | SN2
49.5 | SN2
48.8 | SN2
49.2 | SN2
49 | SN2
48.4 | SN2
48.8 | SN2
48.4 | SN2
48.9 | SN2
48.9 | SN2
48.8 | SN2
48.9 | SN2
48.8 | SN2
48.9 | SN2
49.3 | SN2
53.6 | SN2
54.2 | SN2
54.4 | SN2
55 | SN2
55.5 | SN2
56.4 | SN2
53 | SN2
52.5 | SN2
51.9 | SN2
51.8 | SN2
52.1 | SN2
51.6 | SN2
50.9 | SN2
51.3 | SN2
50.9 | SN2
50.7 | SN2
50.5 | SN2
50.4 | SN2
49.7 | SN2
49.3 | SN2
49.2 | SN2
49.2 | SN2
49.6 | SN2
49.3 | SN2
48.9 | SN2
49 | SN2
48.6 | SN2
48.7 | SN2
48.8 | SN2
48.8 | SN2
48.8 | SN2
48.6 | SN2
48.6 | SN2
48.5 | SN2
48.7 | SN2
48.8 | SN2
48.4 | SN2
48.7 | SN2
48.4 | SN2
48.2 | SN2
48.2 | SN2
48.2 | SN2
48.5 | SN2
48.1 | SN2
48.1 | SN2
48.1 | SN2
47.7 | SN2
48.3 | SN2
48.4 | SN2
48.9 | SN2
50 | SN2
51.4 | SN2
52.3 | SN2
51.3 | SN2
51.8 | SN2
52.1 | SN2
52.1 | SN2
51.5 | SN2
50.7 | SN2
51 | SN2
50.9 | SN2
51.1 | SN2
50.4 | SN2
49.6 | SN2
49.3 | SN2
49.1 | SN2
48.5 | SN2
49 | SN2
49.2 | SN2
48.6 | SN2
48.7 | SN2
48.7 | SN2
48.6 | SN2
48.7 | SN2
48.8 | SN2
48.7 | SN2
48.7 | SN2
48.7 | SN2
48.5 | SN2
48.6 | SN2
48.5 | SN2
48.1 | SN2
48.4 | SN2
48.4 | SN2
48.3 | SN2
48.7 | SN2
48.4 | SN2
48.4 | SN2
48.1 | SN2
48.1 | SN2
47.8 | SN2
48.2 | SN2
48.1 | SN2
48.6 | SN2
48.2 | SN2
48.7 | SN2
48.9 | SN2
49.3 | SN2
49.6 | SN2
50.9 | SN2
51.7 | SN2
51.5 | SN2
52 | SN2
51.6 | SN2
50.9 | SN2
51.2 | SN2
50.8 | SN2
50.5 | SN2
49.6 | SN2
49.3 | SN2
49.4 | SN2
48.7 | SN2
49.1 | SN2
48.7 | SN2
48.3 | SN2
48 | SN2
48 | SN2
48.1 | SN2
48 | SN2
48.1 | SN2
48.1 | SN2
48.1 | SN2
48.1 | SN2
47.5 | SN2
47.3 | SN2
47.5 | SN2
47.5 | SN2
47.3 | SN2
47.1 | SN2
46.8 | SN2
46.6 | SN2
46.6 | SN2
45.9 | SN2
46.5 | SN2
46.4 | SN2
46.3 | SN2
46.1 | SN2
46.1 | SN2
46.6 | SN2
46.7 | SN2
46.8 | SN2
47.5 | SN2
47.7 | SN2
48.3 | SN2
48.9 | SN2
49.7 | SN2
50.9 | SN2
50.6 | SN2
50.3 | SN2
50.3 | SN2
50.4 | SN2
50 | SN2
49.7 | SN2
49.5 | SN2
48.8 | SN2
48.2 | SN2
48 | SN2
47.3 | SN2
47.1 | SN2
47.5 | SN2
47.2 | SN2
47 | SN2
47.1 | SN2
47.4 | SN2
47.1 | SN2
46.8 | SN2
46.8 | SN2
46.5 | SN2
46.8 | SN2
46.7 | SN2
46.9 | SN2
46.7 | SN2
46.3 | SN2
46.5 | SN2
46.8 | SN2
47.4 | SN2
46.4 | SN2
46.5 | SN2
46.3 | SN2
46.3 | SN2
46 | SN2
46 | SN2
46.6 | SN2
46.3 | SN2
46.6 | SN2
46.8 | SN2
46.8 | SN2
47.1 | SN2
47.7 | SN2
47.7 | SN2
48.5 | SN2
50.1 | SN2
50.4 | SN2
49.9 | SN2
50 | SN2
50 | SN2
50.9 | SN2
50.4 | SN2
50.3 | SN2
49.9 | SN2
49.9 | SN2
49.4 | SN2
49 | SN2
48.8 | SN2
48.5 | SN2
48.5 | SN2
48.4 | SN2
48.2 | SN2
48.4 | SN2
48.4 | SN2
48.4 | SN2
48.3 | SN2
48 | SN2
47.9 | SN2
47.8 | SN2
48.2 | SN2
48.1 | SN2
47.9 | SN2
47.8 | SN2
47.8 | SN2
47.9 | SN2
47.9 | SN2
47.6 | SN2
47.6 | SN2
47.2 | SN2
47.4 | SN2
47.7 | SN2
47.4 | SN2
47.6 | SN2
47.4 | SN2
47.3 | SN2
47.4 | SN2
47.9 | SN2
48.5 | SN2
48.4 | SN2
49.1 | SN2
49.4 | SN2
50.8 | SN2
50.9 | SN2
50 | SN2
50 | SN2
50.5 | SN2
50.1 | SN2
50.1 | SN2
50.2 | SN2
50 | SN2
49.2 | SN2
48.7 | SN2
48.9 | SN2
48.1 | SN2
47.7 | SN2
47.9 | SN2
47.9 | SN2
48.1 | SN2
47.9 | SN2
48.2 | SN2
47.5 | SN2
47.7 | SN2
47.5 | SN2
47.9 | SN2
47.5 | SN2
47.5 | SN2
47.5 | SN2
47.7 | SN2
47.4 | SN2
47.4 | SN2
47.6 | SN2
47.4 | SN2
47 | SN2
47.2 | SN2
47 | SN2
47.3 | SN2
47.1 | SN2
47.4 | SN2
47.3 | SN2
47.2 | SN2
47.3 | SN2
47.4 | SN2
47.6 | SN2
48 | SN2
48.2 | SN2
48.7 | SN2
49.7 | SN2
51.3 | SN2
51.5 | SN2
50.6 | SN2
49.8 | SN2
50.6 | SN2
50.6 | SN2
50.8 | SN2
50.4 | SN2
49.8 | SN2
49.8 | SN2
49.6 | SN2
49.4 | SN2
48.4 | SN2
48.2 | SN2
47.9 | SN2
48.2 | SN2
48.3 | SN2
48.5 | SN2
48.7 | SN2
47.9 | SN2
48.5 | SN2
48.3 | SN2
48 | SN2
48.2 | SN2
48.1 | SN2
48.3 | SN2
48.4 | SN2
47.8 | SN2
47.9 | SN2
47.8 | SN2
48.2 | SN2
47.9 | SN2
47.7 | SN2
47.7 | SN2
47.5 | SN2
47.5 | SN2
47.5 | SN2
47.9 | SN2
47.7 | SN2
47.7 | SN2
48 | SN2
48 | SN2
48.4 | SN2
48.7 | SN2
49.8 | SN2
50.8 | SN2
51.3 | SN2
51.8 | SN2
51.8 | SN2
52 | SN2
52.7 | SN2
51 | SN2
51.9 | SN2
51.6 | SN2
51.3 | SN2
51.2 | SN2
50.3 | SN2
50.5 | SN2
50.2 | SN2
50.2 | SN2
50.2 | SN2
49.8 | SN2
49.6 | SN2
49.3 | SN2
49.2 | SN2
48.8 | SN2
48.9 | SN2
49.1 | SN2
49.1 | SN2
49.1 | SN2
49 | SN2
49.1 | SN2
49.2 | SN2
48.9 | SN2
49.2 | SN2
48.4 | SN2
48.7 | SN2
48.5 | SN2
48.9 | SN2
48.6 | SN2
48.5 | SN2
48.7 | SN2
48.6 | SN2
48.4 | SN2
48.3 | SN2
48.5 | SN2
48.7 | SN2
48.9 | SN2
49.3 | SN2
49.7 | SN2
50.1 | SN2
50.4 | SN2
51.1 | SN2
51.6 | SN2
51.9 | SN2
50.8 | SN2
51.3 | SN2
51.5 | SN2
51.4 | SN2
51 | SN2
50.7 | SN2
50.2 | SN2
50.4 | SN2
50.6 | SN2
50.1 | SN2
50 | SN2
49.6 | SN2
49.4 | SN2
48.9 | SN2
48.7 | SN2
48.6 | SN2
49 | SN2
48.8 | SN2
48.8 | SN2
48.4 | SN2
49 | SN2
48.6 | SN2
48.6 | SN2
48.7 | SN2
48.3 | SN2
48.5 | SN2
48.4 | SN2
48.3 | SN2
48.6 | SN2
48.4 | SN2
48.7 | SN2
48 | SN2
47.5 | SN2
48.1 | SN2
48.3 | SN2
48.6 | SN2
48.3 | SN2
48.4 | SN2
48.7 | SN2
49.1 | SN2
49.6 | SN2
50 | SN2
50.6 | SN2
51 | SN2
51.5 | SN2
51.3 | SN2
51.2 | SN2
51.5 | SN2
51.5 | SN2
51.6 | SN2
51.8 | SN2
50.9 | SN2
51.1 | SN2
50.6 | SN2
49.7 | SN2
49.2 | SN2
49.1 | SN2
48.9 | SN2
48.9 | SN2
48.8 | SN2
48.6 | SN2
48.4 | SN2
48.4 | SN2
48.4 | SN2
48.2 | SN2
47.6 | SN2
48.2 | SN2
48.1 | SN2
47.6 | SN2
48.1 | SN2
47.7 | SN2
47.9 | SN2
47.6 | SN2
48 | SN2
48.4 | SN2
48.1 | SN2
47.5 | SN2
47.9 | SN2
47.8 | SN2
47.8 | SN2
47.9 | SN2
47.5 | SN2
47.5 | SN2
47.6 | SN2
47.8 | SN2
48.4 | SN2
48.2 | SN2
48.9 | SN2
49.8 | SN2
50.5 | SN2
50.9 | SN2
51.4 | SN2
51.1 | SN2
51.5 | SN2
51.4 | SN2
51.1 | SN2
51.1 | SN2
51 | SN2
50.7 | SN2
49.9 | SN2
49.8 | SN2
49.7 | SN2
49 | SN2
48.4 | SN2
48.6 | SN2
48.6 | SN2
48.5 | SN2
48.7 | SN2
48.7 | SN2
48.4 | SN2
48.3 | SN2
47.8 | SN2
48.1 | SN2
48.5 | SN2
48.3 | SN2
48.4 | SN2
48.2 | SN2
47.8 | SN2
47.9 | SN2
47.8 | SN2
48 | SN2
47.9 | SN2
47.8 | SN2
47.7 | SN2
48.1 | SN2
47.9 | SN2
47.6 | SN2
47.6 | SN2
47.6 | SN2
47.8 | SN2
48.1 | SN2
48.8 | SN2
48.9 | SN2
49.3 | SN2
49.3 | SN2
50.4 | SN2
51.4 | SN2
51.3 | SN2
51.1 | SN2
51.9 | SN2
51.1 | SN2
50.7 | SN2
50.6 | SN2
50.5 | SN2
49.6 | SN2
49.5 | SN2
49.7 | SN2
49.2 | SN2
49.2 | SN2
49.1 | SN2
48.8 | SN2
48.1 | SN2
48.5 | SN2
48.4 | SN2
48.5 | SN2
48.4 | SN2
48.2 | SN2
48 | SN2
48 | SN2
47.6 | SN2
47.6 | SN2
47.6 | SN2
48 | SN2
47.8 | SN2
47.9 | SN2
47.8 | SN2
47.3 | SN2
47.3 | SN2
47.3 | SN2
47.4 | SN2
47.1 | SN2
47.2 | SN2
47.5 | SN2
47.1 | SN2
47.3 | SN2
46.6 | SN2
47.2 | SN2
47.7 | SN2
48.1 | SN2
48.3 | SN2
49.3 | SN2
49.8 | SN2
50.7 | SN2
51 | SN2
51.3 | SN2
51.5 | SN2
51.6 | SN2
51.3 | SN2
51.2 | SN2
51 | SN2
49.4 | SN2
49.7 | SN2
49.8 | SN2
49.4 | SN2
49.1 | SN2
48.6 | SN2
48.7 | SN2
48.7 | SN2
48.3 | SN2
48.5 | SN2
48.6 | SN2
47.9 | SN2
48.2 | SN2
47.6 | SN2
47.8 | SN2
48 | SN2
48.3 | SN2
48.3 | SN2
48 | SN2
47.7 | SN2
47.9 | SN2
47.8 | SN2
47.5 | SN2
47.8 | SN2
47.4 | SN2
47.1 | SN2
47.3 | SN2
47.2 | SN2
47 | SN2
47.4 | SN2
47.2 | SN2
47.4 | SN2
47.2 | SN2
47.4 | SN2
48 | SN2
48.8 | SN2
49.7 | SN2
50.1 | SN2
50.5 | SN2
50.1 | SN2
50.3 | SN2
48.8 | SN2
50.6 | SN2
50.8 | SN2
50.5 | SN2
50.2 | SN2
49.8 | SN2
49 | SN2
48.7 | SN2
48.6 | SN2
48.4 | SN2
48.2 | SN2
47.8 | SN2
47.7 | SN2
48.3 | SN2
48.2 | SN2
47.9 | SN2
47.5 | SN2
47.9 | SN2
47.8 | SN2
47.3 | SN2
47.4 | SN2
47.4 | SN2
47.2 | SN2
47.3 | SN2
47.4 | SN2
47.5 | SN2
47.3 | SN2
47.3 | SN2
47 | SN2
47 | SN2
47.1 | SN2
47.3 | SN2
47.1 | SN2
47.1 | SN2
47 | SN2
46.9 | SN2
46.8 | SN2
47.3 | SN2
52 | SN2
50.3 | SN2
50.5 | SN2
50.9 | SN2
51.5 | SN2
52 | SN2
51.2 | SN2
50.8 | SN2
50.6 | SN2
51 | SN2
50.8 | SN2
50.5 | SN2
50.4 | SN2
50.1 | SN2
49.6 | SN2
49.6 | SN2
49.1 | SN2
49.4 | SN2
48.9 | SN2
49 | SN2
49 | SN2
48.5 | SN2
47.9 | SN2
48.2 | SN2
48.2 | SN2
47.4 | SN2
48.1 | SN2
48.1 | SN2
47.8 | SN2
48.1 | SN2
47.9 | SN2
48.1 | SN2
48 | SN2
48.1 | SN2
48.2 | SN2
48.3 | SN2
48.1 | SN2
47.9 | SN2
47.8 | SN2
47.8 | SN2
47.5 | SN2
47.6 | SN2
47.6 | SN2
47.9 | SN2
47.6 | SN2
47.9 | SN2
48.4 | SN2
48.6 | SN2
48.9 | SN2
50.2 | SN2
51.3 | SN2
51 | SN2
50.9 | SN2
50.9 | SN2
51.2 | SN2
51.3 | SN2
51.3 | SN2
51 | SN2
50.8 | SN2
50.8 | SN2
50.1 | SN2
49.6 | SN2
49.4 | SN2
48.9 | SN2
48.4 | SN2
46.4 | SN2
49.5 | SN2
49.2 | SN2
48.6 | SN2
48.5 | SN2
49 | SN2
48.2 | SN2
48.6 | SN2
48.6 | SN2
48.8 | SN2
48.6 | SN2
48.3 | SN2
48.4 | SN2
48.2 | SN2
49 | SN2
48.6 | SN2
48.3 | SN2
48.3 | SN2
48.5 | SN2
48.5 | SN2
48.4 | SN2
48.7 | SN2
48.2 | SN2
48.1 | SN2
48.4 | SN2
48.7 | SN2
48.6 | SN2
49.3 | SN2
49 | SN2
49.3 | SN2
49.7 | SN2
49.6 | SN2
50.1 | SN2
50.1 | SN2
50.7 | SN2
50.8 | SN2
50.6 | SN2
50.5 | SN2
50.2 | SN2
49.8 | SN2
49.9 | SN2
50 | SN2
49.5 | SN2
49.3 | SN2
49 | SN2
48.6 | SN2
49 | SN2
48.8 | SN2
48.4 | SN2
48.6 | SN2
48.6 | SN2
49 | SN2
48.3 | SN2
48.3 | SN2
48.8 | SN2
49.9 | SN2
51.5 | SN2
52.6 | SN2
52.5 | SN2
53.1 | SN2
53.8 | SN2
54.9 | SN2
54.1 | SN2
53.8 | SN2
54.1 | SN2
54 | SN2
53.8 | SN2
53.8 | SN2
53.6 | SN2
53.8 | SN2
53.9 | SN2
53.7 | SN2
53.8 | SN2
53.8 | SN2
54.3 | SN2
54.8 | SN2
54.9 | SN2
55.2 | SN2
55.2 | SN2
55.1 | SN2
55.2 | SN2
55.2 | SN2
55 | SN2
55 | SN2
54.4 | SN2
54.6 | SN2
54.6 | SN2
54.4 | SN2
53.6 | SN2
53.6 | SN2
53.1 | SN2
53.3 | SN2
53 | SN2
52.7 | SN2
52.6 | SN2
52.3 | SN2
52.4 | SN2
52.3 | SN2
52.2 | SN2
52.2 | SN2
52.4 | SN2
52.4 | SN2
52.2 | SN2
52.1 | SN2
52.3 | SN2
52.1 | SN2
52.1 | SN2
52.1 | SN2
51.9 | SN2
52.1 | SN2
51.9 | SN2
52.2 | SN2
52 | SN2
52.2 | SN2
51.9 | SN2
51.9 | SN2
51.4 | SN2
51.8 | SN2
51.7 | SN2
51.8 | SN2
52.3 | SN2
52.5 | SN2
53.4 | SN2
55.3 | SN2
55.8 | SN2
55.8 | SN2
56.1 | SN2
56 | SN2
56 | SN2
55.7 | SN2
55.7 | SN2
55.7 | SN2
55.4 | SN2
54.6 | SN2
54.7 | SN2
54.7 | SN2
54.2 | SN2
54.3 | SN2
53.9 | SN2
54 | SN2
53.9 | SN2
53.9 | SN2
53.9 | SN2
53.8 | SN2
53.7 | SN2
53.9 | SN2
53.6 | SN2
53.8 | SN2
53.7 | SN2
53.3 | SN2
53.5 | SN2
53.6 | SN2
53.7 | SN2
53.9 | SN2
53.8 | SN2
53.5 | SN2
53.4 | SN2
53.2 | SN2
53.6 | SN2
53.6 | SN2
53.5 | SN2
53.6 | SN2
53.7 | SN2
53.2 | SN2
53.6 | SN2
53.4 | SN2
53.9 | SN2
53.7 | SN2
54 | SN2
53.7 | SN2
54.9 | SN2
56.1 | SN2
55.5 | SN2
55.4 | SN2
55.7 | SN2
55.7 | SN2
55.1 | SN2
55.2 | SN2
54.9 | SN2
55 | SN2
54.5 | SN2
54.3 | SN2
53.9 | SN2
54.1 | SN2
56.5 | SN2
54.6 | SN2
54.1 | SN2
53.8 | SN2
53.2 | SN2
53.4 | SN2
53.5 | SN2
53.5 | SN2
53.4 | SN2
53.4 | SN2
53.2 | SN2
53.5 | SN2
53.2 | SN2
53.3 | SN2
53.2 | SN2
53.1 | SN2
53.3 | SN2
52.9 | SN2
53.1 | SN2
53 | SN2
52.9 | SN2
53.1 | SN2
53.3 | SN2
53 | SN2
53.1 | SN2
52.8 | SN2
52.7 | SN2
53.3 | SN2
53.1 | SN2
53.5 | SN2
53.3 | SN2
53.9 | SN2
54.4 | SN2
55.5 | SN2
56.1 | SN2
54.8 | SN2
55.1 | SN2
54.8 | SN2
54.8 | SN2
54.4 | SN2
53.9 | SN2
53.3 | SN2
52.8 | SN2
52.8 | SN2
51.6 | SN2
51.4 | SN2
51 | SN2
51.3 | SN2
50.9 | SN2
50.9 | SN2
50.8 | SN2
50.5 | SN2
50.4 | SN2
50.5 | SN2
50.4 | SN2
50.3 | SN2
50 | SN2
50.1 | SN2
50.1 | SN2
49.8 | SN2
49.8 | SN2
49.7 | SN2
50 | SN2
49.6 | SN2
49.6 | SN2
49.5 | SN2
49.4 | SN2
49.7 | SN2
49.4 | SN2
49.2 | SN2
49.4 | SN2
49.4 | SN2
49.4 | SN2
49.1 | SN2
49.7 | SN2
49.8 | SN2
50.1 | SN2
50.4 | SN2
51.2 | SN2
51.9 | SN2
52.4 | SN2
53.5 | SN2
58.3 | SN2
54.9 | SN2
54.7 | SN2
54.2 | SN2
53.5 | SN2
53.7 | SN2
53 | SN2
52.5 | SN2
51.8 | SN2
51.7 | SN2
51.1 | SN2
51 | SN2
51.1 | SN2
50.9 | SN2
50.2 | SN2
50.3 | SN2
50.4 | SN2
50.5 | SN2
50.6 | SN2
50.7 | SN2
50.3 | SN2
50.4 | SN2
50.4 | SN2
50.2 | SN2
50.3 | SN2
50.2 | SN2
50 | SN2
49.8 | SN2
50.1 | SN2
49.8 | SN2
49.8 | SN2
49.9 | SN2
50 | SN2
49.8 | SN2
49.7 | SN2
49.4 | SN2
49.6 | SN2
49.9 | SN2
49.9 | SN2
49.9 | SN2
50.6 | SN2
51.2 | SN2
51.6 | SN2
52.3 | SN2
54 | SN2
53.4 | SN2
53.4 | SN2
54.1 | SN2
54 | SN2
54 | SN2
54.1 | SN2
53.6 | SN2
53 | SN2
52.2 | SN2
51.8 | SN2
51.5 | SN2
51.2 | SN2
50.7 | SN2
50.7 | SN2
50.4 | SN2
50.5 | SN2
50.4 | SN2
50.5 | SN2
50 | SN2
50.4 | SN2
50.5 | SN2
50.5 | SN2
49.7 | SN2
50.1 | SN2
50.3 | SN2
50.1 | SN2
49.8 | SN2
50 | SN2
49.8 | SN2
50 | SN2
50.4 | SN2
49.9 | SN2
49.9 | SN2
49.8 | SN2
49.6 | SN2
49.4 | SN2
49.3 | SN2
49.3 | SN2
49.6 | SN2
49.8 | SN2
50.3 | SN2
50.6 | SN2
51.1 | SN2
52 | SN2
52.3 | SN2
53 | SN2
52.9 | SN2
52.8 | SN2
53.6 | SN2
53.7 | SN2
53.5 | SN2
53.3 | SN2
53.2 | SN2
53.2 | SN2
53.1 | SN2
52.3 | SN2
51.5 | SN2
50.9 | SN2
50.6 | SN2
50 | SN2
49.8 | SN2
50 | SN2
49.9 | SN2
50.1 | SN2
49.6 | SN2
49.8 | SN2
49.9 | SN2
49.8 | SN2
49.7 | SN2
49.8 | SN2
49.8 | SN2
49.5 | SN2
49.7 | SN2
49.7 | SN2
49.4 | SN2
49.6 | SN2
49.5 | SN2
49.3 | SN2
49.1 | SN2
48.9 | SN2
49 | SN2
48.7 | SN2
48.7 | SN2
49.1 | SN2
49.3 | SN2
49 | SN2
49.3 | SN2
49.7 | SN2
50.4 | SN2
51.1 | SN2
51.7 | SN2
52.2 | SN2
52.3 | SN2
52.6 | SN2
52.9 | SN2
52.7 | SN2
53 | SN2
53.3 | SN2
53.1 | SN2
53.1 | SN2
52.3 | SN2
52.2 | SN2
51.6 | SN2
51.1 | SN2
50.7 | SN2
49.6 | SN2
49.6 | SN2
49.8 | SN2
49.9 | SN2
49.9 | SN2
49.6 | SN2
49.6 | SN2
49.5 | SN2
49.6 | SN2
49.6 | SN2
49.6 | SN2
49.8 | SN2
49.7 | SN2
49.7 | SN2
49.4 | SN2
49.6 | SN2
49.3 | SN2
49.1 | SN2
49.3 | SN2
49.3 | SN2
49.3 | SN2
49.3 | SN2
49.4 | SN2
49 | SN2
49.6 | SN2
49.5 | SN2
49.9 | SN2
50 | SN2
50.2 | SN2
50.4 | SN2
50.4 | SN2
50.2 | SN2
50.5 | SN2
50.7 | SN2
50.5 | SN2
50.5 | SN2
50.8 | SN2
50.8 | SN2
51.3 | SN2
51.3 | SN2
51.3 | SN2
51.1 | SN2
50.7 | SN2
50.6 | SN2
50.4 | SN2
50.2 | SN2
50.2 | SN2
50.1 | SN2
49.5 | SN2
49.8 | SN2
49.4 | SN2
49.9 | SN2
49.8 | SN2
49.9 | SN2
49.6 | SN2
50 | SN2
49.5 | SN2
49.9 | SN2
49.6 | SN2
49.7 | SN2
49.6 | SN2
49.7 | SN2
49.5 | SN2
49.3 | SN2
49.3 | SN2
49 | SN2
47.9 | SN2
47.7 | SN2
47.6 | SN2
47.5 | SN2
47.2 | SN2
47.5 | SN2
47.7 | SN2
48.1 | SN2
48.6 | SN2
48.5 | SN2
49.2 | SN2
49.5 | SN2
50.4 | SN2
50.2 | SN2
50.2 | SN2
50.3 | SN2
50.3 | SN2
50.7 | SN2
51.3 | SN2
51.7 | SN2
51.6 | SN2
51.6 | SN2
51.1 | SN2
52.1 | SN2
51.7 | SN2
51 | SN2
50.3 | SN2
49.9 | SN2
50 | SN2
49.6 | SN2
49.5 | SN2
49.5 | SN2
49.3 | SN2
48.8 | SN2
48.8 | SN2
48.8 | SN2
49 | SN2
48.6 | SN2
48.4 | SN2
48.2 | SN2
48.4 | SN2
48.4 | SN2
47.2 | SN2
46.8 | SN2
46.7 | SN2
46.7 | SN2
45.7 | SN2
45.4 | SN2
45.2 | SN2
45.1 | SN2
45.1 | SN2
45.3 | SN2
46.5 | SN2
47.3 | SN2
48 | SN2
47.9 | SN2
49.2 | SN2
51.2 | SN2
49.5 | SN2
52.3 | SN2
52.4 | SN2
52.9 | SN2
52.3 | SN2
52.5 | SN2
53.2 | SN2
52 | SN2
51.9 | SN2
53.9 | SN2
53.1 | SN2
52.1 | SN2
51.4 | SN2
50.7 | SN2
50.1 | SN2
49.4 | SN2
49.2 | SN2
49.4 | SN2
48.9 | SN2
49.2 | SN2
48.5 | SN2
49.1 | SN2
49 | SN2
48.2 | SN2
48 | SN2
48 | SN2
47.5 | SN2
47.8 | SN2
48 | SN2
47.9 | SN2
47.9 | SN2
47.8 | SN2
47.7 | SN2
47.6 | SN2
47.6 | SN2
47.3 | SN2
47.2 | SN2
47.6 | SN2
47.4 | SN2
47.7 | SN2
47.8 | SN2
48.2 | SN2
56.6 | SN2
54 | SN2
51.9 | SN2
52 | SN2
52.5 | SN2
52.5 | SN2
51.8 | SN2
53.5 | SN2
54 | SN2
54.3 | SN2
54.4 | SN2
54.4 | SN2
54.1 | SN2
53.7 | SN2
52.4 | SN2
53.3 | SN2
51.9 | SN2
52.1 | SN2
51.3 | SN2
50.7 | SN2
50.8 | SN2
50.3 | SN2
50.5 | SN2
50.6 | SN2
50.1 | SN2
49.7 | SN2
50 | SN2
50.1 | SN2
50.2 | SN2
50.2 | SN2
49.9 | SN2
49.4 | SN2
49.7 | SN2
49.4 | SN2
49.3 | SN2
49.4 | SN2
49.2 | SN2
49 | SN2
49 | SN2
49 | SN2
49.2 | SN2
48.9 | SN2
49.2 | SN2
49.3 | SN2
49.3 | SN2
50.1 | SN2
50.4 | SN2
51.1 | SN2
52.3 | SN2
53.2 | SN2
53.4 | SN2
53.7 | SN2
53.9 | SN2
54.1 | SN2
54.6 | SN2
54.5 | SN2
54.6 | SN2
53.8 | SN2
54.7 | SN2
53.8 | SN2
53 | SN2
52.5 | SN2
51.9 | SN2
51.7 | SN2
51.7 | SN2
51.1 | SN2
50.8 | SN2
51 | SN2
51.1 | SN2
50.8 | SN2
50.8 | SN2
50.5 | SN2
50.6 | SN2
50.8 | SN2
50.5 | SN2
50.3 | SN2
50.5 | SN2
50.3 | SN2
50.1 | SN2
50.1 | SN2
49.5 | SN2
50.2 | SN2
49.9 | SN2
49.8 | SN2
49.7 | SN2
49.4 | SN2
49.4 | SN2
49.2 | SN2
49.6 | SN2
49.8 | SN2
49.7 | SN2
50.4 | SN2
51 | SN2
51.8 | SN2
52.6 | SN2
53.1 | SN2
53.6 | SN2
53.9 | SN2
53.7 | SN2
53.8 | SN2
53.8 | SN2
54.2 | SN2
54.1 | SN2
53.8 | SN2
53.5 | SN2
53.5 | SN2
52.9 | SN2
52 | SN2
51.9 | SN2
51.7 | SN2
51.6 | SN2
50.8 | SN2
50.5 | SN2
50.6 | SN2
51 | SN2
50.8 | SN2
50.8 | SN2
50.5 | SN2
50.5 | SN2
50.8 | SN2
51.1 | SN2
50.5 | SN2
50.3 | SN2
50.2 | SN2
50.2 | SN2
49.9 | SN2
50.2 | SN2
50.1 | SN2
49.8 | SN2
49.7 | SN2
49.7 | SN2
49.4 | SN2
49.7 | SN2
49.3 | SN2
49.3 | SN2
49.3 | SN2
49.9 | SN2
50.2 | SN2
50.8 | SN2
51.4 | SN2
52.2 | SN2
52 | SN2
52.6 | SN2
52.7 | SN2
53.1 | SN2
52.8 | SN2
52.8 | SN2
53.4 | SN2
53.4 | SN2
53 | SN2
53 | SN2
52.9 | SN2
52.2 | SN2
52.2 | SN2
51.6 | SN2
51.5 | SN2
51.3 | SN2
50.8 | SN2
51 | SN2
50.4 | SN2
50.3 | SN2
50.5 | SN2
50.5 | SN2
50.2 | SN2
50.1 | SN2
50.1 | SN2
50.1 | SN2
50.4 | SN2
50.4 | SN2
50.3 | SN2
49.8 | SN2
50.2 | SN2
50.1 | SN2
50.3 | SN2
50.1 | SN2
49.8 | SN2
50 | SN2
49.9 | SN2
49.8 | SN2
50 | SN2
49.8 | SN2
49.5 | SN2
49.7 | SN2
49.1 | SN2
52.4 | SN2
52.3 | SN2
53.1 | SN2
53 | SN2
53.4 | SN2
52.9 | SN2
53.1 | SN2
52.6 | SN2
53.4 | SN2
53.7 | SN2
53.3 | SN2
53.4 | SN2
53.9 | SN2
52.7 | SN2
52.8 | SN2
52.2 | SN2
52 | SN2
51.7 | SN2
51.2 | SN2
51.1 | SN2
50.9 | SN2
50.7 | SN2
50.8 | SN2
50.7 | SN2
50.8 | SN2
50.8 | SN2
50.7 | SN2
50.8 | SN2
50.9 | SN2
50.8 | SN2
50.7 | SN2
50.7 | SN2
50.6 | SN2
50.5 | SN2
50.7 | SN2
50.7 | SN2
50.7 | SN2
50.5 | SN2
50.7 | SN2
50.6 | SN2
50.3 | SN2
50.3 | SN2
50.1 | SN2
50.5 | SN2
50.5 | SN2
50.8 | SN2
51.5 | SN2
52 | SN2
52.9 | SN2
53.9 | SN2
54.3 | SN2
53.8 | SN2
53.9 | SN2
54.5 | SN2
54 | SN2
54.3 | SN2
53.9 | SN2
53.9 | SN2
53.8 | SN2
53.6 | SN2
53 | SN2
52.7 | SN2
52.9 | SN2
52.1 | SN2
52.1 | SN2
51.7 | SN2
51.4 | SN2
51.1 | SN2
51.3 | SN2
51.2 | SN2
51.1 | SN2
51.1 | SN2
51.1 | SN2
50.8 | SN2
51 | SN2
51.1 | SN2
51 | SN2
51.4 | SN2
50.7 | SN2
50.8 | SN2
50.8 | SN2
50.7 | SN2
50.4 | SN2
50.5 | SN2
50.5 | SN2
50.3 | SN2
50.3 | SN2
50.2 | SN2
50.2 | SN2
50.1 | SN2
50 | SN2
50.4 | SN2
51 | SN2
51.4 | SN2
51.8 | SN2
52.1 | SN2
54.1 | SN2
53.3 | SN2
53.1 | SN2
53.1 | SN2
53.3 | SN2
54.2 | SN2
54 | SN2
54 | SN2
53.6 | SN2
53.5 | SN2
53 | SN2
52.9 | SN2
52.5 | SN2
52.5 | SN2
51.8 | SN2
51.8 | SN2
51.3 | SN2
51 | SN2
51.5 | SN2
51.3 | SN2
51.3 | SN2
51.2 | SN2
51.2 | SN2
51.6 | SN2
51.4 | SN2
51.5 | SN2
51.4 | SN2
51.5 | SN2
51.5 | SN2
51.2 | SN2
51.4 | SN2
51 | SN2
51.2 | SN2
51.3 | SN2
51.3 | SN2
51.2 | SN2
50.9 | SN2
50.8 | SN2
50.8 | SN2
50.7 | SN2
51 | SN2
51 | SN2
51.5 | SN2
51.9 | SN2
52.5 | SN2
53.8 | SN2
54.3 | SN2
54.6 | SN2
54.6 | SN2
54.6 | SN2
55 | SN2
55.2 | SN2
55 | SN2
54.4 | SN2
54.3 | SN2
54.3 | SN2
53.8 | SN2
52.9 | SN2
52.6 | SN2
52.5 | SN2
52.2 | SN2
52 | SN2
51.9 | SN2
51.7 | SN2
51.9 | SN2
51.7 | SN2
51.7 | SN2
51.7 | SN2
51.6 | SN2
51.8 | SN2
51.1 | SN2
51.3 | SN2
51.2 | SN2
51.3 | SN2
51.1 | SN2
51.2 | SN2
51 | SN2
51 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
51.9 | SN2
52 | SN2
51.8 | SN2
51.9 | SN2
51.8 | SN2
51.8 | SN2
51.4 | SN2
51.6 | SN2
51.4 | SN2
51.8 | SN2
51.5 | SN2
51.7 | SN2
52.1 | SN2
52.5 | SN2
53.1 | SN2
53.6 | SN2
54.2 | SN2
54.4 | SN2
54.7 | SN2
55.4 | SN2
55.1 | SN2
55.1 | SN2
54.3 | SN2
54.1 | SN2
53.8 | SN2
53.9 | SN2
53.6 | SN2
53.1 | SN2
52.8 | SN2
52.5 | SN2
52.5 | SN2
52.3 | SN2
52.2 | SN2
52.6 | SN2
52.3 | SN2
52.5 | SN2
52.5 | SN2
52.7 | SN2
52.5 | SN2
52.6 | SN2
52.2 | SN2
52.5 | SN2
52.5 | SN2
52.5 | SN2
52.4 | SN2
52.4 | SN2
52 | SN2
52.1 | SN2
52.1 | SN2
51.7 | SN2
51.8 | SN2
51.8 | SN2
51.8 | SN2
51.8 | SN2
51.5 | SN2
51.5 | SN2
51.7 | SN2
52.1 | SN2
52.4 | SN2
52.5 | SN2
52.7 | SN2
53.1 | SN2
54 | SN2
54.1 | SN2
54.3 | SN2
53.6 | SN2
53.4 | SN2
53.7 | SN2
54.1 | SN2
53.6 | SN2
53.6 | SN2
52.8 | SN2
52.4 | SN2
52.3 | SN2
52.1 | SN2
52 | SN2
52 | SN2
51.7 | SN2
51.6 | SN2
51.7 | SN2
51.4 | SN2
51.5 | SN2
51.5 | SN2
51.5 | SN2
51.4 | SN2
51.4 | SN2
51.5 | SN2
51.5 | SN2
51.4 | SN2
51.4 | SN2
51.5 | SN2
51.1 | SN2
51.4 | SN2
50.9 | SN2
51.1 | SN2
51.3 | SN2
50.9 | SN2
51.1 | SN2
50.9 | SN2
50.7 | SN2
50.6 | SN2
50.9 | SN2
51 | SN2
50.9 | SN2
51.1 | SN2
51.3 | SN2
52 | SN2
52.5 | SN2
53 | SN2
53.7 | SN2
54.2 | SN2
54.6 | SN2
54.6 | SN2
55 | SN2
55.7 | SN2
55.9 | SN2
55.6 | SN2
55.4 | SN2
54.4 | SN2
54.5 | SN2
54 | SN2
53.5 | SN2
53 | SN2
52.5 | SN2
52.6 | SN2
52.4 | SN2
52.7 | SN2
52.7 | SN2
52.6 | SN2
52.6 | SN2
52.7 | SN2
52.4 | SN2
52.3 | SN2
52.2 | SN2
52.3 | SN2
52.1 | SN2
52.4 | SN2
52.3 | SN2
52 | SN2
52 | SN2
52.2 | SN2
51.9 | SN2
52.1 | SN2
52.1 | SN2
52.1 | SN2
52.1 | SN2
51.9 | SN2
52.3 | SN2
52.6 | SN2
52.3 | SN2
59.5 | SN2
59.4 | SN2
58 | SN2
56.6 | SN2
56.7 | SN2
56.6 | SN2
56.3 | SN2
56.5 | SN2
56.3 | SN2
56.3 | SN2
56.5 | SN2
56 | SN2
55.9 | SN2
56.1 | SN2
54.9 | SN2
54.6 | SN2
54.5 | SN2
57.1 | SN2
55 | SN2
54.1 | SN2
56.4 | SN2
54.7 | SN2
54.1 | SN2
53.5 | SN2
53.6 | SN2
53.6 | SN2
53.2 | SN2
53.3 | SN2
52.7 | SN2
52.7 | SN2
52.7 | SN2
52.5 | SN2
52.8 | SN2
52.8 | SN2
52.6 | SN2
52.7 | SN2
52.6 | SN2
52.5 | SN2
52.5 | SN2
52.3 | SN2
52.5 | SN2
52.3 | SN2
52.3 | SN2
52.5 | SN2
52.3 | SN2
52.6 | SN2
52.8 | SN2
52.9 | SN2
53.4 | SN2
53.5 | SN2
53.8 | SN2
54.4 | SN2
54.7 | SN2
54.5 | SN2
54.8 | SN2
55 | SN2
54.7 | SN2
54 | SN2
54.1 | SN2
53.7 | SN2
53 | SN2
53.5 | SN2
52.9 | SN2
52.7 | SN2
52.3 | SN2
52 | SN2
52.1 | SN2
51.9 | SN2
52 | SN2
52.2 | SN2
52.1 | SN2
52.1 | SN2
52.4 | SN2
52.8 | SN2
52.5 | SN2
52.3 | SN2
52.2 | SN2
52.2 | SN2
52.4 | SN2
52.4 | SN2
52.3 | SN2
52.4 | SN2
52.4 | SN2
52.3 | SN2
52.4 | SN2
52.4 | SN2
52.5 | SN2
52.6 | SN2
52.4 | SN2
52.1 | SN2
52.2 | SN2
52.3 | SN2
52.1 | SN2
52.2 | SN2
52.8 | SN2
52.5 | SN2
49.4 | SN2
42.7 | SN2
38.8 | SN2
35.4 | SN2
33 | SN2
29 | SN2
27.8 | SN2
27 | SN2
27.8 | SN2
27.2 | SN2
26.8 | SN2
23.3 | SN2
19.3 | SN2
13.5 | SN2
10.6 | SN2
9.5 | SN2
8.8 | SN2
7.6 | SN2
6.8 | SN2
6.8 | SN2
7.1 | SN2
6.9 | SN2
5.8 | SN2
5.4 | SN2
5.3 | SN2
5.2 | SN2
5.1 | SN2
5 | SN2
4.9 | SN2
4.8 | SN2
4.4 | SN2
4.1 | SN2
3.8 | SN2
3.5 | SN2
3.4 | SN2
3.4 | SN2
3.2 | SN2
3 | SN2
2.9 | SN2
2.9 | SN2
2.8 | SN2
2.8 | SN2
2.7 | SN2
2.6 | SN2
2.7 | SN2
2.7 | SN2
2.7 | SN2
2.5 | SN2
2.3 | SN2
2.1 | SN2
1.9 | SN2
1.6 | SN2
1.6 | SN2
1.6 | SN2
1.5 | SN2
1.4 | SN2
1.3 | SN2
1.2 | SN2
1.2 | SN2
0.8 | SN2
0.8 | SN2
0 | SN2
0 | SN2
2 | SN2
56.1 | SN2
57.6 | SN2
57.4 | SN2
57.6 | SN2
57.4 | SN2
57.5 | SN2
57.1 | SN2
57 | SN2
57 | SN2
56.9 | SN2
56.8 | SN2
56.6 | SN2
56.9 | SN2
56.6 | SN2
56.4 | SN2
56.6 | SN2
56.1 | SN2
56.2 | SN2
56.1 | SN2
56.6 | SN2
56.4 | SN2
56 | SN2
56.7 | SN2
56.4 | SN2
56.7 | SN2
56.6 | SN2
56.7 | SN2
56.9 | SN2
57.8 | SN2
58.5 | SN2
58.3 | SN2
58 | SN2
55.6 | SN2
55.1 | SN2
55.5 | SN2
55.4 | SN2
55.1 | SN2
54.6 | SN2
54.1 | SN2
54.1 | SN2
53.5 | SN2
53.3 | SN2
52.7 | SN2
52.3 | SN2
53.8 | SN2
55.5 | SN2
55.7 | SN2
55.6 | SN2
56 | SN2
55.8 | SN2
56.2 | SN2
55.8 | SN2
55.8 | SN2
55.7 | SN2
55.4 | SN2
56.1 | SN2
55.9 | SN2
56.1 | SN2
55.8 | SN2
55.8 | SN2
55.8 | SN2
55.9 | SN2
56 | SN2
55.8 | SN2
55.7 | SN2
55.6 | SN2
55.8 | SN2
55.8 | SN2
55.7 | SN2
56 | SN2
55.8 | SN2
55.1 | SN2
53 | SN2
55.7 | SN2
56.3 | SN2
54.4 | SN2
54.2 | SN2
54.5 | SN2
55.4 | SN2
55.5 | SN2
56.2 | SN2
55.4 | SN2
55.9 | SN2
55 | SN2
55.1 | SN2
54.5 | SN2
53.9 | SN2
53.5 | SN2
53.5 | SN2
53.2 | SN2
52.8 | SN2
55.9 | SN2
55.7 | SN2
56.2 | SN2
56.2 | SN2
56.4 | SN2
56.1 | SN2
56.5 | SN2
56.5 | SN2
55.8 | SN2
56.3 | SN2
56.5 | SN2
56.3 | SN2
56.1 | SN2
56.4 | SN2
56.3 | SN2
56.1 | SN2
56.5 | SN2
56.2 | SN2
55.8 | SN2
55.9 | SN2
56.2 | SN2
56.2 | SN2
56 | SN2
56.3 | SN2
56.4 | SN2
56.3 | SN2
57.1 | SN2
54.6 | SN2
54.8 | SN2
55 | SN2
55.1 | SN2
55.1 | SN2
55.3 | SN2
55.6 | SN2
55.1 | SN2
56 | SN2
55.5 | SN2
55.4 | SN2
55.3 | SN2
55.2 | SN2
54.2 | SN2
54.1 | SN2
53.5 | SN2
53.1 | SN2
52.9 | SN2
52.6 | SN2
52.3 | SN2
52.1 | SN2
52 | SN2
52.1 | SN2
52.1 | SN2
52.3 | SN2
56 | SN2
56.4 | SN2
56.3 | SN2
56.5 | SN2
56.6 | SN2
56.1 | SN2
56.2 | SN2
56.6 | SN2
56.4 | SN2
56.2 | SN2
56.4 | SN2
56.1 | SN2
55.9 | SN2
55.8 | SN2
55.8 | SN2
55.9 | SN2
55.9 | SN2
56.4 | SN2
56.6 | SN2
57 | SN2
54.8 | SN2
54 | SN2
57.6 | SN2
55.6 | SN2
55.6 | SN2
55.5 | SN2
55.2 | SN2
55.7 | SN2
55.7 | SN2
55.2 | SN2
54.9 | SN2
54.5 | SN2
54.4 | SN2
53.7 | SN2
53.6 | SN2
53.1 | SN2
52.7 | SN2
52.6 | SN2
52 | SN2
51.9 | SN2
51.7 | SN2
51.7 | SN2
51.6 | SN2
51.4 | SN2
51.2 | SN2
51.5 | SN2
51.5 | SN2
51.6 | SN2
51.9 | SN2
51.4 | SN2
51.3 | SN2
51.7 | SN2
51.3 | SN2
51.3 | SN2
51.6 | SN2
51.3 | SN2
51.2 | SN2
51.2 | SN2
51.4 | SN2
50.9 | SN2
51.4 | SN2
51.2 | SN2
51.2 | SN2
51.1 | SN2
51.2 | SN2
51.8 | SN2
51.9 | SN2
52.2 | SN2
52.2 | SN2
53.3 | SN2
54 | SN2
53.8 | SN2
53.8 | SN2
53.4 | SN2
53.2 | SN2
53.6 | SN2
53.4 | SN2
53.2 | SN2
53.3 | SN2
53.1 | SN2
53.1 | SN2
52.8 | SN2
52.3 | SN2
52 | SN2
51.9 | SN2
51.5 | SN2
51.1 | SN2
50.9 | SN2
51 | SN2
50.9 | SN2
50.8 | SN2
51 | SN2
50.9 | SN2
50.8 | SN2
50.8 | SN2
50.8 | SN2
50.5 | SN2
50.6 | SN2
50.5 | SN2
50.4 | SN2
50.4 | SN2
50.5 | SN2
50.3 | SN2
50.4 | SN2
50 | SN2
50 | SN2
49.9 | SN2
50.3 | SN2
50.1 | SN2
49.8 | SN2
50.1 | SN2
50.3 | SN2
50.8 | SN2
51 | SN2
51.9 | SN2
52.7 | SN2
53.2 | SN2
53.9 | SN2
53.9 | SN2
54.3 | SN2
54 | SN2
54.7 | SN2
54.8 | SN2
54.7 | SN2
54.6 | SN2
54.4 | SN2
54.6 | SN2
53.7 | SN2
53.2 | SN2
52.3 | SN2
51.5 | SN2
51.4 | SN2
50.8 | SN2
51 | SN2
51.2 | SN2
51 | SN2
51.3 | SN2
51.1 | SN2
51.2 | SN2
51.5 | SN2
51 | SN2
55.3 | SN2
55.9 | SN2
55.9 | SN2
56.1 | SN2
55.8 | SN2
56 | SN2
55.8 | SN2
55.9 | SN2
55.8 | SN2
56.1 | SN2
56.1 | SN2
55.5 | SN2
55.7 | SN2
55.8 | SN2
55.5 | SN2
56.1 | SN2
55.7 | SN2
56.9 | SN2
53.5 | SN2
54.3 | SN2
54.6 | SN2
54.9 | SN2
54.4 | SN2
54.7 | SN2
54.9 | SN2
55.1 | SN2
55 | SN2
55.1 | SN2
54.8 | SN2
54.8 | SN2
54.4 | SN2
54 | SN2
53 | SN2
53.2 | SN2
52.8 | SN2
52.5 | SN2
52 | SN2
52 | SN2
51.6 | SN2
51.6 | SN2
51 | SN2
51.3 | SN2
51.9 | SN2
51.9 | SN2
51.7 | SN2
51.5 | SN2
51.9 | SN2
51.4 | SN2
51.4 | SN2
51.3 | SN2
51.5 | SN2
51.1 | SN2
51.3 | SN2
51.2 | SN2
51.3 | SN2
51 | SN2
51.1 | SN2
50.9 | SN2
51.2 | SN2
51 | SN2
50.9 | SN2
50.8 | SN2
50.7 | SN2
51.3 | SN2
51.7 | SN2
52.4 | SN2
53.3 | SN2
53.8 | SN2
53.7 | SN2
53.6 | SN2
53.9 | SN2
53.7 | SN2
54.3 | SN2
54.3 | SN2
54.4 | SN2
54.1 | SN2
53.9 | SN2
53.5 | SN2
53.5 | SN2
52.9 | SN2
52.5 | SN2
51.8 | SN2
51.8 | SN2
51.4 | SN2
51.4 | SN2
51.1 | SN2
51.2 | SN2
51.2 | SN2
51.4 | SN2
51.3 | SN2
51.3 | SN2
51.3 | SN2
51.3 | SN2
51.1 | SN2
51.2 | SN2
51 | SN2
51.1 | SN2
51 | SN2
50.9 | SN2
50.8 | SN2
50.7 | SN2
50.3 | SN2
50.1 | SN2
49.9 | SN2
50.1 | SN2
50 | SN2
50.1 | SN2
50.3 | SN2
0 | SN2
50.4 | SN2
57.3 | SN2
53.6 | SN2
53.5 | SN2
53.9 | SN2
54 | SN2
54 | SN2
53.8 | SN2
53.9 | SN2
54.7 | SN2
54 | SN2
53.7 | SN2
53.8 | SN2
53.4 | SN2
53.3 | SN2
52.9 | SN2
52.1 | SN2
51.8 | SN2
51.5 | SN2
51.5 | SN2
50.8 | SN2
50.9 | SN2
50.5 | SN2
50.5 | SN2
50.7 | SN2
50.6 | SN2
50.7 | SN2
50.5 | SN2
50.8 | SN2
50.7 | SN2
50.9 | SN2
51 | SN2
50.8 | SN2
50.6 | SN2
50.8 | SN2
50.3 | SN2
50.6 | SN2
50.6 | SN2
50.8 | SN2
50.9 | SN2
50.6 | SN2
50.7 | SN2
50.1 | SN2
50.4 | SN2
49.8 | SN2
50.3 | SN2
50.4 | SN2
50.8 | SN2
50.4 | SN2
51 | SN2
51.5 | SN2
51.1 | SN2
52.8 | SN2
52.4 | SN2
53.1 | SN2
54.1 | SN2
54 | SN2
53.5 | SN2
53.5 | SN2
53.3 | SN2
53.1 | SN2
52.8 | SN2
52.7 | SN2
52.5 | SN2
52.8 | SN2
51.3 | SN2
51.7 | SN2
51.8 | SN2
51.4 | SN2
51.7 | SN2
51.5 | SN2
51.6 | SN2
51.6 | SN2
51.8 | SN2
51.7 | SN2
51.5 | SN2
52.1 | SN2
52.1 | SN2
51.6 | SN2
51.8 | SN2
51.7 | SN2
51.6 | SN2
51.4 | SN2
51.5 | SN2
51.4 | SN2
51.7 | SN2
51.4 | SN2
51.5 | SN2
51.8 | SN2
51.5 | SN2
51.4 | SN2
51.4 | SN2
51.7 | SN2
51.6 | SN2
52 | SN2
52.6 | SN2
52.7 | SN2
52 | SN2
53.5 | SN2
53.6 | SN2
54.2 | SN2
54 | SN2
54 | SN2
54.2 | SN2
53.8 | SN2
53.6 | SN2
53.1 | SN2
52.6 | SN2
52.1 | SN2
52 | SN2
51.8 | SN2
51.8 | SN2
51.2 | SN2
51.3 | SN2
51.4 | SN2
51.2 | SN2
51.6 | SN2
51.7 | SN2
51.2 | SN2
51.8 | SN2
51.3 | SN2
51.5 | SN2
51.3 | SN2
51.5 | SN2
51.2 | SN2
51.4 | SN2
51.2 | SN2
51.4 | SN2
51.1 | SN2
51 | SN2
50.9 | SN2
51.1 | SN2
51.1 | SN2
50.8 | SN2
51 | SN2
50.8 | SN2
50.9 | SN2
51.2 | SN2
51 | SN2
51.5 | SN2
51.6 | SN2
51.9 | SN2
52 | SN2
52.5 | SN2
52.5 | SN2
52.2 | SN2
52.3 | SN2
52.9 | SN2
53.3 | SN2
53.1 | SN2
53 | SN2
52.7 | SN2
52.1 | SN2
51.8 | SN2
51 | SN2
50.5 | SN2
50.5 | SN2
50.4 | SN2
50.4 | SN2
50.5 | SN2
50.6 | SN2
50.5 | SN2
50.3 | SN2
50.3 | SN2
50.5 | SN2
50.4 | SN2
50.5 | SN2
50.5 | SN2
50.3 | SN2
50.5 | SN2
50.3 | SN2
50.1 | SN2
50.2 | SN2
50.2 | SN2
50 | SN2
50.1 | SN2
50 | SN2
49.8 | SN2
49.9 | SN2
49.8 | SN2
49.4 | SN2
49.3 | SN2
49.4 | SN2
49.3 | SN2
49.5 | SN2
49.5 | SN2
49.7 | SN2
52.7 | SN2
56.5 | SN2
56.8 | SN2
52.5 | SN2
52.7 | SN2
53 | SN2
52.6 | SN2
52.9 | SN2
53.8 | SN2
54.1 | SN2
54.2 | SN2
54.6 | SN2
53.5 | SN2
53.4 | SN2
52.7 | SN2
51.8 | SN2
51.3 | SN2
51.3 | SN2
51.1 | SN2
51.4 | SN2
51.4 | SN2
51.4 | SN2
51.3 | SN2
51.3 | SN2
51.4 | SN2
51.2 | SN2
51.3 | SN2
51 | SN2
51.2 | SN2
51.2 | SN2
51.2 | SN2
50.9 | SN2
51 | SN2
50.7 | SN2
50.6 | SN2
50 | SN2
50.3 | SN2
50 | SN2
50.3 | SN2
50.3 | SN2
50 | SN2
50.3 | SN2
50.5 | SN2
50.5 | SN2
50.5 | SN2
51 | SN2
51.5 | SN2
51.6 | SN2
52.2 | SN2
52.5 | SN2
52.7 | SN2
52.5 | SN2
52.4 | SN2
52.8 | SN2
52.9 | SN2
53.4 | SN2
53.2 | SN2
53.3 | SN2
53 | SN2
52.8 | SN2
52.4 | SN2
52.2 | SN2
51.6 | SN2
50.7 | SN2
50.5 | SN2
50.7 | SN2
50.8 | SN2
50.7 | SN2
50.8 | SN2
50.6 | SN2
50.4 | SN2
50.7 | SN2
50.2 | SN2
50.1 | SN2
50.1 | SN2
50.1 | SN2
49.9 | SN2
49.7 | SN2
48.9 | SN2
49.2 | SN2
49.3 | SN2
49.1 | SN2
49 | SN2
48.9 | SN2
49.2 | SN2
48.7 | SN2
49 | SN2
49 | SN2
48.6 | SN2
48.4 | SN2
49.2 | SN2
49.7 | SN2
50.5 | SN2
50.9 | SN2
51.7 | SN2
51.9 | SN2
52.1 | SN2
52 | SN2
52.3 | SN2
52.1 | SN2
52.9 | SN2
53 | SN2
53.3 | SN2
53.6 | SN2
53 | SN2
52.7 | SN2
52.9 | SN2
52.3 | SN2
50.9 | SN2
50.2 | SN2
49.5 | SN2
49.5 | SN2
49.5 | SN2
48.4 | SN2
48 | SN2
48 | SN2
48 | SN2
48.1 | SN2
47.6 | SN2
47.6 | SN2
47.4 | SN2
47.7 | SN2
47.4 | SN2
47.2 | SN2
47.6 | SN2
47.4 | SN2
47.1 | SN2
47 | SN2
46.7 | SN2
46.6 | SN2
46.7 | SN2
46.7 | SN2
47 | SN2
46.9 | SN2
47.3 | SN2
48 | SN2
48 | SN2
48.1 | SN2
48.8 | SN2
49.4 | SN2
49.4 | SN2
50 | SN2
50.3 | SN2
50.1 | SN2
50.4 | SN2
50.7 | SN2
51 | SN2
51.4 | SN2
51.1 | SN2
51 | SN2
50.7 | SN2
50.4 | SN2
50.2 | SN2
49.5 | SN2
52.6 | SN2
51.9 | SN2
51.8 | SN2
51.8 | SN2
52 | SN2
51.8 | SN2
52 | SN2
52 | SN2
51.8 | SN2
51.8 | SN2
52.2 | SN2
51.9 | SN2
52 | SN2
51.8 | SN2
52 | SN2
52.3 | SN2
51.8 | SN2
52.1 | SN2
51.6 | SN2
51.8 | SN2
51.8 | SN2
51.8 | SN2
51.7 | SN2
52.1 | SN2
51.9 | SN2
51.9 | SN2
51.9 | SN2
51.8 | SN2
52.1 | SN2
52 | SN2
52 | SN2
52.2 | SN2
52.1 | SN2
52.7 | SN2
52.9 | SN2
52.5 | SN2
51.8 | SN2
51.9 | SN2
51.3 | SN2
52.1 | SN2
51.9 | SN2
51.6 | SN2
51.7 | SN2
51.8 | SN2
51.7 | SN2
51.7 | SN2
51.4 | SN2
51.6 | SN2
51.1 | SN2
51.3 | SN2
51.2 | SN2
51.1 | SN2
50.6 | SN2
51.4 | SN2
51.1 | SN2
51.1 | SN2
51.1 | SN2
51.1 | SN2
51.3 | SN2
51.3 | SN2
51.1 | SN2
51.1 | SN2
50.7 | SN2
50.9 | SN2
51.1 | SN2
51.2 | SN2
51.3 | SN2
50.9 | SN2
51.2 | SN2
50.8 | SN2
50.9 | SN2
50.9 | SN2
50.6 | SN2
50.9 | SN2
51.1 | SN2
51.2 | SN2
51 | SN2
51.5 | SN2
51.8 | SN2
51.7 | SN2
51.7 | SN2
52 | SN2
51.7 | SN2
52.1 | SN2
52.6 | SN2
52.7 | SN2
53 | SN2
52.8 | SN2
52.9 | SN2
52.5 | SN2
51.7 | SN2
52.1 | SN2
52.1 | SN2
51.4 | SN2
51.6 | SN2
51.2 | SN2
51.2 | SN2
50.8 | SN2
50.8 | SN2
50.9 | SN2
50.8 | SN2
50.8 | SN2
50.4 | SN2
50.7 | SN2
50.7 | SN2
50.4 | SN2
50.4 | SN2
50.6 | SN2
50.5 | SN2
50.4 | SN2
50.1 | SN2
50.5 | SN2
50.2 | SN2
50.2 | SN2
49.8 | SN2
49.9 | SN2
49.7 | SN2
49.6 | SN2
49.6 | SN2
49.5 | SN2
49.7 | SN2
49.9 | SN2
50.2 | SN2
50.4 | SN2
50.8 | SN2
50.6 | SN2
51.2 | SN2
51.5 | SN2
51 | SN2
50.6 | SN2
51 | SN2
51 | SN2
51.9 | SN2
52 | SN2
52 | SN2
51.8 | SN2
51.7 | SN2
51 | SN2
51 | SN2
50.5 | SN2
50.2 | SN2
50 | SN2
50.8 | SN2
50.3 | SN2
50.3 | SN2
50 | SN2
49.9 | SN2
49.7 | SN2
50.1 | SN2
49.9 | SN2
49.7 | SN2
50.2 | SN2
49.8 | SN2
49.9 | SN2
49.9 | SN2
50.3 | SN2
50.3 | SN2
50.1 | SN2
50.4 | SN2
50.6 | SN2
50.8 | SN2
50.9 | SN2
51.1 | SN2
51.4 | SN2
51.1 | SN2
51.2 | SN2
51.4 | SN2
51.9 | SN2
52.8 | SN2
56.3 | SN2
54.2 | SN2
51.9 | SN2
51.4 | SN2
51 | SN2
51.2 | SN2
51 | SN2
51.1 | SN2
49.9 | SN2
49.7 | SN2
49.2 | SN2
48.9 | SN2
48.8 | SN2
48 | SN2
49 | SN2
49.2 | SN2
49.1 | SN2
48.7 | SN2
48.5 | SN2
49 | SN2
48.5 | SN2
48.2 | SN2
48.4 | SN2
48.6 | SN2
48.2 | SN2
48.3 | SN2
48.5 | SN2
48.9 | SN2
48.8 | SN2
48.9 | SN2
49.1 | SN2
49.1 | SN2
48.2 | SN2
49 | SN2
48.9 | SN2
48.6 | SN2
48.7 | SN2
48.6 | SN2
48.5 | SN2
48.4 | SN2
48.1 | SN2
48.2 | SN2
48.4 | SN2
48.4 | SN2
48.9 | SN2
49.2 | SN2
48.8 | SN2
49.2 | SN2
49.4 | SN2
49.5 | SN2
51.4 | SN2
50.5 | SN2
50.6 | SN2
51.2 | SN2
51 | SN2
51 | SN2
51.1 | SN2
51 | SN2
50.9 | SN2
50.8 | SN2
50.4 | SN2
50.2 | SN2
50 | SN2
49.5 | SN2
49 | SN2
48.7 | SN2
48.3 | SN2
48.7 | SN2
48.6 | SN2
48.5 | SN2
48.4 | SN2
48.5 | SN2
48.4 | SN2
48.2 | SN2
48.4 | SN2
48.8 | SN2
48.5 | SN2
48.5 | SN2
48.3 | SN2
48 | SN2
48.1 | SN2
48.2 | SN2
48.1 | SN2
48.1 | SN2
48.1 | SN2
48.2 | SN2
48.3 | SN2
48.2 | SN2
48 | SN2
48.1 | SN2
48.4 | SN2
48.5 | SN2
48.8 | SN2
48.9 | SN2
49.6 | SN2
50.6 | SN2
52.1 | SN2
51.7 | SN2
51.8 | SN2
52.1 | SN2
52.4 | SN2
52.6 | SN2
52.2 | SN2
52 | SN2
52.2 | SN2
52 | SN2
52 | SN2
51.7 | SN2
51.1 | SN2
50.9 | SN2
50.3 | SN2
50.2 | SN2
50.6 | SN2
50.2 | SN2
50.4 | SN2
50.3 | SN2
50.1 | SN2
50.2 | SN2
50.4 | SN2
50.1 | SN2
49.7 | SN2
50.1 | SN2
50.1 | SN2
49.8 | SN2
49.9 | SN2
49.7 | SN2
49.6 | SN2
49.7 | SN2
49.7 | SN2
49.8 | SN2
49.7 | SN2
49.5 | SN2
49.3 | SN2
49.5 | SN2
49.5 | SN2
49.8 | SN2
49.7 | SN2
50.1 | SN2
50.4 | SN2
50.5 | SN2
50.8 | SN2
51.6 | SN2
51.5 | SN2
51.2 | SN2
50.9 | SN2
51.2 | SN2
51 | SN2
51.6 | SN2
51.7 | SN2
51.6 | SN2
51.6 | SN2
51 | SN2
50.6 | SN2
50.4 | SN2
49.9 | SN2
49.7 | SN2
49.6 | SN2
49.7 | SN2
49.6 | SN2
49.2 | SN2
49.1 | SN2
49.3 | SN2
49.4 | SN2
49.4 | SN2
49.3 | SN2
49 | SN2
49.5 | SN2
49.3 | SN2
49.2 | SN2
49.1 | SN2
49.3 | SN2
49.2 | SN2
49.3 | SN2
49.1 | SN2
48.8 | SN2
49.1 | SN2
48.6 | SN2
48.6 | SN2
48.9 | SN2
48.3 | SN2
48.4 | SN2
48.9 | SN2
48.8 | SN2
49.2 | SN2
50.1 | SN2
50.7 | SN2
51.2 | SN2
51.3 | SN2
51 | SN2
51.7 | SN2
52.1 | SN2
52.6 | SN2
52.4 | SN2
52.7 | SN2
52.6 | SN2
52.6 | SN2
52.4 | SN2
52.2 | SN2
51.9 | SN2
51.6 | SN2
51.1 | SN2
51.3 | SN2
51.2 | SN2
51.2 | SN2
50.4 | SN2
50.9 | SN2
50.6 | SN2
50.5 | SN2
50.9 | SN2
50.6 | SN2
50.8 | SN2
50.9 | SN2
51 | SN2
51.7 | SN2
52.3 | SN2
52.4 | SN2
52.4 | SN2
52 | SN2
52.3 | SN2
52.3 | SN2
52.5 | SN2
52.5 | SN2
52.4 | SN2
52 | SN2
51.8 | SN2
52.1 | SN2
52.3 | SN2
52.1 | SN2
52.2 | SN2
52.1 | SN2
52.2 | SN2
51.8 | SN2
51.3 | SN2
51.7 | SN2
51.5 | SN2
51.7 | SN2
51.9 | SN2
51.7 | SN2
51.7 | SN2
51.4 | SN2
51.3 | SN2
51.4 | SN2
51.7 | SN2
51.4 | SN2
51.4 | SN2
51.3 | SN2
51.3 | SN2
51.5 | SN2
51 | SN2
51.7 | SN2
51.4 | SN2
51 | SN2
52.3 | SN2
52.4 | SN2
52.4 | SN2
52.6 | SN2
52.5 | SN2
52.8 | SN2
52.7 | SN2
53.1 | SN2
53.8 | SN2
53.8 | SN2
54.1 | SN2
54.5 | SN2
54.8 | SN2
54.5 | SN2
54.2 | SN2
53.9 | SN2
54 | SN2
54.2 | SN2
54 | SN2
53.9 | SN2
53.9 | SN2
53.6 | SN2
53.6 | SN2
53.6 | SN2
53.2 | SN2
53.4 | SN2
53.4 | SN2
53.1 | SN2
53.4 | SN2
53.3 | SN2
53.1 | SN2
53.4 | SN2
53.1 | SN2
53 | SN2
53.2 | SN2
53.2 | SN2
53.2 | SN2
53.2 | SN2
53.3 | SN2
53.1 | SN2
53.3 | SN2
53.5 | SN2
53.4 | SN2
53.2 | SN2
52.9 | SN2
53.2 | SN2
53.1 | SN2
52.8 | SN2
53 | SN2
53.3 | SN2
53 | SN2
53.2 | SN2
53.1 | SN2
53.7 | SN2
53.9 | SN2
54 | SN2
55 | SN2
54.6 | SN2
55.1 | SN2
54.5 | SN2
55 | SN2
55 | SN2
55.9 | SN2
55 | SN2
54.8 | SN2
55.5 | SN2
55.1 | SN2
55.1 | SN2
54.1 | SN2
53.1 | SN2
52.3 | SN2
52.8 | SN2
53 | SN2
52.4 | SN2
53.2 | SN2
53.7 | SN2
54 | SN2
54.5 | SN2
54.4 | SN2
54.5 | SN2
54.3 | SN2
54.1 | SN2
54.6 | SN2
54.1 | SN2
54.1 | SN2
53.9 | SN2
53.9 | SN2
54 | SN2
53.6 | SN2
53.7 | SN2
53.7 | SN2
53.6 | SN2
53.4 | SN2
53.6 | SN2
53.3 | SN2
53.4 | SN2
53 | SN2
53.3 | SN2
53.5 | SN2
53.9 | SN2
54.2 | SN2
54.9 | SN2
55.4 | SN2
55.2 | SN2
54.8 | SN2
55.1 | SN2
55.1 | SN2
55.3 | SN2
55.4 | SN2
55.1 | SN2
55.1 | SN2
54.6 | SN2
54.9 | SN2
54.4 | SN2
54.4 | SN2
53.9 | SN2
53.6 | SN2
53 | SN2
53 | SN2
52.4 | SN2
52.4 | SN2
52.5 | SN2
52.1 | SN2
52.5 | SN2
52.6 | SN2
52.2 | SN2
52.6 | SN2
52.4 | SN2
52.2 | SN2
51.8 | SN2
52.3 | SN2
52.1 | SN2
52.3 | SN2
52.2 | SN2
51.8 | SN2
52.4 | SN2
52 | SN2
52 | SN2
52 | SN2
51.9 | SN2
51.8 | SN2
51.8 | SN2
51.5 | SN2
51.3 | SN2
51.5 | SN2
51.9 | SN2
52 | SN2
52.6 | SN2
52.8 | SN2
53.4 | SN2
54.1 | SN2
54.1 | SN2
54.2 | SN2
54.4 | SN2
54.7 | SN2
54.1 | SN2
54.3 | SN2
53.5 | SN2
53.4 | SN2
53.5 | SN2
53.3 | SN2
53.2 | SN2
53 | SN2
53 | SN2
52.2 | SN2
52 | SN2
51.9 | SN2
51.6 | SN2
51.6 | SN2
51.4 | SN2
51.7 | SN2
51.8 | SN2
51.6 | SN2
51.3 | SN2
51.5 | SN2
51.1 | SN2
51.3 | SN2
51.3 | SN2
51.5 | SN2
51.4 | SN2
51.3 | SN2
51.3 | SN2
51.1 | SN2
51.4 | SN2
51.3 | SN2
51 | SN2
50.9 | SN2
51.2 | SN2
50.9 | SN2
51.2 | SN2
51.1 | SN2
51.2 | SN2
51.1 | SN2
51.7 | SN2
52.4 | SN2
52.6 | SN2
52.8 | SN2
53.6 | SN2
54.7 | SN2
54.8 | SN2
55.1 | SN2
54.9 | SN2
54.4 | SN2
53.9 | SN2
54 | SN2
53.6 | SN2
53.4 | SN2
53.5 | SN2
53.1 | SN2
53 | SN2
52.6 | SN2
52.4 | SN2
52.1 | SN2
52.3 | SN2
52.1 | SN2
51.9 | SN2
51.9 | SN2
52.1 | SN2
51.9 | SN2
52.3 | SN2
52.2 | SN2
52.1 | SN2
52.1 | SN2
52 | SN2
51.9 | SN2
52 | SN2
52.1 | SN2
51.8 | SN2
52 | SN2
51.8 | SN2
51.6 | SN2
51.9 | SN2
51.7 | SN2
51.7 | SN2
51.6 | SN2
51.6 | SN2
51.3 | SN2
51.4 | SN2
52.3 | SN2
52.7 | SN2
53.2 | SN2
54.1 | SN2
54 | SN2
54.6 | SN2
54.9 | SN2
55 | SN2
55.1 | SN2
55 | SN2
55.4 | SN2
54.4 | SN2
54.3 | SN2
53.9 | SN2
53.8 | SN2
53.2 | SN2
53.5 | SN2
53.2 | SN2
53.1 | SN2
53 | SN2
52.5 | SN2
52.2 | SN2
52.6 | SN2
52.4 | SN2
52.2 | SN2
52.4 | SN2
52.2 | SN2
52.1 | SN2
52.1 | SN2
51.8 | SN2
52 | SN2
52.2 | SN2
52 | SN2
52.1 | SN2
51.6 | SN2
51.6 | SN2
51.5 | SN2
51.9 | SN2
51.6 | SN2
51.4 | SN2
51.5 | SN2
51.5 | SN2
51.8 | SN2
51.7 | SN2
51.6 | SN2
51.8 | SN2
51.9 | SN2
52.7 | SN2
53 | SN2
53.2 | SN2
53.3 | SN2
53.9 | SN2
54.2 | SN2
54.4 | SN2
53.9 | SN2
55 | SN2
54.9 | SN2
54.7 | SN2
54.5 | SN2
53.8 | SN2
53.4 | SN2
53.1 | SN2
52.9 | SN2
52.9 | SN2
52.2 | SN2
52.2 | SN2
51.7 | SN2
52 | SN2
52 | SN2
51.9 | SN2
52 | SN2
51.9 | SN2
52.1 | SN2
52.1 | SN2
51.9 | SN2
51.6 | SN2
51.8 | SN2
51.8 | SN2
51.6 | SN2
51.4 | SN2
51.3 | SN2
51.5 | SN2
51.7 | SN2
51.3 | SN2
51.3 | SN2
51.1 | SN2
51.1 | SN2
50.8 | SN2
51 | SN2
51.5 | SN2
51.1 | SN2
51.6 | SN2
51.9 | SN2
52.1 | SN2
52.9 | SN2
52.8 | SN2
53.3 | SN2
54.1 | SN2
54.2 | SN2
54.2 | SN2
54.1 | SN2
54.3 | SN2
54.6 | SN2
54.4 | SN2
54.3 | SN2
53.8 | SN2
54.1 | SN2
53.6 | SN2
53 | SN2
52.9 | SN2
52.8 | SN2
52 | SN2
51.7 | SN2
50.8 | SN2
51.8 | SN2
52.1 | SN2
52.2 | SN2
51.7 | SN2
51.7 | SN2
51.8 | SN2
51.5 | SN2
51.9 | SN2
52 | SN2
51.9 | SN2
51.9 | SN2
52 | SN2
51.7 | SN2
51.6 | SN2
51.6 | SN2
51.6 | SN2
51.3 | SN2
51.1 | SN2
51.3 | SN2
51.1 | SN2
51.4 | SN2
51.5 | SN2
51.3 | SN2
51.5 | SN2
51.9 | SN2
52 | SN2
52.3 | SN2
52.5 | SN2
52.8 | SN2
53.2 | SN2
53.5 | SN2
53.7 | SN2
53.8 | SN2
54.3 | SN2
54.8 | SN2
54.8 | SN2
54.2 | SN2
54.1 | SN2
54.2 | SN2
53.9 | SN2
53.5 | SN2
53.6 | SN2
53.6 | SN2
52.5 | SN2
52.1 | SN2
52 | SN2
52.1 | SN2
52.1 | SN2
51.9 | SN2
52.2 | SN2
51.9 | SN2
51.8 | SN2
52.2 | SN2
52 | SN2
51.7 | SN2
51.9 | SN2
51.9 | SN2
51.8 | SN2
51.5 | SN2
51.1 | SN2
51.1 | SN2
51.2 | SN2
51.2 | SN2
51.3 | SN2
51 | SN2
51.1 | SN2
51.1 | SN2
51.5 | SN2
51 | SN2
51.3 | SN2
51.8 | SN2
51.7 | SN2
52.5 | SN2
52.5 | SN2
53.6 | SN2
54 | SN2
54.6 | SN2
55 | SN2
54.9 | SN2
55.1 | SN2
54.9 | SN2
55.3 | SN2
54.8 | SN2
54.5 | SN2
53.9 | SN2
54.2 | SN2
53.9 | SN2
53.8 | SN2
53.6 | SN2
53.7 | SN2
53.6 | SN2
53.1 | SN2
53 | SN2
52.9 | SN2
52.4 | SN2
52.3 | SN2
52.4 | SN2
52.7 | SN2
52.4 | SN2
52.7 | SN2
52.8 | SN2
52.5 | SN2
52.4 | SN2
52.4 | SN2
52.7 | SN2
52.3 | SN2
52.5 | SN2
52.4 | SN2
52.2 | SN2
52.4 | SN2
52.4 | SN2
52.5 | SN2
52.3 | SN2
52.3 | SN2
52.6 | SN2
52.7 | SN2
52.6 | SN2
53.2 | SN2
53.3 | SN2
53.8 | SN2
54.2 | SN2
54.9 | SN2
55 | SN2
55.1 | SN2
54.8 | SN2
55 | SN2
55.1 | SN2
55.5 | SN2
54.9 | SN2
54.6 | SN2
54.6 | SN2
54.5 | SN2
54.6 | SN2
54.2 | SN2
54.2 | SN2
54 | SN2
53.2 | SN2
53.1 | SN2
52.7 | SN2
53.1 | SN2
53.2 | SN2
53.1 | SN2
52.6 | SN2
53 | SN2
53.1 | SN2
52.5 | SN2
52.4 | SN2
52.8 | SN2
52.9 | SN2
52.4 | SN2
52.3 | SN2
52.5 | SN2
52.3 | SN2
52.3 | SN2
52.2 | SN2
52.1 | SN2
51.9 | SN2
51.9 | SN2
51.9 | SN2
52.1 | SN2
52 | SN2
52.3 | SN2
52.6 | SN2
53 | SN2
52.9 | SN2
53.3 | SN2
53.5 | SN2
54.4 | SN2
54.8 | SN2
54.5 | SN2
54.7 | SN2
54.8 | SN2
54.5 | SN2
54.3 | SN2
54.2 | SN2
54.2 | SN2
53.3 | SN2
53.2 | SN2
53 | SN2
52.9 | SN2
52.4 | SN2
52.5 | SN2
52.3 | SN2
52.5 | SN2
52.4 | SN2
52.2 | SN2
52.5 | SN2
51.9 | SN2
51.6 | SN2
51.6 | SN2
52.1 | SN2
52.1 | SN2
52.1 | SN2
52.3 | SN2
52.1 | SN2
52 | SN2
52 | SN2
51.6 | SN2
51.4 | SN2
51.6 | SN2
51.8 | SN2
51.6 | SN2
51.4 | SN2
51.8 | SN2
51.5 | SN2
51.4 | SN2
51.7 | SN2
51.9 | SN2
52 | SN2
52.8 | SN2
52.8 | SN2
52.8 | SN2
52.9 | SN2
53.5 | SN2
53.8 | SN2
54.3 | SN2
54 | SN2
54.3 | SN2
53.9 | SN2
54.1 | SN2
53.7 | SN2
53.3 | SN2
53.4 | SN2
53 | SN2
52.8 | SN2
52.6 | SN2
52.3 | SN2
52.1 | SN2
52.3 | SN2
51.8 | SN2
51.3 | SN2
51.2 | SN2
51.2 | SN2
51.2 | SN2
51.3 | SN2
51.2 | SN2
51 | SN2
50.8 | SN2
50.8 | SN2
50.9 | SN2
50.9 | SN2
50.8 | SN2
50.7 | SN2
50.8 | SN2
51 | SN2
50.8 | SN2
50.6 | SN2
51.1 | SN2
50.8 | SN2
50.1 | SN2
50.7 | SN2
50.2 | SN2
50.5 | SN2
50.7 | SN2
51.6 | SN2
51.2 | SN2
52.5 | SN2
52.6 | SN2
52.7 | SN2
53.3 | SN2
54 | SN2
54.2 | SN2
53.9 | SN2
54.1 | SN2
54.4 | SN2
54.2 | SN2
54 | SN2
53.7 | SN2
53.4 | SN2
53.4 | SN2
52.7 | SN2
52.3 | SN2
52.3 | SN2
52.4 | SN2
52.1 | SN2
52 | SN2
51.5 | SN2
51 | SN2
51.1 | SN2
51.2 | SN2
51.1 | SN2
51.5 | SN2
51.4 | SN2
51.2 | SN2
51.2 | SN2
51.4 | SN2
51 | SN2
50.9 | SN2
50.8 | SN2
50.8 | SN2
50.7 | SN2
50.8 | SN2
50.7 | SN2
50.5 | SN2
50.4 | SN2
50.6 | SN2
50.6 | SN2
51.1 | SN2
51.1 | SN2
51.2 | SN2
51.3 | SN2
51.1 | SN2
52.1 | SN2
52.2 | SN2
53.1 | SN2
53.4 | SN2
54.3 | SN2
54.3 | SN2
54.1 | SN2
54.9 | SN2
54.9 | SN2
54.5 | SN2
54.2 | SN2
53.5 | SN2
53.6 | SN2
53.6 | SN2
53.2 | SN2
52.6 | SN2
52.6 | SN2
52.6 | SN2
52.2 | SN2
52.2 | SN2
51.7 | SN2
51.6 | SN2
51.9 | SN2
52 | SN2
51.6 | SN2
51.6 | SN2
52.1 | SN2
51.8 | SN2
51.6 | SN2
51.8 | SN2
51.8 | SN2
51.8 | SN2
51.8 | SN2
51.5 | SN2
51.5 | SN2
51.4 | SN2
51.4 | SN2
51.2 | SN2
51.5 | SN2
50.9 | SN2
50.8 | SN2
51.1 | SN2
51 | SN2
51.1 | SN2
51.2 | SN2
51.6 | SN2
52.1 | SN2
52.3 | SN2
52.6 | SN2
53.4 | SN2
53.5 | SN2
53.9 | SN2
54 | SN2
54.2 | SN2
53.8 | SN2
52.8 | SN2
52.8 | SN2
52.3 | SN2
51.4 | SN2
51.2 | SN2
50.8 | SN2
50.5 | SN2
50.8 | SN2
50.5 | SN2
50.3 | SN2
50.2 | SN2
49.6 | SN2
49.8 | SN2
49.7 | SN2
49.7 | SN2
49.4 | SN2
49 | SN2
49.5 | SN2
49.4 | SN2
49.4 | SN2
49.5 | SN2
49.4 | SN2
49.5 | SN2
49.2 | SN2
49.4 | SN2
49.2 | SN2
49 | SN2
49.2 | SN2
49.2 | SN2
49.1 | SN2
49 | SN2
49 | SN2
48.8 | SN2
57.5 | SN2
37.2 | SN2
4.9 | SN2
28.7 | SN2
60.4 | SN2
60.3 | SN2
54.8 | SN2
53.9 | SN2
53.8 | SN2
53.4 | SN2
53 | SN2
53.3 | SN2
53.3 | SN2
52.5 | SN2
52.2 | SN2
52.2 | SN2
51.9 | SN2
51.6 | SN2
51.2 | SN2
51.2 | SN2
50.8 | SN2
51 | SN2
50.7 | SN2
50.4 | SN2
50.1 | SN2
49.9 | SN2
49.7 | SN2
49.4 | SN2
49.4 | SN2
49.2 | SN2
49.4 | SN2
49 | SN2
48.9 | SN2
49.3 | SN2
49.3 | SN2
49.1 | SN2
49.2 | SN2
49 | SN2
48.8 | SN2
48.9 | SN2
48.7 | SN2
48.8 | SN2
48.7 | SN2
48.7 | SN2
48.7 | SN2
48.7 | SN2
48.2 | SN2
48.2 | SN2
49.1 | SN2
49.3 | SN2
49.4 | SN2
50.1 | SN2
50.6 | SN2
50.8 | SN2
51.4 | SN2
50.8 | SN2
51.6 | SN2
51.3 | SN2
51.3 | SN2
51.6 | SN2
50.9 | SN2
51 | SN2
50.6 | SN2
50.4 | SN2
50.3 | SN2
49.8 | SN2
49 | SN2
49.2 | SN2
49.4 | SN2
49.2 | SN2
49.4 | SN2
49.3 | SN2
49.2 | SN2
48.9 | SN2
49 | SN2
48.6 | SN2
48.7 | SN2
48.7 | SN2
49 | SN2
48.9 | SN2
48.8 | SN2
48.9 | SN2
48.6 | SN2
48.6 | SN2
48.4 | SN2
48.6 | SN2
48.4 | SN2
48 | SN2
48.2 | SN2
48.1 | SN2
48.2 | SN2
48.1 | SN2
48.1 | SN2
48.5 | SN2
11 | SN2
12 | SN2
12.1 | SN2
63.4 | SN2
64.5 | SN2
64.2 | SN2
64 | SN2
63.3 | SN2
63.1 | SN2
62.9 | SN2
62.7 | SN2
50.3 | SN2
49.3 | SN2
48.7 | SN2
55.1 | SN2
57.1 | SN2
58.6 | SN2
58.1 | SN2
58.9 | SN2
58.6 | SN2
58.5 | SN2
58.8 | SN2
58.7 | SN2
58.7 | SN2
58.5 | SN2
58.4 | SN2
58.4 | SN2
58.5 | SN2
58.4 | SN2
58.4 | SN2
58.6 | SN2
58.5 | SN2
58.5 | SN2
58.5 | SN2
58.3 | SN2
58.6 | SN2
58.3 | SN2
58.1 | SN2
58.1 | SN2
58.2 | SN2
58.2 | SN2
57.8 | SN2
58 | SN2
58.2 | SN2
58.3 | SN2
58.3 | SN2
58.8 | SN2
59 | SN2
59 | SN2
59.3 | SN2
57.6 | SN2
57.2 | SN2
57.1 | SN2
56.5 | SN2
56.4 | SN2
56.2 | SN2
56.5 | SN2
56 | SN2
55 | SN2
54.4 | SN2
54.2 | SN2
53.9 | SN2
53.6 | SN2
53.3 | SN2
52.8 | SN2
52.4 | SN2
52.1 | SN2
52.2 | SN2
52.1 | SN2
51.7 | SN2
51.3 | SN2
51.5 | SN2
51.4 | SN2
51.6 | SN2
51.1 | SN2
51.1 | SN2
51.4 | SN2
51 | SN2
51.1 | SN2
50.8 | SN2
51 | SN2
50.9 | SN2
50.8 | SN2
50.8 | SN2
50.9 | SN2
50.6 | SN2
51.1 | SN2
50.6 | SN2
50.4 | SN2
50.4 | SN2
50.4 | SN2
50.8 | SN2
50.9 | SN2
51.2 | SN2
51.4 | SN2
51.6 | SN2
52.1 | SN2
52.7 | SN2
52.8 | SN2
52.9 | SN2
53.1 | SN2
53.3 | SN2
53 | SN2
52.8 | SN2
52.7 | SN2
52.4 | SN2
52.2 | SN2
52.3 | SN2
51.8 | SN2
51.6 | SN2
51.6 | SN2
51.6 | SN2
51.2 | SN2
50.7 | SN2
50.2 | SN2
50.2 | SN2
50.2 | SN2
50.2 | SN2
50.7 | SN2
50.1 | SN2
50.8 | SN2
49.9 | SN2
50.4 | SN2
50.4 | SN2
49.7 | SN2
50.1 | SN2
50.4 | SN2
49.9 | SN2
50.8 | SN2
50.2 | SN2
50.2 | SN2
50 | SN2
49.9 | SN2
50 | SN2
49.9 | SN2
50.2 | SN2
50.1 | SN2
50 | SN2
50.4 | SN2
51.1 | SN2
51.4 | SN2
51.4 | SN2
51.9 | SN2
53 | SN2
53.3 | SN2
52.7 | SN2
52.4 | SN2
52.6 | SN2
52.3 | SN2
52.3 | SN2
51.8 | SN2
52 | SN2
52.1 | SN2
51.5 | SN2
51.6 | SN2
51.4 | SN2
51.2 | SN2
51.1 | SN2
50.8 | SN2
50.4 | SN2
50.2 | SN2
50.4 | SN2
49.9 | SN2
50.6 | SN2
50.6 | SN2
51 | SN2
50.6 | SN2
50.6 | SN2
50.7 | SN2
50.6 | SN2
50.1 | SN2
50.3 | SN2
50.5 | SN2
50.7 | SN2
50.5 | SN2
49.7 | SN2
50.3 | SN2
50 | SN2
50.1 | SN2
49.7 | SN2
50 | SN2
49.6 | SN2
49.9 | SN2
49.5 | SN2
50.5 | SN2
50.6 | SN2
51.5 | SN2
0 | SN2
47.6 | SN2
47.6 | SN2
54.3 | SN2
46.3 | SN2
51.5 | SN2
50.5 | SN2
50.9 | SN2
50 | SN2
49.9 | SN2
49.1 | SN2
49 | SN2
48.7 | SN2
48.8 | SN2
48.5 | SN2
48.5 | SN2
47.9 | SN2
48 | SN2
47.7 | SN2
47.6 | SN2
47.2 | SN2
47.5 | SN2
47 | SN2
47.1 | SN2
46.7 | SN2
45.9 | SN2
45.4 | SN2
57.5 | SN2
48.5 | SN2
47.2 | SN2
46.7 | SN2
45.6 | SN2
45.9 | SN2
45.4 | SN2
45.2 | SN2
45.4 | SN2
45.3 | SN2
45.2 | SN2
45.2 | SN2
44.9 | SN2
45 | SN2
45 | SN2
44.9 | SN2
45.5 | SN2
45.2 | SN2
45.8 | SN2
45.7 | SN2
45.9 | SN2
47.6 | SN2
48.5 | SN2
49.2 | SN2
48.8 | SN2
49 | SN2
49.6 | SN2
49.5 | SN2
49.6 | SN2
49.4 | SN2
49 | SN2
49.2 | SN2
49 | SN2
48.5 | SN2
48.1 | SN2
48.2 | SN2
56 | SN2
49.5 | SN2
48.7 | SN2
48 | SN2
47.8 | SN2
47.4 | SN2
46.7 | SN2
53.3 | SN2
48.7 | SN2
47.3 | SN2
46.9 | SN2
46.9 | SN2
46.8 | SN2
46.6 | SN2
46.8 | SN2
46.2 | SN2
46.4 | SN2
45.9 | SN2
46.3 | SN2
45.8 | SN2
46.6 | SN2
46.5 | SN2
46.4 | SN2
46.1 | SN2
46.1 | SN2
45.5 | SN2
45.8 | SN2
46.8 | SN2
46.4 | SN2
49.5 | SN2
47.7 | SN2
48.1 | SN2
48.9 | SN2
49.9 | SN2
50.2 | SN2
50.4 | SN2
50.5 | SN2
50.4 | SN2
50.5 | SN2
50.1 | SN2
50.1 | SN2
49.5 | SN2
49.8 | SN2
49 | SN2
48.8 | SN2
48.7 | SN2
48.7 | SN2
48.6 | SN2
48.4 | SN2
48.1 | SN2
47.6 | SN2
47.8 | SN2
47.5 | SN2
47.6 | SN2
47.7 | SN2
47.8 | SN2
47.5 | SN2
47 | SN2
47.6 | SN2
47.9 | SN2
47.2 | SN2
47.6 | SN2
46.8 | SN2
47 | SN2
46.9 | SN2
47 | SN2
46.8 | SN2
46.9 | SN2
46.8 | SN2
46.7 | SN2
46.9 | SN2
46.7 | SN2
47.1 | SN2
47 | SN2
47.6 | SN2
48.1 | SN2
49 | SN2
49.3 | SN2
49.2 | SN2
50.6 | SN2
51.3 | SN2
50.7 | SN2
51.5 | SN2
51.7 | SN2
51.7 | SN2
50.8 | SN2
51 | SN2
51 | SN2
50.9 | SN2
50.6 | SN2
50.6 | SN2
49.7 | SN2
49.9 | SN2
50 | SN2
53.9 | SN2
50.8 | SN2
50.6 | SN2
50 | SN2
50 | SN2
49.6 | SN2
49.9 | SN2
49.7 | SN2
49.3 | SN2
49.6 | SN2
49.1 | SN2
49.2 | SN2
49 | SN2
49 | SN2
49.1 | SN2
48.8 | SN2
48.6 | SN2
48.9 | SN2
48.8 | SN2
51.4 | SN2
50.1 | SN2
49.6 | SN2
49.7 | SN2
49.1 | SN2
48.9 | SN2
49.7 | SN2
50 | SN2
50.1 | SN2
50.9 | SN2
51.1 | SN2
50.9 | SN2
51.8 | SN2
52.1 | SN2
51.9 | SN2
51.8 | SN2
51.7 | SN2
51.8 | SN2
51.7 | SN2
51.8 | SN2
51.1 | SN2
51.2 | SN2
50.9 | SN2
50.5 | SN2
50.5 | SN2
50.4 | SN2
50.3 | SN2
49.8 | SN2
49.8 | SN2
49.4 | SN2
49.4 | SN2
48.9 | SN2
49 | SN2
49.1 | SN2
49.4 | SN2
48.9 | SN2
49.2 | SN2
49 | SN2
48.5 | SN2
48.9 | SN2
49.2 | SN2
49.1 | SN2
49.2 | SN2
49.1 | SN2
48.4 | SN2
48.6 | SN2
48.3 | SN2
48.4 | SN2
48.2 | SN2
48 | SN2
48.4 | SN2
48.3 | SN2
48.6 | SN2
48.4 | SN2
49.1 | SN2
48.9 | SN2
50 | SN2
50.2 | SN2
50.6 | SN2
51.2 | SN2
51.2 | SN2
51.3 | SN2
51.6 | SN2
51.7 | SN2
51.8 | SN2
51.5 | SN2
51.4 | SN2
51.3 | SN2
51.4 | SN2
53.1 | SN2
51.3 | SN2
50.7 | SN2
50.6 | SN2
50.5 | SN2
50.3 | SN2
50.4 | SN2
50 | SN2
49.6 | SN2
49.3 | SN2
48.9 | SN2
49 | SN2
51.6 | SN2
50.3 | SN2
50.1 | SN2
49.8 | SN2
49.2 | SN2
49 | SN2
48.8 | SN2
48.6 | SN2
48.7 | SN2
48.7 | SN2
48.7 | SN2
48.5 | SN2
48.6 | SN2
48.3 | SN2
48.6 | SN2
48.3 | SN2
48.6 | SN2
47.8 | SN2
48.5 | SN2
48.9 | SN2
49.9 | SN2
50 | SN2
50.4 | SN2
50.8 | SN2
51.8 | SN2
52.6 | SN2
55.9 | SN2
53.9 | SN2
53.4 | SN2
52.1 | SN2
52.8 | SN2
52.1 | SN2
52.3 | SN2
52.1 | SN2
51.7 | SN2
51.8 | SN2
53.6 | SN2
50.8 | SN2
49.7 | SN2
49.7 | SN2
49.4 | SN2
49.3 | SN2
48.9 | SN2
49 | SN2
48.8 | SN2
48.8 | SN2
48.7 | SN2
48.6 | SN2
48.3 | SN2
48.2 | SN2
47.9 | SN2
48 | SN2
48 | SN2
47.8 | SN2
47.7 | SN2
48 | SN2
47.4 | SN2
47.6 | SN2
47.9 | SN2
47.7 | SN2
47.3 | SN2
47.5 | SN2
48 | SN2
47.8 | SN2
48.4 | SN2
48.3 | SN2
49 | SN2
49.1 | SN2
49.7 | SN2
50.6 | SN2
51.5 | SN2
51.6 | SN2
51.8 | SN2
52.5 | SN2
52.7 | SN2
53.2 | SN2
52.9 | SN2
52.9 | SN2
56.7 | SN2
52.7 | SN2
52.5 | SN2
51.5 | SN2
51.2 | SN2
51 | SN2
50.8 | SN2
50.2 | SN2
49.5 | SN2
49.4 | SN2
49.1 | SN2
49.1 | SN2
49 | SN2
48.9 | SN2
48.8 | SN2
48.6 | SN2
48.5 | SN2
48.6 | SN2
48.7 | SN2
48.5 | SN2
48.7 | SN2
48.1 | SN2
48.5 | SN2
48.2 | SN2
48 | SN2
48.2 | SN2
47.9 | SN2
47.8 | SN2
47.7 | SN2
47.9 | SN2
47.7 | SN2
47.9 | SN2
48.4 | SN2
49 | SN2
49.5 | SN2
50.6 | SN2
50.8 | SN2
51.2 | SN2
53.4 | SN2
52.5 | SN2
52.6 | SN2
52.9 | SN2
53.2 | SN2
53.7 | SN2
52.9 | SN2
53.3 | SN2
53.5 | SN2
53.6 | SN2
52.6 | SN2
52.4 | SN2
52.5 | SN2
52.5 | SN2
52.2 | SN2
52 | SN2
51.7 | SN2
51.5 | SN2
51.2 | SN2
51.4 | SN2
51 | SN2
51 | SN2
51 | SN2
51.1 | SN2
51.4 | SN2
51.4 | SN2
50.9 | SN2
50.9 | SN2
51 | SN2
50.7 | SN2
50.8 | SN2
50.5 | SN2
51 | SN2
50.7 | SN2
50.7 | SN2
50.9 | SN2
50.6 | SN2
50.8 | SN2
50.4 | SN2
50.7 | SN2
58.9 | SN2
53.3 | SN2
53.3 | SN2
53.2 | SN2
53.6 | SN2
53.9 | SN2
54.3 | SN2
54.2 | SN2
54.2 | SN2
54.1 | SN2
54.1 | SN2
53.1 | SN2
53.2 | SN2
53 | SN2
52.9 | SN2
52.4 | SN2
52.4 | SN2
51.9 | SN2
51.9 | SN2
51.6 | SN2
51.7 | SN2
51.2 | SN2
51.3 | SN2
51.1 | SN2
51.3 | SN2
50.9 | SN2
50.6 | SN2
50.3 | SN2
50.2 | SN2
50.6 | SN2
50.2 | SN2
50.1 | SN2
50.1 | SN2
50.3 | SN2
50.5 | SN2
50.5 | SN2
50.5 | SN2
50.4 | SN2
50.2 | SN2
49.6 | SN2
50.1 | SN2
49.4 | SN2
49.6 | SN2
49.8 | SN2
49.6 | SN2
49.8 | SN2
49.9 | SN2
48.9 | SN2
48.5 | SN2
48.1 | SN2
47.6 | SN2
48.4 | SN2
48.2 | SN2
48 | SN2
47.7 | SN2
52.7 | SN2
56.7 | SN2
56.5 | SN2
56.1 | SN2
55.6 | SN2
55.4 | SN2
54.6 | SN2
54.6 | SN2
54.1 | SN2
54.4 | SN2
53.9 | SN2
53.9 | SN2
53.7 | SN2
53.7 | SN2
53.2 | SN2
53.1 | SN2
52.9 | SN2
52.6 | SN2
52.8 | SN2
52.4 | SN2
52.2 | SN2
52.5 | SN2
52.5 | SN2
52.5 | SN2
52.4 | SN2
52.5 | SN2
52.4 | SN2
52 | SN2
52.1 | SN2
51.8 | SN2
51.7 | SN2
52 | SN2
52 | SN2
51.9 | SN2
52.1 | SN2
51.9 | SN2
51.8 | SN2
52.5 | SN2
52.7 | SN2
57.2 | SN2
58.6 | SN2
53.7 | SN2
53 | SN2
53.6 | SN2
53.3 | SN2
53.3 | SN2
52.9 | SN2
52.8 | SN2
53.5 | SN2
52.8 | SN2
52.2 | SN2
51.8 | SN2
51.8 | SN2
51.7 | SN2
51.2 | SN2
51.1 | SN2
51.1 | SN2
51 | SN2
50.6 | SN2
50.6 | SN2
50.5 | SN2
49.9 | SN2
50.2 | SN2
50.3 | SN2
50 | SN2
50.1 | SN2
50.3 | SN2
50.1 | SN2
49.5 | SN2
49.4 | SN2
49.5 | SN2
50 | SN2
49.5 | SN2
49 | SN2
49.5 | SN2
49.2 | SN2
49.2 | SN2
49.1 | SN2
49 | SN2
49 | SN2
49.1 | SN2
49.1 | SN2
48.8 | SN2
48.9 | SN2
49.9 | SN2
50 | SN2
50.3 | SN2
50.9 | SN2
51.7 | SN2
51.8 | SN2
51.6 | SN2
52.2 | SN2
51.7 | SN2
51.9 | SN2
51 | SN2
51.4 | SN2
51.5 | SN2
51 | SN2
51.2 | SN2
51.3 | SN2
50.5 | SN2
50.5 | SN2
50 | SN2
50.3 | SN2
50.1 | SN2
50.4 | SN2
49.9 | SN2
50.1 | SN2
49.9 | SN2
50 | SN2
49.7 | SN2
49.6 | SN2
49.4 | SN2
49.5 | SN2
49.2 | SN2
49.3 | SN2
49.2 | SN2
49.3 | SN2
49.1 | SN2
49.1 | SN2
48.9 | SN2
49.3 | SN2
49 | SN2
49 | SN2
49 | SN2
49.1 | SN2
49.4 | SN2
49 | SN2
48.9 | SN2
49.6 | SN2
49.6 | SN2
49.2 | SN2
50 | SN2
50.4 | SN2
50.9 | SN2
50.9 | SN2
50.6 | SN2
50.9 | SN2
50.8 | SN2
50.8 | SN2
51.3 | SN2
51 | SN2
50.9 | SN2
51.2 | SN2
51 | SN2
51.1 | SN2
50.9 | SN2
50.8 | SN2
50.5 | SN2
50.3 | SN2
50 | SN2
50.1 | SN2
49.6 | SN2
49.9 | SN2
49.8 | SN2
49.4 | SN2
49.1 | SN2
48.6 | SN2
48.8 | SN2
49.1 | SN2
49.1 | SN2
49.4 | SN2
49.1 | SN2
48.8 | SN2
48.8 | SN2
49 | SN2
49 | SN2
48.9 | SN2
48.6 | SN2
48.7 | SN2
48.1 | SN2
48.2 | SN2
48.3 | SN2
48.4 | SN2
48.9 | SN2
49.8 | SN2
49.7 | SN2
50.1 | SN2
50.4 | SN2
50.5 | SN2
51.9 | SN2
51.5 | SN2
51.9 | SN2
52.1 | SN2
51.7 | SN2
51.5 | SN2
51.9 | SN2
52.3 | SN2
52.2 | SN2
51.9 | SN2
51.5 | SN2
51 | SN2
50.8 | SN2
50.2 | SN2
50.8 | SN2
50.4 | SN2
49.7 | SN2
50.3 | SN2
50 | SN2
49.7 | SN2
49.9 | SN2
49.7 | SN2
49.9 | SN2
49.7 | SN2
49.4 | SN2
49.1 | SN2
49.4 | SN2
49.2 | SN2
49.2 | SN2
49 | SN2
49.1 | SN2
49.1 | SN2
49.5 | SN2
49.7 | SN2
49.4 | SN2
49.3 | SN2
49.1 | SN2
48.8 | SN2
48.6 | SN2
49.1 | SN2
48.9 | SN2
49.4 | SN2
49.3 | SN2
49.7 | SN2
50.2 | SN2
50.6 | SN2
51 | SN2
51.2 | SN2
51.6 | SN2
51.6 | SN2
51.3 | SN2
51.4 | SN2
51.1 | SN2
51.8 | SN2
51.8 | SN2
51.4 | SN2
51.7 | SN2
51.2 | SN2
51.1 | SN2
50.1 | SN2
50.7 | SN2
50.6 | SN2
50.4 | SN2
49.7 | SN2
49.7 | SN2
49.5 | SN2
49.3 | SN2
49 | SN2
48.6 | SN2
49.2 | SN2
48.9 | SN2
49 | SN2
48.9 | SN2
49 | SN2
49.2 | SN2
49.2 | SN2
49.1 | SN2
48.7 | SN2
48.6 | SN2
48.9 | SN2
48.7 | SN2
48.1 | SN2
48 | SN2
47.8 | SN2
48.3 | SN2
48.3 | SN2
48.1 | SN2
49 | SN2
49.5 | SN2
49.1 | SN2
49.7 | SN2
50.1 | SN2
50.7 | SN2
50.7 | SN2
51.6 | SN2
51.3 | SN2
51.6 | SN2
51.5 | SN2
51.2 | SN2
51.4 | SN2
51.2 | SN2
51 | SN2
50.8 | SN2
50.6 | SN2
50.2 | SN2
50 | SN2
49.7 | SN2
49.7 | SN2
49 | SN2
49.5 | SN2
49 | SN2
48.4 | SN2
48.7 | SN2
48.3 | SN2
48.2 | SN2
47.8 | SN2
47.7 | SN2
48.4 | SN2
47.7 | SN2
48 | SN2
47.5 | SN2
47.6 | SN2
48.1 | SN2
47.6 | SN2
47.7 | SN2
47.7 | SN2
47.5 | SN2
47.5 | SN2
47.4 | SN2
47.3 | SN2
47.4 | SN2
47.1 | SN2
47.5 | SN2
47.4 | SN2
47.3 | SN2
48.7 | SN2
49.4 | SN2
49.1 | SN2
50.3 | SN2
51 | SN2
51.2 | SN2
51 | SN2
51.2 | SN2
51.1 | SN2
51.3 | SN2
51.2 | SN2
50.9 | SN2
50.5 | SN2
50.2 | SN2
50.1 | SN2
49.9 | SN2
49.8 | SN2
49.2 | SN2
49.2 | SN2
49 | SN2
48.7 | SN2
48.6 | SN2
48.8 | SN2
48.7 | SN2
48.6 | SN2
48.2 | SN2
48.4 | SN2
48 | SN2
48.2 | SN2
48 | SN2
48.1 | SN2
48.2 | SN2
48.2 | SN2
48.2 | SN2
48 | SN2
47.4 | SN2
47.5 | SN2
47.5 | SN2
47.8 | SN2
47.1 | SN2
47.7 | SN2
47.1 | SN2
47.3 | SN2
47.1 | SN2
47.9 | SN2
47.9 | SN2
48.6 | SN2
49 | SN2
49.2 | SN2
49.8 | SN2
50.9 | SN2
51.6 | SN2
51.5 | SN2
51.5 | SN2
52 | SN2
52.1 | SN2
52.1 | SN2
51.7 | SN2
51.7 | SN2
53.1 | SN2
51.7 | SN2
49.6 | SN2
48.5 | SN2
47.9 | SN2
47.2 | SN2
47.6 | SN2
47.2 | SN2
46.6 | SN2
46.5 | SN2
46.6 | SN2
46.1 | SN2
46 | SN2
45.8 | SN2
45.8 | SN2
45.9 | SN2
45.7 | SN2
45.2 | SN2
46.3 | SN2
45.9 | SN2
45.1 | SN2
46.2 | SN2
45.8 | SN2
45.7 | SN2
45.6 | SN2
45.7 | SN2
45 | SN2
45.3 | SN2
45.5 | SN2
45.5 | SN2
45.4 | SN2
45.1 | SN2
45.7 | SN2
45.7 | SN2
45.9 | SN2
46 | SN2
47.1 | SN2
48.3 | SN2
49.7 | SN2
51.9 | SN2
53.3 | SN2
52.6 | SN2
52.1 | SN2
52.4 | SN2
52.3 | SN2
52.2 | SN2
52.2 | SN2
51.3 | SN2
51.2 | SN2
50.8 | SN2
51 | SN2
50.8 | SN2
50.4 | SN2
50.8 | SN2
50.4 | SN2
50.4 | SN2
50.5 | SN2
49.9 | SN2
50.2 | SN2
50.1 | SN2
49.9 | SN2
49.9 | SN2
49.5 | SN2
50 | SN2
50.2 | SN2
49.7 | SN2
49.9 | SN2
49.9 | SN2
49.9 | SN2
49.7 | SN2
49.4 | SN2
49.9 | SN2
49.6 | SN2
49.4 | SN2
49.5 | SN2
49.6 | SN2
49.9 | SN2
49.5 | SN2
49.6 | SN2
49.8 | SN2
50.3 | SN2
50.5 | SN2
50.8 | SN2
51 | SN2
51.8 | SN2
52 | SN2
52 | SN2
52 | SN2
52.2 | SN2
51.8 | SN2
51.1 | SN2
51.3 | SN2
50.6 | SN2
51.1 | SN2
50.2 | SN2
50.1 | SN2
50.5 | SN2
50.2 | SN2
50.5 | SN2
50.5 | SN2
50.5 | SN2
50.4 | SN2
50.5 | SN2
50.7 | SN2
50.1 | SN2
50.1 | SN2
49.9 | SN2
50 | SN2
49.9 | SN2
49.9 | SN2
49.7 | SN2
49.7 | SN2
50 | SN2
49.9 | SN2
49.7 | SN2
49.9 | SN2
49.7 | SN2
49.9 | SN2
49.7 | SN2
49.6 | SN2
49.8 | SN2
49.5 | SN2
49.7 | SN2
49.6 | SN2
49.6 | SN2
49.7 | SN2
50 | SN2
50.6 | SN2
51.1 | SN2
51.3 | SN2
51.7 | SN2
51.6 | SN2
52.1 | SN2
51.9 | SN2
52 | SN2
51.9 | SN2
52.1 | SN2
50.8 | SN2
50.6 | SN2
50.7 | SN2
50.5 | SN2
50.4 | SN2
50.5 | SN2
50.2 | SN2
50.4 | SN2
50.3 | SN2
50.4 | SN2
50.3 | SN2
50.5 | SN2
50.4 | SN2
50.3 | SN2
50.6 | SN2
50.2 | SN2
50 | SN2
49.8 | SN2
49.9 | SN2
49.8 | SN2
49.9 | SN2
49.9 | SN2
49.7 | SN2
49.8 | SN2
50 | SN2
49.3 | SN2
49.7 | SN2
49.3 | SN2
49.2 | SN2
49.4 | SN2
49.2 | SN2
49.5 | SN2
49.4 | SN2
49.6 | SN2
49.8 | SN2
49.8 | SN2
50.4 | SN2
51.1 | SN2
51.7 | SN2
51.7 | SN2
51.9 | SN2
51.8 | SN2
52 | SN2
51.6 | SN2
51.8 | SN2
51.9 | SN2
51.4 | SN2
51.5 | SN2
51.3 | SN2
51.1 | SN2
50.5 | SN2
50.6 | SN2
51 | SN2
50.5 | SN2
50.3 | SN2
50.9 | SN2
50.7 | SN2
50.5 | SN2
50.6 | SN2
50.2 | SN2
50.5 | SN2
50.2 | SN2
49.9 | SN2
49.9 | SN2
49.8 | SN2
49.6 | SN2
49.9 | SN2
49.9 | SN2
49.7 | SN2
49.8 | SN2
49.6 | SN2
49.8 | SN2
49.4 | SN2
49.6 | SN2
49.2 | SN2
49.5 | SN2
49.6 | SN2
49.4 | SN2
49.9 | SN2
49.1 | SN2
49.4 | SN2
49.9 | SN2
50.2 | SN2
51.1 | SN2
52 | SN2
52.5 | SN2
52.5 | SN2
52.4 | SN2
53.2 | SN2
52.9 | SN2
52.8 | SN2
52.7 | SN2
52.7 | SN2
51.7 | SN2
52 | SN2
51.8 | SN2
51.7 | SN2
51.4 | SN2
51.1 | SN2
51.2 | SN2
50.9 | SN2
51.3 | SN2
50.9 | SN2
51 | SN2
50.6 | SN2
51.3 | SN2
51.1 | SN2
51.3 | SN2
51.1 | SN2
51.2 | SN2
51.2 | SN2
50.7 | SN2
50.8 | SN2
50.5 | SN2
50.4 | SN2
50.8 | SN2
50.6 | SN2
50.8 | SN2
50.6 | SN2
50.6 | SN2
50.5 | SN2
50.3 | SN2
50.1 | SN2
50.4 | SN2
50.2 | SN2
51.1 | SN2
50.8 | SN2
51.1 | SN2
51.5 | SN2
51.7 | SN2
52.2 | SN2
52.4 | SN2
52.6 | SN2
53.2 | SN2
52.7 | SN2
52.8 | SN2
53.1 | SN2
52.9 | SN2
52.9 | SN2
52.4 | SN2
52.5 | SN2
52.8 | SN2
51.8 | SN2
52.1 | SN2
52 | SN2
51.9 | SN2
52 | SN2
51.7 | SN2
51.7 | SN2
51.9 | SN2
51.3 | SN2
51.2 | SN2
51.2 | SN2
51.6 | SN2
50.9 | SN2
50.9 | SN2
50.8 | SN2
50.7 | SN2
51 | SN2
51.2 | SN2
51.2 | SN2
51.1 | SN2
50.8 | SN2
51.1 | SN2
50.7 | SN2
50.6 | SN2
50.3 | SN2
50.7 | SN2
50.6 | SN2
50.4 | SN2
51 | SN2
50.5 | SN2
51.1 | SN2
51.2 | SN2
51.7 | SN2
52 | SN2
52.2 | SN2
52.9 | SN2
52.8 | SN2
52.1 | SN2
52.7 | SN2
53 | SN2
52.4 | SN2
52.3 | SN2
52.3 | SN2
52.2 | SN2
52.2 | SN2
52 | SN2
52 | SN2
51.7 | SN2
51.6 | SN2
51.6 | SN2
51.7 | SN2
51.4 | SN2
51.1 | SN2
51.5 | SN2
51.4 | SN2
51.2 | SN2
50.8 | SN2
50.9 | SN2
51.1 | SN2
50.8 | SN2
51.2 | SN2
50.7 | SN2
50.8 | SN2
50.3 | SN2
50.3 | SN2
50.5 | SN2
50.4 | SN2
50.6 | SN2
50.3 | SN2
50.6 | SN2
50.5 | SN2
50.5 | SN2
50.4 | SN2
50.4 | SN2
50 | SN2
50.5 | SN2
50.8 | SN2
51 | SN2
51.5 | SN2
51.8 | SN2
52.3 | SN2
52.5 | SN2
52.4 | SN2
52.6 | SN2
52.4 | SN2
52.2 | SN2
52.2 | SN2
52.6 | SN2
52 | SN2
52.1 | SN2
52.1 | SN2
51.8 | SN2
51.6 | SN2
51.7 | SN2
51.7 | SN2
51.8 | SN2
51.5 | SN2
51.3 | SN2
51.5 | SN2
51.3 | SN2
51.1 | SN2
51.2 | SN2
51.3 | SN2
51.2 | SN2
51.3 | SN2
51.1 | SN2
51.1 | SN2
51.1 | SN2
50.7 | SN2
50.7 | SN2
50.6 | SN2
50.9 | SN2
50.6 | SN2
50.4 | SN2
50.6 | SN2
50.5 | SN2
50.4 | SN2
50.4 | SN2
50.6 | SN2
50.7 | SN2
50.8 | SN2
51 | SN2
51.5 | SN2
51.4 | SN2
52 | SN2
51.9 | SN2
52.2 | SN2
52.3 | SN2
52.4 | SN2
52.8 | SN2
52.3 | SN2
52.3 | SN2
52.2 | SN2
52.2 | SN2
51.7 | SN2
51.9 | SN2
51.6 | SN2
51.8 | SN2
51.7 | SN2
51.6 | SN2
52 | SN2
51.6 | SN2
51.2 | SN2
51.4 | SN2
51.1 | SN2
51.1 | SN2
50.9 | SN2
51.1 | SN2
51.1 | SN2
51 | SN2
51 | SN2
50.7 | SN2
50.7 | SN2
50.8 | SN2
50.8 | SN2
50.6 | SN2
50 | SN2
50.2 | SN2
50.7 | SN2
50.5 | SN2
50.5 | SN2
50.3 | SN2
50.4 | SN2
50.6 | SN2
50.6 | SN2
50.6 | SN2
50.8 | SN2
50.9 | SN2
50.8 | SN2
51 | SN2
51.5 | SN2
51.8 | SN2
52 | SN2
52.8 | SN2
53 | SN2
53.2 | SN2
52.6 | SN2
52.4 | SN2
52.2 | SN2
52.6 | SN2
52.6 | SN2
52.2 | SN2
52 | SN2
52.1 | SN2
52 | SN2
51.5 | SN2
51.2 | SN2
51.4 | SN2
50.9 | SN2
51.2 | SN2
50.8 | SN2
51.2 | SN2
51 | SN2
50.9 | SN2
50.8 | SN2
50.9 | SN2
50.3 | SN2
50.3 | SN2
50.6 | SN2
50.3 | SN2
50.4 | SN2
50.5 | SN2
50.3 | SN2
50.3 | SN2
50.4 | SN2
50.4 | SN2
50.2 | SN2
50.2 | SN2
50.2 | SN2
50.6 | SN2
50.2 | SN2
50.3 | SN2
50.5 | SN2
50.9 | SN2
51.1 | SN2
51.4 | SN2
51.2 | SN2
52.2 | SN2
52.6 | SN2
53.2 | SN2
53.1 | SN2
52.8 | SN2
53 | SN2
52.8 | SN2
52.3 | SN2
52.2 | SN2
52 | SN2
52.4 | SN2
52.5 | SN2
51.9 | SN2
51.6 | SN2
51.3 | SN2
51.2 | SN2
51.1 | SN2
51.3 | SN2
51.2 | SN2
51.2 | SN2
51.3 | SN2
51.1 | SN2
51 | SN2
51.3 | SN2
51.4 | SN2
51.2 | SN2
51 | SN2
50.8 | SN2
50.6 | SN2
50.6 | SN2
50.7 | SN2
50.4 | SN2
50.6 | SN2
50.7 | SN2
50.6 | SN2
50 | SN2
50.5 | SN2
50.7 | SN2
50.5 | SN2
50.5 | SN2
50.3 | SN2
50.7 | SN2
51.1 | SN2
51 | SN2
51.6 | SN2
52.1 | SN2
52.3 | SN2
52.7 | SN2
52.8 | SN2
53 | SN2
52.7 | SN2
52.6 | SN2
52.8 | SN2
52.7 | SN2
52.5 | SN2
52.1 | SN2
51.8 | SN2
52 | SN2
52 | SN2
51.5 | SN2
51.7 | SN2
51.2 | SN2
51.4 | SN2
51.4 | SN2
51.1 | SN2
51 | SN2
51.2 | SN2
51.1 | SN2
51.2 | SN2
51 | SN2
51 | SN2
50.7 | SN2
50.9 | SN2
50.5 | SN2
50.6 | SN2
50.8 | SN2
50.7 | SN2
50.6 | SN2
50.6 | SN2
50.8 | SN2
50.9 | SN2
50.6 | SN2
50.6 | SN2
50.4 | SN2
50.5 | SN2
50.5 | SN2
50.2 | SN2
51 | SN2
51.2 | SN2
51.7 | SN2
51.9 | SN2
51.9 | SN2
52.4 | SN2
52.6 | SN2
54.3 | SN2
53.1 | SN2
53.1 | SN2
52.7 | SN2
52.5 | SN2
52.5 | SN2
52.7 | SN2
51.9 | SN2
51.9 | SN2
52.3 | SN2
51.8 | SN2
51.4 | SN2
51.1 | SN2
51.3 | SN2
50.9 | SN2
50.7 | SN2
50.7 | SN2
50.9 | SN2
51 | SN2
50.9 | SN2
50.9 | SN2
50.9 | SN2
50.8 | SN2
50.9 | SN2
50.7 | SN2
50.8 | SN2
50.6 | SN2
50.8 | SN2
50.5 | SN2
50.1 | SN2
50.5 | SN2
49.9 | SN2
50.3 | SN2
50.2 | SN2
50.2 | SN2
50 | SN2
50 | SN2
50.3 | SN2
49.7 | SN2
50.5 | SN2
50.8 | SN2
51.1 | SN2
51.5 | SN2
51.5 | SN2
51.8 | SN2
52.2 | SN2
52.1 | SN2
52.8 | SN2
52.7 | SN2
52.1 | SN2
52.5 | SN2
52.3 | SN2
52.6 | SN2
52 | SN2
51.9 | SN2
51.7 | SN2
51.5 | SN2
51.5 | SN2
51.1 | SN2
50.9 | SN2
51.1 | SN2
50.8 | SN2
50.9 | SN2
50.9 | SN2
51 | SN2
50.7 | SN2
51 | SN2
51 | SN2
51 | SN2
50.8 | SN2
50.6 | SN2
50.5 | SN2
50.9 | SN2
50.4 | SN2
50.7 | SN2
50.5 | SN2
50.6 | SN2
50.5 | SN2
50.1 | SN2
50.1 | SN2
50 | SN2
50.4 | SN2
50 | SN2
50.1 | SN2
49.9 | SN2
50.2 | SN2
51.1 | SN2
51.6 | SN2
51.3 | SN2
51.8 | SN2
51.8 | SN2
52.1 | SN2
51.8 | SN2
52.7 | SN2
52 | SN2
52.6 | SN2
52.1 | SN2
51.8 | SN2
52.5 | SN2
52.1 | SN2
51.6 | SN2
51.8 | SN2
51.4 | SN2
51.3 | SN2
51.2 | SN2
50.9 | SN2
50.7 | SN2
50.7 | SN2
50.9 | SN2
51 | SN2
51 | SN2
50.6 | SN2
50.6 | SN2
50.7 | SN2
50.4 | SN2
50.3 | SN2
50.3 | SN2
50 | SN2
50.5 | SN2
50.3 | SN2
50 | SN2
50.4 | SN2
50.3 | SN2
50.2 | SN2
50.5 | SN2
50.6 | SN2
50.1 | SN2
50.1 | SN2
50 | SN2
50.4 | SN2
50.1 | SN2
50.3 | SN2
49.9 | SN2
50.7 | SN2
50.5 | SN2
51.5 | SN2
52.1 | SN2
52.1 | SN2
52.2 | SN2
51.6 | SN2
51.7 | SN2
51.6 | SN2
51.8 | SN2
51.5 | SN2
51.7 | SN2
51.5 | SN2
51.4 | SN2
51.2 | SN2
50.6 | SN2
50.7 | SN2
50.6 | SN2
51 | SN2
50.8 | SN2
50.6 | SN2
50.8 | SN2
50.5 | SN2
50.4 | SN2
50.4 | SN2
49.9 | SN2
49.9 | SN2
50.3 | SN2
50.1 | SN2
50.1 | SN2
50.5 | SN2
49.8 | SN2
50.5 | SN2
50 | SN2
50.2 | SN2
50.2 | SN2
50.8 | SN2
50.2 | SN2
50.5 | SN2
50.2 | SN2
50.2 | SN2
50.1 | SN2
50.1 | SN2
49.8 | SN2
50.3 | SN2
49.9 | SN2
50.3 | SN2
50.2 | SN2
50.8 | SN2
51.3 | SN2
51.9 | SN2
52.4 | SN2
52.4 | SN2
52.6 | SN2
52.5 | SN2
52.2 | SN2
51.7 | SN2
51.5 | SN2
51.1 | SN2
51 | SN2
51.3 | SN2
51.4 | SN2
51.4 | SN2
51 | SN2
50.9 | SN2
50.8 | SN2
51 | SN2
50.6 | SN2
50.2 | SN2
50.7 | SN2
50.3 | SN2
50.2 | SN2
50.7 | SN2
50.5 | SN2
50.6 | SN2
50.5 | SN2
50.4 | SN2
50.1 | SN2
50.4 | SN2
50.5 | SN2
50 | SN2
50.2 | SN2
50.1 | SN2
50 | SN2
50.2 | SN2
50.4 | SN2
50.2 | SN2
50.2 | SN2
49.7 | SN2
50.1 | SN2
50.4 | SN2
50.4 | SN2
50.5 | SN2
50.7 | SN2
51.4 | SN2
52.2 | SN2
52.1 | SN2
52.7 | SN2
53.3 | SN2
53.4 | SN2
52.9 | SN2
53 | SN2
53.1 | SN2
52.6 | SN2
56.6 | SN2
55.8 | SN2
54.9 | SN2
54.1 | SN2
53.2 | SN2
52.9 | SN2
51.8 | SN2
51.4 | SN2
50.3 | SN2
50.9 | SN2
51.6 | SN2
51.2 | SN2
51.1 | SN2
51.1 | SN2
50.7 | SN2
50.7 | SN2
51 | SN2
50.7 | SN2
50.6 | SN2
50.4 | SN2
50.3 | SN2
50.2 | SN2
50.5 | SN2
50.4 | SN2
50.4 | SN2
50.4 | SN2
50.3 | SN2
50 | SN2
50.1 | SN2
50.4 | SN2
50 | SN2
49.9 | SN2
50.1 | SN2
50.1 | SN2
50.4 | SN2
50.7 | SN2
50.8 | SN2
57.5 | SN2
52.2 | SN2
52 | SN2
52.3 | SN2
52.5 | SN2
52.8 | SN2
52.8 | SN2
52.3 | SN2
52.8 | SN2
52.5 | SN2
52.1 | SN2
52.6 | SN2
51.8 | SN2
51.7 | SN2
51.4 | SN2
51.2 | SN2
51.1 | SN2
51 | SN2
50.8 | SN2
51 | SN2
50.7 | SN2
51 | SN2
50.5 | SN2
50.6 | SN2
50.2 | SN2
50.2 | SN2
50.4 | SN2
49.9 | SN2
50.2 | SN2
50.2 | SN2
50.4 | SN2
50.7 | SN2
50.2 | SN2
50 | SN2
50.2 | SN2
49.9 | SN2
50 | SN2
49.9 | SN2
51.2 | SN2
50.1 | SN2
50 | SN2
49.9 | SN2
50 | SN2
50.2 | SN2
50.7 | SN2
51.1 | SN2
51.7 | SN2
51.6 | SN2
52 | SN2
52.6 | SN2
52.9 | SN2
54.1 | SN2
54.4 | SN2
54.1 | SN2
54.1 | SN2
54.4 | SN2
53.6 | SN2
53.6 | SN2
53.6 | SN2
53.1 | SN2
53.7 | SN2
53.2 | SN2
53.1 | SN2
53.2 | SN2
52.6 | SN2
52.6 | SN2
52.9 | SN2
52.7 | SN2
52.9 | SN2
52.8 | SN2
53 | SN2
53.2 | SN2
53.2 | SN2
53 | SN2
53.1 | SN2
53.1 | SN2
54.2 | SN2
53.2 | SN2
53.1 | SN2
53.1 | SN2
53.3 | SN2
53.5 | SN2
53.7 | SN2
53.4 | SN2
53.7 | SN2
53.6 | SN2
53.8 | SN2
53.9 | SN2
54.1 | SN2
54.3 | SN2
54.7 | SN2
54.8 | SN2
55 | SN2
55.3 | SN2
54.9 | SN2
54.9 | SN2
55.2 | SN2
55.8 | SN2
56.1 | SN2
55.8 | SN2
55.3 | SN2
55.1 | SN2
55.2 | SN2
55.5 | SN2
55.3 | SN2
54.8 | SN2
55 | SN2
54.9 | SN2
55.1 | SN2
55.1 | SN2
54.8 | SN2
54.5 | SN2
54.6 | SN2
55.3 | SN2
55.6 | SN2
55.2 | SN2
55.5 | SN2
55.5 | SN2
55.7 | SN2
55.9 | SN2
55.7 | SN2
56.1 | SN2
56.1 | SN2
56 | SN2
56.3 | SN2
56.2 | SN2
56.4 | SN2
56.4 | SN2
56.4 | SN2
56.7 | SN2
56.9 | SN2
56.8 | SN2
57 | SN2
57.1 | SN2
57.5 | SN2
54.2 | SN2
54.3 | SN2
53.3 | SN2
52.5 | SN2
52.5 | SN2
52.4 | SN2
52.4 | SN2
52.6 | SN2
52.9 | SN2
52.7 | SN2
52.6 | SN2
52.2 | SN2
52 | SN2
51.6 | SN2
51.6 | SN2
51.1 | SN2
51.1 | SN2
50.7 | SN2
50.6 | SN2
50.2 | SN2
49.9 | SN2
49.7 | SN2
49.6 | SN2
49.7 | SN2
49.8 | SN2
49.8 | SN2
49.6 | SN2
49.6 | SN2
49.8 | SN2
49.4 | SN2
49.4 | SN2
49.8 | SN2
49.7 | SN2
49.7 | SN2
49.7 | SN2
49.4 | SN2
49.5 | SN2
49.8 | SN2
49.6 | SN2
49.6 | SN2
49.9 | SN2
49.5 | SN2
49.2 | SN2
49.3 | SN2
49.3 | SN2
49.5 | SN2
49.5 | SN2
50 | SN2
50.3 | SN2
50 | SN2
50.5 | SN2
50.7 | SN2
51 | SN2
52 | SN2
52.3 | SN2
52.4 | SN2
51.9 | SN2
51.7 | SN2
51.8 | SN2
51.8 | SN2
51.5 | SN2
51.7 | SN2
51.1 | SN2
51 | SN2
50.7 | SN2
51 | SN2
50.6 | SN2
50.6 | SN2
50.6 | SN2
50.2 | SN2
49.9 | SN2
49.6 | SN2
49.4 | SN2
49.5 | SN2
49.9 | SN2
49.3 | SN2
49.6 | SN2
49.5 | SN2
49.5 | SN2
49.5 | SN2
49.2 | SN2
49.6 | SN2
49.7 | SN2
49.8 | SN2
49.3 | SN2
49.1 | SN2
49.1 | SN2
49.2 | SN2
48.6 | SN2
49.1 | SN2
49.1 | SN2
49 | SN2
49.2 | SN2
49.5 | SN2
49.7 | SN2
50.1 | SN2
50.8 | SN2
51.2 | SN2
51.2 | SN2
51.6 | SN2
52.3 | SN2
52.2 | SN2
52.1 | SN2
51.9 | SN2
51.8 | SN2
51.5 | SN2
51.3 | SN2
51 | SN2
51.3 | SN2
51.2 | SN2
50.8 | SN2
51 | SN2
50.6 | SN2
50.5 | SN2
50.2 | SN2
50 | SN2
49.6 | SN2
49.3 | SN2
49.4 | SN2
49.3 | SN2
49.5 | SN2
49.5 | SN2
49.2 | SN2
49.3 | SN2
49.4 | SN2
48.9 | SN2
49.2 | SN2
49.4 | SN2
49 | SN2
48.6 | SN2
49.3 | SN2
48.6 | SN2
49 | SN2
48.2 | SN2
48.6 | SN2
48.7 | SN2
48.6 | SN2
49 | SN2
49.1 | SN2
49.4 | SN2
49.7 | SN2
50.1 | SN2
50.2 | SN2
50.8 | SN2
51.3 | SN2
51.8 | SN2
52.4 | SN2
52.5 | SN2
52.6 | SN2
52.4 | SN2
51.8 | SN2
51.8 | SN2
51.9 | SN2
51.5 | SN2
51.4 | SN2
51.4 | SN2
51 | SN2
50.9 | SN2
50.6 | SN2
50.8 | SN2
50.5 | SN2
50.3 | SN2
50.2 | SN2
49.8 | SN2
49.7 | SN2
49.7 | SN2
49.4 | SN2
49.6 | SN2
49.7 | SN2
49.7 | SN2
49.4 | SN2
49.3 | SN2
49.4 | SN2
49.3 | SN2
49.2 | SN2
49.2 | SN2
49.3 | SN2
48.8 | SN2
48.9 | SN2
48.7 | SN2
48.8 | SN2
49.3 | SN2
49.2 | SN2
48.8 | SN2
48.9 | SN2
50 | SN2
50.2 | SN2
50.5 | SN2
50.8 | SN2
51.3 | SN2
51.5 | SN2
51.7 | SN2
52.4 | SN2
52.7 | SN2
52.1 | SN2
51.9 | SN2
51.6 | SN2
51.2 | SN2
51 | SN2
50.8 | SN2
50.5 | SN2
50.3 | SN2
50.2 | SN2
50.2 | SN2
50.1 | SN2
50.2 | SN2
50.4 | SN2
50.2 | SN2
50.3 | SN2
50 | SN2
50.1 | SN2
49.8 | SN2
49.7 | SN2
49.5 | SN2
49.5 | SN2
48.9 | SN2
49.1 | SN2
49 | SN2
48.9 | SN2
49.2 | SN2
49.2 | SN2
48.8 | SN2
49 | SN2
48.7 | SN2
48.5 | SN2
48.6 | SN2
48.2 | SN2
48.7 | SN2
48.9 | SN2
48.9 | SN2
49.4 | SN2
50 | SN2
50 | SN2
50.3 | SN2
50.4 | SN2
50.7 | SN2
50.9 | SN2
51.6 | SN2
52.5 | SN2
52.3 | SN2
51.9 | SN2
51.7 | SN2
51.8 | SN2
51.7 | SN2
51.7 | SN2
51.3 | SN2
51.2 | SN2
50.8 | SN2
50.8 | SN2
50.4 | SN2
50.5 | SN2
50.5 | SN2
50.3 | SN2
50.2 | SN2
50.4 | SN2
50 | SN2
49.9 | SN2
49.9 | SN2
49.3 | SN2
49.6 | SN2
49.3 | SN2
49.4 | SN2
49.1 | SN2
49.1 | SN2
49.1 | SN2
48.9 | SN2
49.3 | SN2
48.9 | SN2
49.1 | SN2
49.1 | SN2
48.7 | SN2
48.7 | SN2
49.2 | SN2
49 | SN2
49.2 | SN2
49.4 | SN2
49.4 | SN2
50.2 | SN2
50.6 | SN2
50.7 | SN2
50.7 | SN2
50.7 | SN2
51.2 | SN2
51.4 | SN2
52.2 | SN2
52 | SN2
51.7 | SN2
52.2 | SN2
52.1 | SN2
51.9 | SN2
52 | SN2
51.9 | SN2
51.6 | SN2
51.2 | SN2
51.2 | SN2
51.2 | SN2
51.2 | SN2
50.6 | SN2
51.3 | SN2
50.9 | SN2
50.7 | SN2
50.4 | SN2
50.4 | SN2
50 | SN2
50 | SN2
50.2 | SN2
49.6 | SN2
49.8 | SN2
50.2 | SN2
49.6 | SN2
49.8 | SN2
49.7 | SN2
49.5 | SN2
49.9 | SN2
50.1 | SN2
49.9 | SN2
49.9 | SN2
49.8 | SN2
49.5 | SN2
50 | SN2
50.3 | SN2
49.9 | SN2
50.3 | SN2
50.8 | SN2
51.5 | SN2
51.7 | SN2
51.6 | SN2
51.9 | SN2
52.2 | SN2
52.5 | SN2
53.3 | SN2
53 | SN2
53.1 | SN2
52.8 | SN2
52.2 | SN2
51.9 | SN2
52 | SN2
51.5 | SN2
50.7 | SN2
51.2 | SN2
50.8 | SN2
50.4 | SN2
50.7 | SN2
50.7 | SN2
50.7 | SN2
51 | SN2
51 | SN2
51.1 | SN2
50.7 | SN2
50.4 | SN2
50 | SN2
49.8 | SN2
49.8 | SN2
49.8 | SN2
49.9 | SN2
49.9 | SN2
49.7 | SN2
49.9 | SN2
49.9 | SN2
49.8 | SN2
49.7 | SN2
49.5 | SN2
49.9 | SN2
49.4 | SN2
49.5 | SN2
49.5 | SN2
49.5 | SN2
49.5 | SN2
49.8 | SN2
50.4 | SN2
50.8 | SN2
51.4 | SN2
51.3 | SN2
51.7 | SN2
52.8 | SN2
53.1 | SN2
53.6 | SN2
53.1 | SN2
52.9 | SN2
52.8 | SN2
51.9 | SN2
51.8 | SN2
51.3 | SN2
51.6 | SN2
51.1 | SN2
51.2 | SN2
51.1 | SN2
50.6 | SN2
50.8 | SN2
50.8 | SN2
50.9 | SN2
50.6 | SN2
51.3 | SN2
50.6 | SN2
50.3 | SN2
50.4 | SN2
49.8 | SN2
50 | SN2
49.8 | SN2
49.7 | SN2
49.9 | SN2
50 | SN2
50.1 | SN2
49.9 | SN2
50.1 | SN2
49.7 | SN2
50.1 | SN2
49.8 | SN2
50.2 | SN2
49.9 | SN2
49.7 | SN2
49.4 | SN2
50 | SN2
50.2 | SN2
50.4 | SN2
51.1 | SN2
51.6 | SN2
51.6 | SN2
52.1 | SN2
51.9 | SN2
52.4 | SN2
52.3 | SN2
52.6 | SN2
51.4 | SN2
52 | SN2
51.8 | SN2
51.5 | SN2
51.6 | SN2
51.4 | SN2
51.4 | SN2
51 | SN2
51.1 | SN2
51 | SN2
50.9 | SN2
50.9 | SN2
50.4 | SN2
50.5 | SN2
51 | SN2
50.8 | SN2
51 | SN2
50.9 | SN2
50.9 | SN2
51 | SN2
51 | SN2
51 | SN2
51.2 | SN2
50.6 | SN2
50.5 | SN2
50.6 | SN2
50.4 | SN2
50 | SN2
49.6 | SN2
50 | SN2
50.3 | SN2
50 | SN2
49.9 | SN2
50.1 | SN2
50.2 | SN2
50 | SN2
50.2 | SN2
50.7 | SN2
51.5 | SN2
51.1 | SN2
51.3 | SN2
51.1 | SN2
51.8 | SN2
51.6 | SN2
51.8 | SN2
51.7 | SN2
51.8 | SN2
51.8 | SN2
52 | SN2
51.8 | SN2
51.6 | SN2
51.5 | SN2
51.7 | SN2
51.2 | SN2
51.2 | SN2
51.4 | SN2
50.8 | SN2
50.7 | SN2
50.8 | SN2
50.9 | SN2
51.1 | SN2
50.8 | SN2
51.1 | SN2
51.1 | SN2
50.9 | SN2
50.5 | SN2
50.6 | SN2
50.4 | SN2
50.4 | SN2
50.2 | SN2
50.3 | SN2
50.1 | SN2
50.1 | SN2
50.6 | SN2
50.2 | SN2
50 | SN2
49.8 | SN2
49.9 | SN2
49.9 | SN2
49.9 | SN2
49.5 | SN2
49.7 | SN2
50.1 | SN2
49.8 | SN2
49.6 | SN2
50 | SN2
51.5 | SN2
51 | SN2
51.6 | SN2
51.9 | SN2
52 | SN2
52.4 | SN2
51.9 | SN2
51.7 | SN2
51.5 | SN2
51.5 | SN2
50.8 | SN2
50.9 | SN2
51 | SN2
50.3 | SN2
50.1 | SN2
50.5 | SN2
50.2 | SN2
50.7 | SN2
51.1 | SN2
50.4 | SN2
50.5 | SN2
50.4 | SN2
50.7 | SN2
50.6 | SN2
50.7 | SN2
50.8 | SN2
50.8 | SN2
50.8 | SN2
50.8 | SN2
50.4 | SN2
50.5 | SN2
50.5 | SN2
50.8 | SN2
50.5 | SN2
50 | SN2
50.1 | SN2
50.4 | SN2
50 | SN2
49.8 | SN2
50.1 | SN2
49.7 | SN2
50.3 | SN2
49.9 | SN2
50.5 | SN2
50.2 | SN2
50.8 | SN2
50.8 | SN2
51.2 | SN2
51.7 | SN2
51.6 | SN2
51.9 | SN2
51.6 | SN2
51.6 | SN2
51.3 | SN2
51.4 | SN2
51.5 | SN2
50.7 | SN2
51.2 | SN2
50.8 | SN2
51.3 | SN2
51.2 | SN2
50.8 | SN2
50.9 | SN2
50.6 | SN2
51.1 | SN2
50.9 | SN2
50.7 | SN2
50.8 | SN2
50.6 | SN2
50.5 | SN2
50.8 | SN2
50.5 | SN2
50.7 | SN2
50.7 | SN2
50.4 | SN2
51 | SN2
50.4 | SN2
50.3 | SN2
50.3 | SN2
50.6 | SN2
50.7 | SN2
50.8 | SN2
50.8 | SN2
50.6 | SN2
50.4 | SN2
50.6 | SN2
50.9 | SN2
50.5 | SN2
50.7 | SN2
50.2 | SN2
50.7 | SN2
51.1 | SN2
50.8 | SN2
50.8 | SN2
51.6 | SN2
50.9 | SN2
51.4 | SN2
51.5 | SN2
52.5 | SN2
51.9 | SN2
51.9 | SN2
51.1 | SN2
51.1 | SN2
51.4 | SN2
50.8 | SN2
51.4 | SN2
50.7 | SN2
50.3 | SN2
50.5 | SN2
50.3 | SN2
50.1 | SN2
49.9 | SN2
50 | SN2
50.1 | SN2
49.9 | SN2
50.1 | SN2
50 | SN2
50.2 | SN2
49.8 | SN2
50.3 | SN2
49.8 | SN2
49.6 | SN2
49.6 | SN2
49.8 | SN2
49.8 | SN2
49.9 | SN2
49.9 | SN2
50.5 | SN2
50.3 | SN2
50.2 | SN2
50.2 | SN2
50 | SN2
49.7 | SN2
50 | SN2
50.2 | SN2
50.3 | SN2
50.6 | SN2
51.2 | SN2
51.6 | SN2
51.1 | SN2
51 | SN2
51 | SN2
51.6 | SN2
51.6 | SN2
52 | SN2
52 | SN2
52 | SN2
52.3 | SN2
52.1 | SN2
51.9 | SN2
51.5 | SN2
51.7 | SN2
51.1 | SN2
51.1 | SN2
50.9 | SN2
50.7 | SN2
51.2 | SN2
50.5 | SN2
50.5 | SN2
50.8 | SN2
50.9 | SN2
51.1 | SN2
50.7 | SN2
50.5 | SN2
50.9 | SN2
50.5 | SN2
50.4 | SN2
50.5 | SN2
50.4 | SN2
49.9 | SN2
50.1 | SN2
50 | SN2
49.9 | SN2
49.7 | SN2
49.5 | SN2
49.7 | SN2
49.9 | SN2
49.5 | SN2
49.4 | SN2
49.5 | SN2
49.8 | SN2
49.5 | SN2
49.3 | SN2
50 | SN2
50.7 | SN2
50.6 | SN2
50.7 | SN2
50.7 | SN2
51 | SN2
51 | SN2
51.5 | SN2
51.6 | SN2
51.7 | SN2
51.2 | SN2
50.9 | SN2
50.7 | SN2
50.1 | SN2
50.1 | SN2
49.9 | SN2
49.3 | SN2
49.7 | SN2
50.8 | SN2
50.2 | SN2
49.4 | SN2
49.8 | SN2
49.9 | SN2
49.5 | SN2
49.8 | SN2
50.1 | SN2
50 | SN2
49.7 | SN2
49.9 | SN2
49.7 | SN2
49.4 | SN2
49.7 | SN2
49.5 | SN2
49.8 | SN2
49 | SN2
49 | SN2
49.4 | SN2
48.8 | SN2
49.2 | SN2
49.6 | SN2
49.2 | SN2
49.4 | SN2
49.2 | SN2
49.3 | SN2
49.3 | SN2
49.8 | SN2
49.9 | SN2
50.8 | SN2
51.1 | SN2
51.2 | SN2
51.6 | SN2
51.1 | SN2
50.6 | SN2
50.5 | SN2
50.6 | SN2
50.6 | SN2
50.5 | SN2
50.1 | SN2
50.2 | SN2
49.8 | SN2
49.4 | SN2
49.4 | SN2
49 | SN2
48.8 | SN2
48.4 | SN2
49.1 | SN2
49.4 | SN2
49.3 | SN2
49.3 | SN2
49.2 | SN2
49.2 | SN2
49.4 | SN2
49.7 | SN2
49.2 | SN2
49.4 | SN2
49.2 | SN2
49.3 | SN2
49.7 | SN2
49.7 | SN2
49.6 | SN2
49.7 | SN2
49.5 | SN2
49.3 | SN2
49.1 | SN2
49.4 | SN2
49.2 | SN2
48.8 | SN2
49.4 | SN2
48.7 | SN2
49 | SN2
49.1 | SN2
49.1 | SN2
49.6 | SN2
49.6 | SN2
49.8 | SN2
50 | SN2
50.2 | SN2
50.1 | SN2
50.3 | SN2
50.7 | SN2
50.7 | SN2
50.7 | SN2
50.5 | SN2
50 | SN2
50.2 | SN2
49.8 | SN2
50.1 | SN2
50.6 | SN2
50.7 | SN2
50.2 | SN2
50.3 | SN2
50.2 | SN2
50.1 | SN2
50.3 | SN2
50 | SN2
49.9 | SN2
50.2 | SN2
49.8 | SN2
49.9 | SN2
49.9 | SN2
49.5 | SN2
49.9 | SN2
49.7 | SN2
49.8 | SN2
49.4 | SN2
49.5 | SN2
49.5 | SN2
49.6 | SN2
49.6 | SN2
49.5 | SN2
49.3 | SN2
49.8 | SN2
49.9 | SN2
49.3 | SN2
49.5 | SN2
49.9 | SN2
49.2 | SN2
50 | SN2
50.6 | SN2
50.4 | SN2
50.5 | SN2
50.7 | SN2
50.8 | SN2
50.8 | SN2
51 | SN2
51.3 | SN2
51.3 | SN2
51.8 | SN2
51.6 | SN2
51.5 | SN2
52.1 | SN2
51.7 | SN2
51.8 | SN2
51.7 | SN2
51.2 | SN2
51.2 | SN2
50.8 | SN2
50.1 | SN2
50.3 | SN2
49.7 | SN2
49.5 | SN2
49.7 | SN2
50.1 | SN2
49.8 | SN2
49.4 | SN2
49.3 | SN2
49.2 | SN2
49.3 | SN2
49.3 | SN2
49 | SN2
48.8 | SN2
49.3 | SN2
49 | SN2
48.9 | SN2
49.2 | SN2
49.1 | SN2
49.4 | SN2
49.4 | SN2
49.1 | SN2
49.2 | SN2
49.1 | SN2
49.5 | SN2
49.3 | SN2
49.3 | SN2
49.7 | SN2
50.6 | SN2
50.2 | SN2
50.8 | SN2
50.3 | SN2
50.5 | SN2
50.7 | SN2
50.8 | SN2
51.4 | SN2
51.4 | SN2
51.2 | SN2
51.5 | SN2
50.8 | SN2
51.1 | SN2
51.4 | SN2
50.8 | SN2
50.3 | SN2
50.8 | SN2
50.6 | SN2
50.4 | SN2
50.3 | SN2
50.6 | SN2
50.8 | SN2
50.8 | SN2
50.5 | SN2
50.6 | SN2
51.1 | SN2
50.3 | SN2
50.5 | SN2
50.5 | SN2
50 | SN2
50.3 | SN2
49.8 | SN2
50 | SN2
50.1 | SN2
49.8 | SN2
49.5 | SN2
49.4 | SN2
49.5 | SN2
49.5 | SN2
49.7 | SN2
49.6 | SN2
49.5 | SN2
49.4 | SN2
49.7 | SN2
50.2 | SN2
50.2 | SN2
50.6 | SN2
51.1 | SN2
51.2 | SN2
51.2 | SN2
51.1 | SN2
51.3 | SN2
50.9 | SN2
7.6 | SN2
55.2 | SN2
55.3 | SN2
55.5 | SN2
52.7 | SN2
52.3 | SN2
51.5 | SN2
51.4 | SN2
50.9 | SN2
51.1 | SN2
50.6 | SN2
50.8 | SN2
50.3 | SN2
50.2 | SN2
50.6 | SN2
50.7 | SN2
50.4 | SN2
50.5 | SN2
50.6 | SN2
50.2 | SN2
49.9 | SN2
50.7 | SN2
49.9 | SN2
50 | SN2
50.2 | SN2
49.9 | SN2
49.8 | SN2
49.9 | SN2
49.7 | SN2
49.6 | SN2
49.4 | SN2
49.6 | SN2
49.5 | SN2
49.3 | SN2
49.6 | SN2
49.5 | SN2
49.6 | SN2
49.7 | SN2
50.5 | SN2
50.9 | SN2
51.3 | SN2
51 | SN2
51 | SN2
50.5 | SN2
50.9 | SN2
50.9 | SN2
51.2 | SN2
51.2 | SN2
50.8 | SN2
51.3 | SN2
51.4 | SN2
50.6 | SN2
50.6 | SN2
50.4 | SN2
50.3 | SN2
50.5 | SN2
50.1 | SN2
50.3 | SN2
50.1 | SN2
49.8 | SN2
49.9 | SN2
50.1 | SN2
50 | SN2
50.4 | SN2
50.3 | SN2
50.2 | SN2
50 | SN2
50.2 | SN2
50.4 | SN2
50.1 | SN2
49.9 | SN2
49.4 | SN2
49.9 | SN2
49.6 | SN2
49.5 | SN2
49.1 | SN2
49.5 | SN2
49.4 | SN2
49.6 | SN2
49.6 | SN2
49.4 | SN2
49.6 | SN2
50 | SN2
50.1 | SN2
50.1 | SN2
50.4 | SN2
50.9 | SN2
50.8 | SN2
50.6 | SN2
51 | SN2
50.5 | SN2
51.3 | SN2
51.3 | SN2
51.3 | SN2
51.4 | SN2
50.7 | SN2
49.8 | SN2
50.4 | SN2
50.4 | SN2
50.6 | SN2
50.4 | SN2
50.6 | SN2
50.6 | SN2
50.4 | SN2
50.7 | SN2
49.9 | SN2
50 | SN2
49.8 | SN2
49.7 | SN2
49.7 | SN2
49.4 | SN2
49.4 | SN2
49.6 | SN2
49.4 | SN2
49.5 | SN2
49.7 | SN2
49.6 | SN2
49.5 | SN2
49.6 | SN2
49.4 | SN2
49.5 | SN2
49.6 | SN2
49.6 | SN2
49.4 | SN2
49.5 | SN2
49.6 | SN2
49.3 | SN2
49.2 | SN2
49.6 | SN2
49.4 | SN2
50.3 | SN2
51 | SN2
50.9 | SN2
51.1 | SN2
51.3 | SN2
51 | SN2
50.9 | SN2
51.1 | SN2
51.6 | SN2
51.6 | SN2
51 | SN2
51.5 | SN2
51.2 | SN2
51.1 | SN2
51.1 | SN2
50.7 | SN2
50.4 | SN2
50.5 | SN2
50.4 | SN2
50.1 | SN2
50.3 | SN2
50.6 | SN2
50 | SN2
50.1 | SN2
50.6 | SN2
50.1 | SN2
50.3 | SN2
50.6 | SN2
50.3 | SN2
50.2 | SN2
50.1 | SN2
50 | SN2
50 | SN2
50.1 | SN2
49.8 | SN2
49.7 | SN2
49.7 | SN2
49.7 | SN2
49.5 | SN2
49.5 | SN2
49.4 | SN2
49.3 | SN2
49.8 | SN2
50 | SN2
50.5 | SN2
50.2 | SN2
49.9 | SN2
50.5 | SN2
50.8 | SN2
50.5 | SN2
50.8 | SN2
51.1 | SN2
51.2 | SN2
51.5 | SN2
51.2 | SN2
51.5 | SN2
51.1 | SN2
51 | SN2
51 | SN2
50.5 | SN2
50.2 | SN2
50.1 | SN2
49.9 | SN2
49.5 | SN2
49.2 | SN2
49 | SN2
49.2 | SN2
49.7 | SN2
49.5 | SN2
49.3 | SN2
49.4 | SN2
49.6 | SN2
49.6 | SN2
49.5 | SN2
49.5 | SN2
49.3 | SN2
49.6 | SN2
49.2 | SN2
49.8 | SN2
49.6 | SN2
49.8 | SN2
49.4 | SN2
49.3 | SN2
49.4 | SN2
49.4 | SN2
49.1 | SN2
48.9 | SN2
48.8 | SN2
49.3 | SN2
48.8 | SN2
49.3 | SN2
49.7 | SN2
50.4 | SN2
50.4 | SN2
50.5 | SN2
50.5 | SN2
50.2 | SN2
50 | SN2
50.3 | SN2
50.5 | SN2
50.7 | SN2
50.7 | SN2
50.7 | SN2
50.8 | SN2
50.7 | SN2
50.4 | SN2
50.2 | SN2
49.7 | SN2
49.7 | SN2
49.3 | SN2
49.6 | SN2
49.7 | SN2
49.3 | SN2
49.4 | SN2
49.2 | SN2
49.6 | SN2
50.1 | SN2
49.4 | SN2
49.5 | SN2
49.4 | SN2
49.2 | SN2
49.2 | SN2
49.3 | SN2
49.6 | SN2
49.2 | SN2
49.3 | SN2
49.1 | SN2
48.9 | SN2
48.9 | SN2
48.8 | SN2
48.4 | SN2
48.3 | SN2
48.3 | SN2
48.5 | SN2
48.5 | SN2
48.1 | SN2
48.6 | SN2
48.6 | SN2
48.9 | SN2
49.1 | SN2
49.3 | SN2
49.4 | SN2
49.7 | SN2
50 | SN2
50.1 | SN2
50.6 | SN2
51.5 | SN2
50.5 | SN2
50.4 | SN2
50.5 | SN2
50.5 | SN2
50.3 | SN2
50.2 | SN2
50 | SN2
50.3 | SN2
50.3 | SN2
49.9 | SN2
49.8 | SN2
49.4 | SN2
49.8 | SN2
49.4 | SN2
49.4 | SN2
49.8 | SN2
49.3 | SN2
49.6 | SN2
49.7 | SN2
49.7 | SN2
49.7 | SN2
50.1 | SN2
49.7 | SN2
49.5 | SN2
49.3 | SN2
49.3 | SN2
49.7 | SN2
49.4 | SN2
49.3 | SN2
49 | SN2
48.9 | SN2
49 | SN2
48.8 | SN2
48.5 | SN2
48.7 | SN2
48.6 | SN2
48.7 | SN2
49.1 | SN2
49.4 | SN2
49.5 | SN2
50.2 | SN2
50.1 | SN2
50.3 | SN2
50.7 | SN2
51.1 | SN2
51.6 | SN2
51.2 | SN2
51.3 | SN2
51.1 | SN2
51.1 | SN2
51.3 | SN2
50.6 | SN2
49.5 | SN2
50.3 | SN2
49.7 | SN2
49.8 | SN2
50.2 | SN2
50.2 | SN2
49.9 | SN2
49.8 | SN2
49.9 | SN2
50.4 | SN2
50.3 | SN2
49.9 | SN2
50.1 | SN2
50 | SN2
50 | SN2
50.1 | SN2
49.7 | SN2
49.8 | SN2
49.9 | SN2
49.6 | SN2
49.8 | SN2
49.8 | SN2
49.7 | SN2
49.9 | SN2
49.9 | SN2
49.5 | SN2
49.2 | SN2
49.4 | SN2
48.7 | SN2
49.2 | SN2
49.2 | SN2
49 | SN2
49.5 | SN2
49.6 | SN2
50.2 | SN2
50.8 | SN2
50.9 | SN2
51.6 | SN2
51.6 | SN2
51.5 | SN2
51.8 | SN2
51.4 | SN2
50.7 | SN2
50.7 | SN2
50.4 | SN2
50.1 | SN2
50.4 | SN2
49.8 | SN2
50 | SN2
50 | SN2
49.7 | SN2
50.1 | SN2
49.6 | SN2
49.7 | SN2
50.4 | SN2
50 | SN2
50.1 | SN2
50 | SN2
49.9 | SN2
49.8 | SN2
50 | SN2
50 | SN2
49.8 | SN2
49.8 | SN2
49.6 | SN2
49.5 | SN2
49.2 | SN2
49.3 | SN2
49.5 | SN2
49.3 | SN2
48.9 | SN2
48.8 | SN2
48.7 | SN2
48.8 | SN2
48.6 | SN2
48.7 | SN2
48.7 | SN2
48.8 | SN2
49 | SN2
49.2 | SN2
49.6 | SN2
50.4 | SN2
50.4 | SN2
50.7 | SN2
50.6 | SN2
51 | SN2
51.2 | SN2
51.6 | SN2
51.2 | SN2
50.9 | SN2
51.5 | SN2
50.9 | SN2
50.4 | SN2
50.1 | SN2
50.2 | SN2
50.7 | SN2
50.2 | SN2
50.3 | SN2
49.9 | SN2
50 | SN2
49.7 | SN2
49.8 | SN2
50.1 | SN2
49.5 | SN2
49.9 | SN2
49.6 | SN2
49.7 | SN2
49.8 | SN2
49.8 | SN2
49.8 | SN2
49.2 | SN2
49.5 | SN2
49.3 | SN2
49.1 | SN2
49.4 | SN2
49.3 | SN2
49.1 | SN2
48.9 | SN2
49.2 | SN2
48.9 | SN2
48.8 | SN2
48.9 | SN2
49.3 | SN2
48.8 | SN2
48.9 | SN2
49.6 | SN2
49.4 | SN2
50.2 | SN2
50.4 | SN2
50.9 | SN2
50.7 | SN2
50.4 | SN2
51.4 | SN2
51.6 | SN2
51.2 | SN2
51.5 | SN2
51.6 | SN2
51 | SN2
51 | SN2
50.6 | SN2
50.9 | SN2
51.1 | SN2
51.1 | SN2
50.5 | SN2
50.5 | SN2
50.1 | SN2
50.4 | SN2
50.4 | SN2
50.3 | SN2
50.1 | SN2
50.1 | SN2
50.1 | SN2
50.8 | SN2
50.8 | SN2
50.5 | SN2
50.6 | SN2
50.3 | SN2
50.3 | SN2
50 | SN2
49.9 | SN2
50.1 | SN2
49.9 | SN2
50.2 | SN2
50.2 | SN2
50 | SN2
50.2 | SN2
50 | SN2
49.6 | SN2
50.2 | SN2
50.1 | SN2
50.5 | SN2
51.1 | SN2
51.5 | SN2
51.5 | SN2
51.5 | SN2
51.8 | SN2
52 | SN2
51.8 | SN2
51.8 | SN2
52.3 | SN2
52.3 | SN2
51.8 | SN2
51.3 | SN2
51.3 | SN2
51.1 | SN2
51.4 | SN2
51.2 | SN2
51.1 | SN2
51.2 | SN2
51 | SN2
50.9 | SN2
50.5 | SN2
49.7 | SN2
50.1 | SN2
50.3 | SN2
50.4 | SN2
50.4 | SN2
49.9 | SN2
49.9 | SN2
49.8 | SN2
50.1 | SN2
50.2 | SN2
50.1 | SN2
50.1 | SN2
50 | SN2
50.2 | SN2
50.2 | SN2
50.1 | SN2
50.2 | SN2
49.9 | SN2
49.8 | SN2
49.7 | SN2
49.7 | SN2
49.6 | SN2
49.8 | SN2
49.4 | SN2
49.7 | SN2
50.3 | SN2
50.8 | SN2
50.6 | SN2
50.7 | SN2
51.5 | SN2
52 | SN2
52.6 | SN2
52.6 | SN2
52.8 | SN2
52.7 | SN2
52.8 | SN2
52.4 | SN2
52.2 | SN2
52.2 | SN2
51.7 | SN2
51.9 | SN2
51.8 | SN2
51.3 | SN2
51.6 | SN2
51.5 | SN2
51.4 | SN2
51.4 | SN2
51.4 | SN2
51.6 | SN2
51.2 | SN2
51.3 | SN2
51.5 | SN2
51.5 | SN2
51.3 | SN2
51.5 | SN2
51.1 | SN2
50.9 | SN2
51.2 | SN2
51.1 | SN2
51.2 | SN2
51 | SN2
51.1 | SN2
50.9 | SN2
51.2 | SN2
50.9 | SN2
50.6 | SN2
51.1 | SN2
50.7 | SN2
51 | SN2
50.8 | SN2
51.7 | SN2
51.8 | SN2
52.3 | SN2
51.6 | SN2
52.5 | SN2
52.5 | SN2
52.7 | SN2
51.9 | SN2
52.3 | SN2
52.2 | SN2
52.7 | SN2
52.2 | SN2
51.8 | SN2
50.6 | SN2
50.8 | SN2
49.3 | SN2
50.5 | SN2
49.8 | SN2
49.3 | SN2
49.8 | SN2
50 | SN2
49.9 | SN2
50.3 | SN2
50.4 | SN2
50.1 | SN2
50.3 | SN2
49.9 | SN2
50.4 | SN2
50.3 | SN2
50.1 | SN2
50 | SN2
50 | SN2
50.1 | SN2
50.1 | SN2
49.7 | SN2
50.2 | SN2
50 | SN2
50.3 | SN2
50.3 | SN2
50.2 | SN2
50.3 | SN2
50 | SN2
50.2 | SN2
50 | SN2
50.1 | SN2
49.9 | SN2
50.2 | SN2
50.6 | SN2
51.3 | SN2
51.7 | SN2
52 | SN2
51.8 | SN2
51.6 | SN2
52.1 | SN2
52.5 | SN2
52.3 | SN2
52.4 | SN2
52.1 | SN2
51.6 | SN2
51.9 | SN2
51 | SN2
51.1 | SN2
50.8 | SN2
50.8 | SN2
50.8 | SN2
50.3 | SN2
50.2 | SN2
50 | SN2
50 | SN2
49.9 | SN2
49.8 | SN2
50.3 | SN2
49.5 | SN2
49.8 | SN2
50 | SN2
49.8 | SN2
49.7 | SN2
49.6 | SN2
49.4 | SN2
49.6 | SN2
49.8 | SN2
49.9 | SN2
49.9 | SN2
50.1 | SN2
49.7 | SN2
49.7 | SN2
49.7 | SN2
49.8 | SN2
49.9 | SN2
49.4 | SN2
49.7 | SN2
49.9 | SN2
50 | SN2
51.1 | SN2
51.1 | SN2
51.5 | SN2
51.5 | SN2
51.5 | SN2
52.2 | SN2
51.8 | SN2
52.2 | SN2
51.9 | SN2
52.6 | SN2
52 | SN2
52.5 | SN2
51.7 | SN2
51.4 | SN2
51.1 | SN2
50.9 | SN2
50.9 | SN2
51.1 | SN2
51.2 | SN2
50.9 | SN2
50.2 | SN2
50.7 | SN2
50.7 | SN2
50.5 | SN2
50.8 | SN2
50.6 | SN2
50.6 | SN2
50.5 | SN2
50.2 | SN2
50.2 | SN2
50.3 | SN2
50.2 | SN2
50.1 | SN2
49.9 | SN2
49.9 | SN2
50.3 | SN2
50.1 | SN2
50.2 | SN2
50.6 | SN2
50.1 | SN2
50.2 | SN2
49.9 | SN2
50 | SN2
50.1 | SN2
50 | SN2
50.3 | SN2
51.2 | SN2
51.4 | SN2
51.5 | SN2
51.8 | SN2
51.9 | SN2
52.1 | SN2
52.5 | SN2
52.1 | SN2
51.9 | SN2
52.4 | SN2
51.7 | SN2
51.5 | SN2
52.1 | SN2
51.1 | SN2
51.2 | SN2
51.2 | SN2
50.5 | SN2
51.2 | SN2
51.1 | SN2
51.1 | SN2
51.1 | SN2
50.9 | SN2
50.7 | SN2
50.9 | SN2
50.8 | SN2
50.4 | SN2
50.8 | SN2
50.6 | SN2
50.6 | SN2
50.5 | SN2
50.4 | SN2
50.4 | SN2
50.5 | SN2
50.8 | SN2
50.6 | SN2
50.6 | SN2
50.5 | SN2
50.1 | SN2
50.2 | SN2
50.3 | SN2
50.3 | SN2
50 | SN2
50.1 | SN2
49.9 | SN2
50.4 | SN2
50.7 | SN2
50.9 | SN2
51.2 | SN2
50.8 | SN2
51.2 | SN2
51.7 | SN2
51.6 | SN2
51.6 | SN2
52 | SN2
51.3 | SN2
51.2 | SN2
48.6 | SN2
48.4 | SN2
48.9 | SN2
48.9 | SN2
49.3 | SN2
49 | SN2
48.3 | SN2
48.5 | SN2
48.4 | SN2
48.7 | SN2
48.4 | SN2
48.2 | SN2
47.9 | SN2
47.8 | SN2
47.9 | SN2
48.3 | SN2
48.8 | SN2
48 | SN2
48.8 | SN2
49 | SN2
48.7 | SN2
48.1 | SN2
48.3 | SN2
48.4 | SN2
48.6 | SN2
48.5 | SN2
48.2 | SN2
47.6 | SN2
47.8 | SN2
47.9 | SN2
47.5 | SN2
47.6 | SN2
47.6 | SN2
47.7 | SN2
47.6 | SN2
48.5 | SN2
48.5 | SN2
48.6 | SN2
48.4 | SN2
48.4 | SN2
48.8 | SN2
48.8 | SN2
48.8 | SN2
48.6 | SN2
51.6 | SN2
51.9 | SN2
52 | SN2
51.6 | SN2
52.1 | SN2
51.7 | SN2
52 | SN2
52 | SN2
51.6 | SN2
52.7 | SN2
51.5 | SN2
51.5 | SN2
51.2 | SN2
51.1 | SN2
51.5 | SN2
51.2 | SN2
51 | SN2
50.9 | SN2
51.1 | SN2
51.2 | SN2
51.4 | SN2
51.4 | SN2
51.6 | SN2
51.1 | SN2
50.9 | SN2
50.7 | SN2
50.6 | SN2
51 | SN2
50.8 | SN2
50.5 | SN2
50.4 | SN2
50.7 | SN2
50.6 | SN2
50.1 | SN2
50.2 | SN2
50 | SN2
50.2 | SN2
50.5 | SN2
51.1 | SN2
51.5 | SN2
52.2 | SN2
52.1 | SN2
52.2 | SN2
51.6 | SN2
51.7 | SN2
52.1 | SN2
52.1 | SN2
52.3 | SN2
52.2 | SN2
51.8 | SN2
51.7 | SN2
51.7 | SN2
51.1 | SN2
50.8 | SN2
50.9 | SN2
50.8 | SN2
51.5 | SN2
51.1 | SN2
51.2 | SN2
51.3 | SN2
51.2 | SN2
50.9 | SN2
51 | SN2
51.1 | SN2
51 | SN2
51.1 | SN2
51 | SN2
50.8 | SN2
50.8 | SN2
50.7 | SN2
50.4 | SN2
50.3 | SN2
50.4 | SN2
50.3 | SN2
50.6 | SN2
50.5 | SN2
50.4 | SN2
50.3 | SN2
50.3 | SN2
50.1 | SN2
50.3 | SN2
50.4 | SN2
50.4 | SN2
50.9 | SN2
51.4 | SN2
56.9 | SN2
53.9 | SN2
52.9 | SN2
51.4 | SN2
51.7 | SN2
51.1 | SN2
50.5 | SN2
50.9 | SN2
51.2 | SN2
50.8 | SN2
50.2 | SN2
50.1 | SN2
50.2 | SN2
50.1 | SN2
50.8 | SN2
49.8 | SN2
50.1 | SN2
50.2 | SN2
50.1 | SN2
49.7 | SN2
49.7 | SN2
49.6 | SN2
49.4 | SN2
49.2 | SN2
49.2 | SN2
49 | SN2
49.4 | SN2
48.9 | SN2
49.3 | SN2
49.6 | SN2
48.9 | SN2
49.1 | SN2
49.2 | SN2
49 | SN2
48.7 | SN2
48.7 | SN2
49.3 | SN2
48.5 | SN2
48.4 | SN2
48.2 | SN2
48.4 | SN2
48.4 | SN2
49 | SN2
48.6 | SN2
48.9 | SN2
49.8 | SN2
50.1 | SN2
50.5 | SN2
51 | SN2
51.6 | SN2
51.9 | SN2
51.7 | SN2
52.1 | SN2
52.7 | SN2
52.5 | SN2
52.3 | SN2
52.1 | SN2
52.6 | SN2
52.3 | SN2
51.8 | SN2
51.6 | SN2
51.7 | SN2
51.2 | SN2
51.1 | SN2
51.3 | SN2
51.7 | SN2
51.5 | SN2
51.6 | SN2
51.7 | SN2
51.4 | SN2
51.3 | SN2
50.8 | SN2
50.8 | SN2
51 | SN2
50.9 | SN2
50.6 | SN2
50.7 | SN2
51 | SN2
50.4 | SN2
50.7 | SN2
50.8 | SN2
50.7 | SN2
50.5 | SN2
50.6 | SN2
50.4 | SN2
50.5 | SN2
50.1 | SN2
50 | SN2
50.5 | SN2
50.4 | SN2
50.7 | SN2
51.1 | SN2
51.6 | SN2
52.4 | SN2
52.7 | SN2
52.8 | SN2
52.8 | SN2
52.9 | SN2
52.7 | SN2
53.4 | SN2
52.9 | SN2
52.9 | SN2
53.1 | SN2
52.5 | SN2
51.8 | SN2
52 | SN2
51.9 | SN2
51.6 | SN2
52.1 | SN2
51.9 | SN2
51.6 | SN2
51.2 | SN2
51.5 | SN2
51 | SN2
51.1 | SN2
51.3 | SN2
51.1 | SN2
51.5 | SN2
51.3 | SN2
51.4 | SN2
51.5 | SN2
51 | SN2
51.2 | SN2
51 | SN2
50.8 | SN2
51 | SN2
51.3 | SN2
50.2 | SN2
50.6 | SN2
50.8 | SN2
51.2 | SN2
50.7 | SN2
50.5 | SN2
51 | SN2
50.5 | SN2
50.5 | SN2
51.2 | SN2
52.1 | SN2
52.1 | SN2
52.2 | SN2
52.7 | SN2
52.8 | SN2
53 | SN2
52.8 | SN2
52.8 | SN2
52.9 | SN2
52.9 | SN2
53.3 | SN2
53 | SN2
53 | SN2
52.8 | SN2
52.5 | SN2
52 | SN2
51.9 | SN2
51.8 | SN2
52.1 | SN2
51.8 | SN2
52.2 | SN2
51.6 | SN2
51.1 | SN2
51.2 | SN2
51.9 | SN2
51.7 | SN2
51.3 | SN2
51.8 | SN2
51.4 | SN2
51.3 | SN2
51.3 | SN2
51.2 | SN2
51.3 | SN2
51.4 | SN2
51.5 | SN2
51.4 | SN2
51.2 | SN2
50.9 | SN2
50.9 | SN2
50.9 | SN2
50.4 | SN2
50.6 | SN2
50.4 | SN2
50.7 | SN2
50.4 | SN2
50.7 | SN2
51.1 | SN2
51.8 | SN2
51.8 | SN2
52.5 | SN2
51.7 | SN2
52.4 | SN2
52.1 | SN2
53 | SN2
52.8 | SN2
52.7 | SN2
52.6 | SN2
52.8 | SN2
52.7 | SN2
52.8 | SN2
52.5 | SN2
52.7 | SN2
52.2 | SN2
52.5 | SN2
52.4 | SN2
52.2 | SN2
51.8 | SN2
52.2 | SN2
51.7 | SN2
51 | SN2
51.2 | SN2
51.2 | SN2
51.3 | SN2
51.3 | SN2
51.2 | SN2
51 | SN2
51.5 | SN2
51 | SN2
50.9 | SN2
50.7 | SN2
50.7 | SN2
50.6 | SN2
51.1 | SN2
50.7 | SN2
50.9 | SN2
50.9 | SN2
50.7 | SN2
50.6 | SN2
50.7 | SN2
50.5 | SN2
50.6 | SN2
50.2 | SN2
50.8 | SN2
50.5 | SN2
51.4 | SN2
51.8 | SN2
51.6 | SN2
51.9 | SN2
52.1 | SN2
52.7 | SN2
53.1 | SN2
53 | SN2
52.8 | SN2
53 | SN2
53.1 | SN2
52.9 | SN2
53 | SN2
52.4 | SN2
53.2 | SN2
52.3 | SN2
51.5 | SN2
51.8 | SN2
51.4 | SN2
51 | SN2
50.9 | SN2
50.8 | SN2
51 | SN2
50.9 | SN2
50.9 | SN2
50.8 | SN2
50.9 | SN2
50.7 | SN2
50.6 | SN2
50.8 | SN2
50.8 | SN2
50.9 | SN2
50.9 | SN2
50.7 | SN2
50.8 | SN2
50.7 | SN2
50.9 | SN2
50.4 | SN2
50.6 | SN2
50.4 | SN2
50.6 | SN2
50.3 | SN2
50.4 | SN2
49.8 | SN2
50.2 | SN2
50.6 | SN2
51 | SN2
51.4 | SN2
52 | SN2
52.5 | SN2
52.6 | SN2
53.1 | SN2
52.4 | SN2
52.7 | SN2
53 | SN2
52.2 | SN2
52.3 | SN2
52 | SN2
52.1 | SN2
51.9 | SN2
51.2 | SN2
51.6 | SN2
51.6 | SN2
51.1 | SN2
51.3 | SN2
51.3 | SN2
51.1 | SN2
50.6 | SN2
51.2 | SN2
50.9 | SN2
51 | SN2
50.7 | SN2
50.8 | SN2
50.9 | SN2
50.7 | SN2
50.5 | SN2
51 | SN2
51.1 | SN2
50.6 | SN2
50.3 | SN2
50.6 | SN2
50.2 | SN2
50.1 | SN2
50.6 | SN2
50.4 | SN2
50.1 | SN2
50.3 | SN2
50 | SN2
50 | SN2
50.2 | SN2
50.1 | SN2
50.9 | SN2
51.5 | SN2
51.5 | SN2
51.8 | SN2
52.5 | SN2
52.4 | SN2
52.3 | SN2
52.9 | SN2
53 | SN2
52.6 | SN2
52.4 | SN2
52.2 | SN2
52.1 | SN2
52.1 | SN2
51.8 | SN2
51.6 | SN2
52.2 | SN2
52.1 | SN2
51.7 | SN2
51.5 | SN2
51.3 | SN2
51 | SN2
50.8 | SN2
50.7 | SN2
50 | SN2
50.1 | SN2
50.4 | SN2
50.3 | SN2
50.4 | SN2
50.2 | SN2
50.1 | SN2
50.2 | SN2
50.5 | SN2
50.5 | SN2
50.4 | SN2
50.6 | SN2
50.6 | SN2
50.5 | SN2
50.5 | SN2
50.3 | SN2
49.9 | SN2
50.2 | SN2
50.1 | SN2
49.9 | SN2
50.2 | SN2
50.2 | SN2
50.8 | SN2
51 | SN2
51.5 | SN2
52.7 | SN2
53.6 | SN2
53.6 | SN2
53.9 | SN2
53.6 | SN2
54 | SN2
54 | SN2
54.5 | SN2
54.4 | SN2
53 | SN2
52.5 | SN2
52.5 | SN2
52.5 | SN2
53.1 | SN2
53.3 | SN2
52.8 | SN2
51.5 | SN2
51.3 | SN2
52.1 | SN2
52.4 | SN2
52.8 | SN2
52.9 | SN2
52.4 | SN2
52.7 | SN2
52.7 | SN2
52.5 | SN2
52.7 | SN2
52.7 | SN2
52.8 | SN2
52.8 | SN2
52.3 | SN2
52.5 | SN2
52.1 | SN2
52.5 | SN2
52.2 | SN2
52.7 | SN2
52.7 | SN2
52.6 | SN2
52.5 | SN2
52.2 | SN2
52.7 | SN2
52.3 | SN2
52.7 | SN2
52.8 | SN2
52.8 | SN2
53.8 | SN2
54.3 | SN2
54 | SN2
54.7 | SN2
53.9 | SN2
54.5 | SN2
54.6 | SN2
55.2 | SN2
54.3 | SN2
54.2 | SN2
54.6 | SN2
54.5 | SN2
54.1 | SN2
53.5 | SN2
53.4 | SN2
53 | SN2
52.9 | SN2
53.1 | SN2
52.7 | SN2
52.6 | SN2
52.1 | SN2
52.7 | SN2
51.9 | SN2
51.9 | SN2
52.3 | SN2
52 | SN2
51.8 | SN2
52 | SN2
51.6 | SN2
51.5 | SN2
51.9 | SN2
52.1 | SN2
52.1 | SN2
52 | SN2
52.1 | SN2
52 | SN2
51.6 | SN2
52.2 | SN2
51.8 | SN2
51.8 | SN2
51.5 | SN2
51.8 | SN2
52.1 | SN2
52.2 | SN2
52.5 | SN2
52.6 | SN2
53.2 | SN2
53.5 | SN2
53.9 | SN2
54.1 | SN2
54.3 | SN2
54.3 | SN2
54.6 | SN2
54.8 | SN2
54.6 | SN2
54.1 | SN2
54.3 | SN2
53.6 | SN2
53.6 | SN2
53.8 | SN2
53.6 | SN2
53.2 | SN2
53 | SN2
53 | SN2
52.6 | SN2
52.8 | SN2
52.9 | SN2
52.7 | SN2
52.6 | SN2
52.7 | SN2
52.4 | SN2
53 | SN2
52.7 | SN2
52.3 | SN2
52.2 | SN2
52.1 | SN2
52.2 | SN2
52.3 | SN2
52.4 | SN2
51.7 | SN2
51.8 | SN2
51.9 | SN2
52.2 | SN2
51.8 | SN2
51.9 | SN2
52.1 | SN2
52 | SN2
51.8 | SN2
52.1 | SN2
52.1 | SN2
52.4 | SN2
53.2 | SN2
54 | SN2
54.2 | SN2
53.8 | SN2
54 | SN2
54 | SN2
54.1 | SN2
53.9 | SN2
54.2 | SN2
54 | SN2
54.3 | SN2
53.7 | SN2
53.9 | SN2
54 | SN2
53.5 | SN2
53 | SN2
53 | SN2
53.1 | SN2
52.2 | SN2
52.5 | SN2
51.8 | SN2
51.7 | SN2
52.1 | SN2
51.6 | SN2
51.7 | SN2
51.7 | SN2
51.8 | SN2
51.9 | SN2
51.7 | SN2
51.6 | SN2
52.1 | SN2
52 | SN2
52.1 | SN2
51.7 | SN2
51.7 | SN2
51.5 | SN2
51.3 | SN2
51.2 | SN2
51.5 | SN2
51.3 | SN2
51.2 | SN2
51.6 | SN2
51.4 | SN2
51.3 | SN2
51.8 | SN2
52.7 | SN2
51.3 | SN2
51.6 | SN2
52.2 | SN2
52.1 | SN2
52.1 | SN2
53 | SN2
52.7 | SN2
53 | SN2
52.5 | SN2
52.3 | SN2
51.7 | SN2
52.7 | SN2
52.3 | SN2
52 | SN2
52 | SN2
51.9 | SN2
51.8 | SN2
51.7 | SN2
51.5 | SN2
51.1 | SN2
51 | SN2
50.5 | SN2
50.8 | SN2
50.6 | SN2
50.6 | SN2
50.5 | SN2
50.7 | SN2
50.7 | SN2
50.2 | SN2
49.9 | SN2
50.2 | SN2
50.4 | SN2
50 | SN2
50.4 | SN2
49.9 | SN2
49.8 | SN2
50 | SN2
49.6 | SN2
49.9 | SN2
49.6 | SN2
49.5 | SN2
49.1 | SN2
49.1 | SN2
49.5 | SN2
50.1 | SN2
50.3 | SN2
51.5 | SN2
52.6 | SN2
52.4 | SN2
52.9 | SN2
53 | SN2
53 | SN2
52.8 | SN2
52 | SN2
52 | SN2
51.3 | SN2
50.7 | SN2
50.7 | SN2
52 | SN2
52.2 | SN2
52.7 | SN2
52.2 | SN2
52.8 | SN2
51.9 | SN2
51.4 | SN2
50.2 | SN2
49.7 | SN2
49.9 | SN2
49.6 | SN2
49.9 | SN2
50.1 | SN2
49.2 | SN2
49.2 | SN2
49.1 | SN2
49.1 | SN2
48.8 | SN2
49.4 | SN2
49.7 | SN2
49.2 | SN2
49 | SN2
50.9 | SN2
49.5 | SN2
48.8 | SN2
48.9 | SN2
48.7 | SN2
48.8 | SN2
48.8 | SN2
48.5 | SN2
49.6 | SN2
49.2 | SN2
49.5 | SN2
49.8 | SN2
51.1 | SN2
51.5 | SN2
52.1 | SN2
52 | SN2
52.3 | SN2
51.8 | SN2
51.8 | SN2
52.4 | SN2
53.1 | SN2
53.2 | SN2
53.4 | SN2
53.3 | SN2
53.7 | SN2
53.5 | SN2
53 | SN2
53.7 | SN2
52.5 | SN2
52.2 | SN2
51.8 | SN2
51.7 | SN2
51.2 | SN2
50.6 | SN2
51 | SN2
51.1 | SN2
50.4 | SN2
50.8 | SN2
50.4 | SN2
50.6 | SN2
50.2 | SN2
50.4 | SN2
49.3 | SN2
49.9 | SN2
50.2 | SN2
49.5 | SN2
49.6 | SN2
49.9 | SN2
50 | SN2
49.7 | SN2
49.6 | SN2
49.8 | SN2
48.9 | SN2
49.3 | SN2
49.8 | SN2
49.8 | SN2
50.4 | SN2
50.7 | SN2
51.2 | SN2
51.2 | SN2
51.7 | SN2
52.1 | SN2
52.9 | SN2
52.7 | SN2
53 | SN2
52.9 | SN2
52.9 | SN2
53.2 | SN2
53.1 | SN2
52.8 | SN2
51.9 | SN2
51.6 | SN2
51.6 | SN2
51.1 | SN2
51.4 | SN2
51.4 | SN2
51.5 | SN2
51.2 | SN2
51.4 | SN2
51 | SN2
50.7 | SN2
50.4 | SN2
51.3 | SN2
51.1 | SN2
51.1 | SN2
51.1 | SN2
51.4 | SN2
51.5 | SN2
51.8 | SN2
51.3 | SN2
51.5 | SN2
50.9 | SN2
51.1 | SN2
51.1 | SN2
50.8 | SN2
50.6 | SN2
50.4 | SN2
50.3 | SN2
50.4 | SN2
50.4 | SN2
50.7 | SN2
50.8 | SN2
51.5 | SN2
51.7 | SN2
52 | SN2
52.5 | SN2
52.8 | SN2
52 | SN2
52.6 | SN2
52.9 | SN2
53 | SN2
53.3 | SN2
53.5 | SN2
53.3 | SN2
52.7 | SN2
52.4 | SN2
51.5 | SN2
51.7 | SN2
51.7 | SN2
51.3 | SN2
51.7 | SN2
51.6 | SN2
51.3 | SN2
51.1 | SN2
51.3 | SN2
51.5 | SN2
51.4 | SN2
51.3 | SN2
51.2 | SN2
51.5 | SN2
51.6 | SN2
51.6 | SN2
51.1 | SN2
51.8 | SN2
51.7 | SN2
51.3 | SN2
51.5 | SN2
51.5 | SN2
51.4 | SN2
51.8 | SN2
50.9 | SN2
51.1 | SN2
51 | SN2
50.9 | SN2
51 | SN2
50.8 | SN2
50.8 | SN2
51.1 | SN2
51.6 | SN2
52.3 | SN2
51.9 | SN2
52.4 | SN2
52.7 | SN2
52.6 | SN2
52.6 | SN2
51.9 | SN2
52.7 | SN2
52.8 | SN2
52.5 | SN2
52.4 | SN2
51.9 | SN2
52 | SN2
52.6 | SN2
52 | SN2
51.6 | SN2
52 | SN2
52.2 | SN2
51.8 | SN2
51.8 | SN2
51.3 | SN2
51.8 | SN2
52 | SN2
52 | SN2
52.5 | SN2
52.7 | SN2
52.2 | SN2
52.4 | SN2
52.8 | SN2
52.1 | SN2
52.1 | SN2
53.1 | SN2
52.7 | SN2
52 | SN2
52.6 | SN2
52.5 | SN2
52.1 | SN2
52 | SN2
51.8 | SN2
51 | SN2
51.6 | SN2
50.9 | SN2
51 | SN2
50.6 | SN2
51.3 | SN2
52.4 | SN2
51.8 | SN2
51.9 | SN2
52.1 | SN2
52.5 | SN2
52.6 | SN2
52.5 | SN2
52.7 | SN2
52.1 | SN2
52.5 | SN2
52.5 | SN2
52.6 | SN2
52.5 | SN2
52.2 | SN2
51.2 | SN2
48.9 | SN2
50.9 | SN2
50.9 | SN2
51 | SN2
50.6 | SN2
50.6 | SN2
50.8 | SN2
50.2 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
50.6 | SN2
50.5 | SN2
48.8 | SN2
49.7 | SN2
49.2 | SN2
49.2 | SN2
49.7 | SN2
49.3 | SN2
49.4 | SN2
49.6 | SN2
49.3 | SN2
49.6 | SN2
49.2 | SN2
49.5 | SN2
49.2 | SN2
49.6 | SN2
49.1 | SN2
48.8 | SN2
48.7 | SN2
49.1 | SN2
49.1 | SN2
48.8 | SN2
48.8 | SN2
48.4 | SN2
48.8 | SN2
49.3 | SN2
49.6 | SN2
50.1 | SN2
50.2 | SN2
51 | SN2
50.9 | SN2
51.4 | SN2
51.6 | SN2
51.4 | SN2
52 | SN2
52 | SN2
52.4 | SN2
52.5 | SN2
52.2 | SN2
52.4 | SN2
51.9 | SN2
51.7 | SN2
51.6 | SN2
51.2 | SN2
51.5 | SN2
51.3 | SN2
50.7 | SN2
50.2 | SN2
50.1 | SN2
50 | SN2
49.6 | SN2
49.7 | SN2
49.8 | SN2
49.3 | SN2
49.2 | SN2
49.3 | SN2
49.5 | SN2
49.2 | SN2
49.5 | SN2
49.4 | SN2
49.5 | SN2
49.5 | SN2
49.4 | SN2
49.6 | SN2
49.1 | SN2
49.3 | SN2
49.5 | SN2
49 | SN2
48.9 | SN2
49 | SN2
48.9 | SN2
49.1 | SN2
49.2 | SN2
49.4 | SN2
50.2 | SN2
50.7 | SN2
50.7 | SN2
51.1 | SN2
51.5 | SN2
52.1 | SN2
52.1 | SN2
51.4 | SN2
51.5 | SN2
51.8 | SN2
51.6 | SN2
51.7 | SN2
51.5 | SN2
51.4 | SN2
51.2 | SN2
51 | SN2
51.1 | SN2
51.1 | SN2
51.1 | SN2
50.9 | SN2
50.6 | SN2
50.8 | SN2
50.9 | SN2
51 | SN2
51.2 | SN2
51.2 | SN2
51.2 | SN2
51.2 | SN2
51.2 | SN2
51.4 | SN2
51.3 | SN2
51.4 | SN2
51.2 | SN2
51.3 | SN2
51.3 | SN2
51.3 | SN2
51.3 | SN2
51.3 | SN2
51.6 | SN2
51.3 | SN2
51.3 | SN2
51.4 | SN2
51.6 | SN2
51.6 | SN2
51.6 | SN2
51.9 | SN2
55.2 | SN2
52.4 | SN2
51.8 | SN2
51.2 | SN2
51.3 | SN2
51.4 | SN2
51.1 | SN2
50.3 | SN2
50.7 | SN2
50.1 | SN2
49.9 | SN2
50 | SN2
49.7 | SN2
49.8 | SN2
48.8 | SN2
48.8 | SN2
48.5 | SN2
48.6 | SN2
48.5 | SN2
48.3 | SN2
47.9 | SN2
48 | SN2
47.6 | SN2
47.4 | SN2
47.3 | SN2
47.6 | SN2
47.6 | SN2
47.4 | SN2
47.6 | SN2
47.4 | SN2
47.6 | SN2
47.5 | SN2
47.8 | SN2
47.8 | SN2
48 | SN2
48 | SN2
47.9 | SN2
47.9 | SN2
47.8 | SN2
47.8 | SN2
47.5 | SN2
47.7 | SN2
47.7 | SN2
47.7 | SN2
47.7 | SN2
48.2 | SN2
48.6 | SN2
49.1 | SN2
49.6 | SN2
49.9 | SN2
50.4 | SN2
50.5 | SN2
51 | SN2
50.8 | SN2
50.8 | SN2
50.4 | SN2
50.6 | SN2
50.9 | SN2
50.8 | SN2
50.1 | SN2
50 | SN2
49.9 | SN2
49.8 | SN2
49.6 | SN2
49.2 | SN2
48.9 | SN2
48.5 | SN2
48.5 | SN2
48.5 | SN2
48.4 | SN2
48.2 | SN2
48.2 | SN2
48.1 | SN2
48.3 | SN2
48.1 | SN2
48.2 | SN2
48.1 | SN2
47.9 | SN2
48.2 | SN2
48.2 | SN2
47.8 | SN2
48 | SN2
48.1 | SN2
47.7 | SN2
48 | SN2
48 | SN2
47.7 | SN2
47.3 | SN2
47.8 | SN2
47.8 | SN2
47.6 | SN2
47.9 | SN2
48.3 | SN2
48.8 | SN2
49 | SN2
49.8 | SN2
50.3 | SN2
50.6 | SN2
50.6 | SN2
50.3 | SN2
49.8 | SN2
50.2 | SN2
49.6 | SN2
49.9 | SN2
49.5 | SN2
49.4 | SN2
49.8 | SN2
49.6 | SN2
49.5 | SN2
49.2 | SN2
49.5 | SN2
49.2 | SN2
49.1 | SN2
48.6 | SN2
48.8 | SN2
48.6 | SN2
48.5 | SN2
47.9 | SN2
48 | SN2
48 | SN2
47.9 | SN2
47.9 | SN2
47.9 | SN2
48.1 | SN2
48 | SN2
47.8 | SN2
47.8 | SN2
47.9 | SN2
47.8 | SN2
48 | SN2
47.8 | SN2
47.5 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
50.5 | SN2
50.2 | SN2
50.5 | SN2
50 | SN2
50.4 | SN2
50 | SN2
50.2 | SN2
50.4 | SN2
50.3 | SN2
50.4 | SN2
50.6 | SN2
50.6 | SN2
50.7 | SN2
50.6 | SN2
50.6 | SN2
50.7 | SN2
50.6 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
57.3 | SN2
54 | SN2
52.8 | SN2
52 | SN2
51.4 | SN2
51.2 | SN2
51.3 | SN2
51 | SN2
50.7 | SN2
50.7 | SN2
50.3 | SN2
49.8 | SN2
49.9 | SN2
49.8 | SN2
49.4 | SN2
49.4 | SN2
49.3 | SN2
49.2 | SN2
49.2 | SN2
49.7 | SN2
49.3 | SN2
49.6 | SN2
49.5 | SN2
49.2 | SN2
49.5 | SN2
49.5 | SN2
49.9 | SN2
49.8 | SN2
49.7 | SN2
49.5 | SN2
49.7 | SN2
49.7 | SN2
49.7 | SN2
49.8 | SN2
49.4 | SN2
49.5 | SN2
49.5 | SN2
49.5 | SN2
49.5 | SN2
49.8 | SN2
49.9 | SN2
50.4 | SN2
52.8 | SN2
50.4 | SN2
49.5 | SN2
49.3 | SN2
49.4 | SN2
49.3 | SN2
49 | SN2
49.4 | SN2
49.3 | SN2
49.6 | SN2
49.4 | SN2
49.4 | SN2
48.8 | SN2
49.1 | SN2
48.8 | SN2
48.3 | SN2
48.5 | SN2
47.8 | SN2
47.8 | SN2
47.7 | SN2
47.1 | SN2
46.9 | SN2
47 | SN2
46.7 | SN2
46.4 | SN2
46.4 | SN2
46.5 | SN2
46.2 | SN2
46.3 | SN2
46.5 | SN2
46.6 | SN2
46.6 | SN2
47 | SN2
46.8 | SN2
46.8 | SN2
46.9 | SN2
47 | SN2
47.1 | SN2
46.8 | SN2
47 | SN2
47.3 | SN2
47.2 | SN2
47 | SN2
47.4 | SN2
47.2 | SN2
47.5 | SN2
47.6 | SN2
47.9 | SN2
47.9 | SN2
48.2 | SN2
48.9 | SN2
49.3 | SN2
49.7 | SN2
49.6 | SN2
50.5 | SN2
51 | SN2
49.7 | SN2
50.2 | SN2
49.5 | SN2
49.3 | SN2
50.2 | SN2
50.4 | SN2
49.8 | SN2
49.4 | SN2
49 | SN2
48.7 | SN2
48.2 | SN2
47.7 | SN2
47.4 | SN2
47.8 | SN2
48.1 | SN2
49.3 | SN2
49.7 | SN2
49.1 | SN2
49.1 | SN2
49.2 | SN2
49.2 | SN2
49.3 | SN2
49.3 | SN2
49 | SN2
49 | SN2
49 | SN2
48.9 | SN2
48.8 | SN2
49 | SN2
48.7 | SN2
49.7 | SN2
49.9 | SN2
50.3 | SN2
50.3 | SN2
50.6 | SN2
50.7 | SN2
51 | SN2
51.2 | SN2
51.4 | SN2
51.4 | SN2
51.9 | SN2
51.7 | SN2
51.7 | SN2
52.4 | SN2
56.8 | SN2
57.1 | SN2
53.4 | SN2
52.9 | SN2
52.5 | SN2
51.9 | SN2
51.4 | SN2
51.4 | SN2
51.4 | SN2
51 | SN2
50.6 | SN2
50.6 | SN2
50.2 | SN2
50.2 | SN2
49.9 | SN2
49.5 | SN2
49.5 | SN2
49.7 | SN2
49.9 | SN2
49.6 | SN2
49.6 | SN2
49.7 | SN2
49.8 | SN2
49.6 | SN2
49.5 | SN2
49.4 | SN2
49.4 | SN2
49.6 | SN2
49.4 | SN2
49.3 | SN2
49.2 | SN2
49.8 | SN2
50.2 | SN2
50.3 | SN2
50.4 | SN2
50.6 | SN2
50.4 | SN2
50.3 | SN2
50.9 | SN2
51 | SN2
51.2 | SN2
51.6 | SN2
51.7 | SN2
51.6 | SN2
52.1 | SN2
52.4 | SN2
51.9 | SN2
51.8 | SN2
51.6 | SN2
52 | SN2
52 | SN2
52.3 | SN2
51.5 | SN2
51.5 | SN2
50.9 | SN2
50.8 | SN2
51 | SN2
50.4 | SN2
50 | SN2
50 | SN2
50.1 | SN2
49.9 | SN2
49.9 | SN2
49.8 | SN2
49.7 | SN2
49.9 | SN2
49.6 | SN2
49.6 | SN2
49.5 | SN2
49.2 | SN2
49.6 | SN2
49.7 | SN2
49.6 | SN2
49.5 | SN2
49.7 | SN2
49.6 | SN2
49.3 | SN2
50.5 | SN2
50.7 | SN2
50.4 | SN2
51.7 | SN2
52.5 | SN2
52.2 | SN2
52.2 | SN2
52.4 | SN2
52.4 | SN2
52.5 | SN2
52.5 | SN2
52.7 | SN2
52.6 | SN2
53 | SN2
53.5 | SN2
53.8 | SN2
53.7 | SN2
53.7 | SN2
53.7 | SN2
53.7 | SN2
53.2 | SN2
53.1 | SN2
52.9 | SN2
51.7 | SN2
51.8 | SN2
52 | SN2
51.3 | SN2
51.1 | SN2
50.7 | SN2
50.7 | SN2
50.6 | SN2
50.4 | SN2
50.7 | SN2
51 | SN2
51.8 | SN2
51.7 | SN2
51.9 | SN2
52.2 | SN2
51.9 | SN2
51.7 | SN2
52 | SN2
51.8 | SN2
51.9 | SN2
51.7 | SN2
51.7 | SN2
51.6 | SN2
51.7 | SN2
51.5 | SN2
51.9 | SN2
51.6 | SN2
51.8 | SN2
51.6 | SN2
52 | SN2
51.9 | SN2
52 | SN2
52.2 | SN2
52.4 | SN2
52.4 | SN2
52.6 | SN2
52.5 | SN2
52.5 | SN2
53.8 | SN2
53.1 | SN2
52.8 | SN2
52.8 | SN2
52.4 | SN2
52.8 | SN2
52.9 | SN2
52.5 | SN2
51.8 | SN2
51.9 | SN2
51.5 | SN2
51.2 | SN2
50.6 | SN2
50.2 | SN2
50.3 | SN2
50 | SN2
49.9 | SN2
49.9 | SN2
49.7 | SN2
50 | SN2
50.1 | SN2
49.9 | SN2
49.9 | SN2
50.1 | SN2
49.9 | SN2
49.4 | SN2
49.6 | SN2
50 | SN2
50.2 | SN2
51 | SN2
52 | SN2
52.4 | SN2
52.5 | SN2
52.7 | SN2
52.8 | SN2
52.6 | SN2
52.5 | SN2
52.6 | SN2
52.5 | SN2
52.7 | SN2
52.9 | SN2
52.9 | SN2
53.5 | SN2
53.3 | SN2
53.2 | SN2
53.6 | SN2
54 | SN2
53.7 | SN2
54.3 | SN2
54 | SN2
53.2 | SN2
53.3 | SN2
51.4 | SN2
49.8 | SN2
49.4 | SN2
49.5 | SN2
49.8 | SN2
49.6 | SN2
49.6 | SN2
49.8 | SN2
49.2 | SN2
49.3 | SN2
49 | SN2
48.9 | SN2
49 | SN2
49.1 | SN2
48.6 | SN2
49.1 | SN2
48.9 | SN2
49 | SN2
48.9 | SN2
49.8 | SN2
50.1 | SN2
50.6 | SN2
52.1 | SN2
52.9 | SN2
53.1 | SN2
53.3 | SN2
53.7 | SN2
54.2 | SN2
54.2 | SN2
53.9 | SN2
54 | SN2
53.8 | SN2
53.5 | SN2
53.4 | SN2
53.5 | SN2
53.6 | SN2
53.8 | SN2
54.1 | SN2
53.5 | SN2
54.5 | SN2
55.1 | SN2
55.2 | SN2
54.7 | SN2
55.7 | SN2
55.9 | SN2
56.1 | SN2
56 | SN2
55.9 | SN2
55.8 | SN2
55.7 | SN2
55.3 | SN2
54.6 | SN2
54.2 | SN2
54.2 | SN2
53.7 | SN2
53.8 | SN2
53.7 | SN2
53.6 | SN2
53.7 | SN2
53.3 | SN2
54 | SN2
55 | SN2
55.3 | SN2
55.3 | SN2
55.3 | SN2
55.8 | SN2
55.7 | SN2
55.7 | SN2
55.5 | SN2
55.7 | SN2
55.4 | SN2
55.4 | SN2
55.6 | SN2
55.2 | SN2
55.2 | SN2
55.2 | SN2
55.3 | SN2
55.3 | SN2
55.3 | SN2
55.2 | SN2
55.5 | SN2
55.7 | SN2
55.7 | SN2
55.8 | SN2
56 | SN2
56.1 | SN2
56.5 | SN2
56.6 | SN2
56.5 | SN2
56.6 | SN2
55.9 | SN2
55.7 | SN2
55.2 | SN2
54.6 | SN2
54.2 | SN2
53.9 | SN2
53.6 | SN2
53.2 | SN2
53 | SN2
52.7 | SN2
52.7 | SN2
52.8 | SN2
52.4 | SN2
52.2 | SN2
52.4 | SN2
52.6 | SN2
51.9 | SN2
52.1 | SN2
51.9 | SN2
51.8 | SN2
51.7 | SN2
51.9 | SN2
52 | SN2
52.1 | SN2
51.9 | SN2
51.9 | SN2
51.9 | SN2
51.9 | SN2
51.6 | SN2
51.7 | SN2
51.8 | SN2
51.8 | SN2
51.8 | SN2
51.7 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.2 | SN2
52.5 | SN2
52.7 | SN2
52.8 | SN2
52.8 | SN2
52.5 | SN2
52.9 | SN2
53.4 | SN2
53.7 | SN2
53.5 | SN2
53.6 | SN2
53.3 | SN2
53.3 | SN2
52.8 | SN2
52 | SN2
52.1 | SN2
51.7 | SN2
51.5 | SN2
51.4 | SN2
51.2 | SN2
51.1 | SN2
51.2 | SN2
51 | SN2
51.1 | SN2
51 | SN2
50.8 | SN2
50.9 | SN2
50.8 | SN2
50.7 | SN2
51 | SN2
50.6 | SN2
50.7 | SN2
50.6 | SN2
50.5 | SN2
50.6 | SN2
50.4 | SN2
50.6 | SN2
50.3 | SN2
50.4 | SN2
50.2 | SN2
50.2 | SN2
50.3 | SN2
50.2 | SN2
50.2 | SN2
50.4 | SN2
50.9 | SN2
51.1 | SN2
51.4 | SN2
51.4 | SN2
51.1 | SN2
51.7 | SN2
51.9 | SN2
52.1 | SN2
52.1 | SN2
52.1 | SN2
51.5 | SN2
51.7 | SN2
51.7 | SN2
51.4 | SN2
51.6 | SN2
51.5 | SN2
51.5 | SN2
50.8 | SN2
50.6 | SN2
50.5 | SN2
50.2 | SN2
50.3 | SN2
50.1 | SN2
50.2 | SN2
49.8 | SN2
49.9 | SN2
49.8 | SN2
49.6 | SN2
49.7 | SN2
49.4 | SN2
49.1 | SN2
48.9 | SN2
49.1 | SN2
49 | SN2
48.4 | SN2
47.7 | SN2
47.6 | SN2
47.4 | SN2
47.1 | SN2
47.3 | SN2
47.3 | SN2
47 | SN2
47.2 | SN2
46.7 | SN2
46.5 | SN2
46.7 | SN2
47.1 | SN2
47.3 | SN2
47.6 | SN2
47.5 | SN2
48.1 | SN2
47.9 | SN2
48.1 | SN2
48 | SN2
47.5 | SN2
47.7 | SN2
47.7 | SN2
47.7 | SN2
47.6 | SN2
47.5 | SN2
47.7 | SN2
47.7 | SN2
47.1 | SN2
47.5 | SN2
46.7 | SN2
46.8 | SN2
46.4 | SN2
46 | SN2
46.2 | SN2
45.8 | SN2
46.1 | SN2
45.9 | SN2
45.8 | SN2
45.9 | SN2
45.8 | SN2
45.7 | SN2
46 | SN2
46 | SN2
45.8 | SN2
45.6 | SN2
45.6 | SN2
45.5 | SN2
45.6 | SN2
45.6 | SN2
45.7 | SN2
45.8 | SN2
45.5 | SN2
45.2 | SN2
45.1 | SN2
44.7 | SN2
45.9 | SN2
49.4 | SN2
49.5 | SN2
49.9 | SN2
49.9 | SN2
50.2 | SN2
50.1 | SN2
50.2 | SN2
50.4 | SN2
50.6 | SN2
50.4 | SN2
50.5 | SN2
50.5 | SN2
50.2 | SN2
50.1 | SN2
50 | SN2
50 | SN2
50 | SN2
49.2 | SN2
49.1 | SN2
48.7 | SN2
48.7 | SN2
48.7 | SN2
48.7 | SN2
48.3 | SN2
48.3 | SN2
48.4 | SN2
48.5 | SN2
48.2 | SN2
48.4 | SN2
48.3 | SN2
48.4 | SN2
48.4 | SN2
48.4 | SN2
48.4 | SN2
48.5 | SN2
48.4 | SN2
48.6 | SN2
48.6 | SN2
48.4 | SN2
48.8 | SN2
48.4 | SN2
48.6 | SN2
48.4 | SN2
48.7 | SN2
48.6 | SN2
48.8 | SN2
48.6 | SN2
48.9 | SN2
49 | SN2
49 | SN2
49 | SN2
49.5 | SN2
49.9 | SN2
49.9 | SN2
50.5 | SN2
50.3 | SN2
50.9 | SN2
50.2 | SN2
50.5 | SN2
50.5 | SN2
50.6 | SN2
50.9 | SN2
50.7 | SN2
50.6 | SN2
50.8 | SN2
50 | SN2
49.8 | SN2
49.3 | SN2
49.2 | SN2
49.4 | SN2
49.1 | SN2
49 | SN2
48.9 | SN2
49 | SN2
48.8 | SN2
48.8 | SN2
48.5 | SN2
48.5 | SN2
50.6 | SN2
52 | SN2
52.8 | SN2
52.7 | SN2
52.7 | SN2
52.4 | SN2
52.7 | SN2
52.9 | SN2
52.6 | SN2
52.6 | SN2
52.5 | SN2
52.1 | SN2
52.3 | SN2
52 | SN2
51.9 | SN2
51.8 | SN2
51.8 | SN2
52.1 | SN2
52.2 | SN2
52.7 | SN2
52.6 | SN2
52.8 | SN2
52.6 | SN2
52.4 | SN2
52.5 | SN2
52.7 | SN2
52.5 | SN2
52.4 | SN2
52.3 | SN2
52.1 | SN2
51.9 | SN2
52.1 | SN2
51.6 | SN2
51.7 | SN2
50.8 | SN2
50.4 | SN2
50.4 | SN2
50.2 | SN2
50.6 | SN2
51.3 | SN2
50.9 | SN2
50.9 | SN2
51.4 | SN2
51.8 | SN2
51.9 | SN2
51.9 | SN2
52.6 | SN2
51.9 | SN2
51.9 | SN2
51.9 | SN2
52.1 | SN2
51.9 | SN2
51.8 | SN2
52 | SN2
51.7 | SN2
51.7 | SN2
51.8 | SN2
51.6 | SN2
51.6 | SN2
51.5 | SN2
51.5 | SN2
51.5 | SN2
51.7 | SN2
51.6 | SN2
51.9 | SN2
52.5 | SN2
52.2 | SN2
52.7 | SN2
53.2 | SN2
53.3 | SN2
52.9 | SN2
52.8 | SN2
52.3 | SN2
52.2 | SN2
51.9 | SN2
52.3 | SN2
52.1 | SN2
52.2 | SN2
52.2 | SN2
52.1 | SN2
51.4 | SN2
50.1 | SN2
50.2 | SN2
50.2 | SN2
50.1 | SN2
50.1 | SN2
50.1 | SN2
50.1 | SN2
50.2 | SN2
49.9 | SN2
50.1 | SN2
50 | SN2
49.7 | SN2
49.9 | SN2
49.9 | SN2
50.7 | SN2
52.3 | SN2
53.4 | SN2
53.4 | SN2
53.7 | SN2
53.5 | SN2
53.7 | SN2
53.6 | SN2
53.7 | SN2
53.6 | SN2
53.4 | SN2
53.4 | SN2
53.3 | SN2
53.2 | SN2
53.1 | SN2
53.2 | SN2
53.4 | SN2
53.3 | SN2
53.4 | SN2
53.4 | SN2
54 | SN2
54 | SN2
53.5 | SN2
54.5 | SN2
6.9 | SN2
6 | SN2
7.1 | SN2
54.1 | SN2
52.8 | SN2
52.2 | SN2
51.8 | SN2
51.5 | SN2
51.2 | SN2
51 | SN2
50.6 | SN2
50.2 | SN2
50.3 | SN2
50 | SN2
50 | SN2
49.6 | SN2
49.6 | SN2
51.5 | SN2
52.5 | SN2
53.2 | SN2
53.6 | SN2
53.8 | SN2
54 | SN2
53.9 | SN2
54.2 | SN2
54.5 | SN2
54.2 | SN2
54.7 | SN2
54.5 | SN2
54.3 | SN2
54.2 | SN2
54.3 | SN2
53.9 | SN2
53.7 | SN2
53.8 | SN2
53.7 | SN2
53.9 | SN2
53.7 | SN2
53.5 | SN2
54.2 | SN2
54.2 | SN2
54 | SN2
54 | SN2
54.2 | SN2
53.8 | SN2
54.1 | SN2
53.7 | SN2
53.4 | SN2
53.2 | SN2
53 | SN2
53.1 | SN2
52.6 | SN2
52.4 | SN2
51.9 | SN2
52.3 | SN2
51.7 | SN2
51.2 | SN2
50.9 | SN2
51.1 | SN2
51 | SN2
50.7 | SN2
51 | SN2
50.8 | SN2
50.7 | SN2
50.5 | SN2
50.6 | SN2
50.6 | SN2
50.6 | SN2
50.5 | SN2
50.5 | SN2
50.6 | SN2
50.3 | SN2
50.6 | SN2
50.6 | SN2
50.6 | SN2
50.5 | SN2
50.3 | SN2
50.3 | SN2
50.2 | SN2
50.3 | SN2
50.4 | SN2
50.6 | SN2
50.6 | SN2
50.9 | SN2
50.3 | SN2
51.2 | SN2
50.8 | SN2
50.6 | SN2
51 | SN2
51 | SN2
50.7 | SN2
51.2 | SN2
51.4 | SN2
50.7 | SN2
51.4 | SN2
50.6 | SN2
51 | SN2
50.3 | SN2
49.9 | SN2
49.3 | SN2
48.9 | SN2
49 | SN2
48.9 | SN2
48.6 | SN2
48.6 | SN2
48.2 | SN2
48.5 | SN2
48.1 | SN2
48.1 | SN2
48.4 | SN2
47.7 | SN2
47.9 | SN2
47.7 | SN2
47.3 | SN2
47.3 | SN2
47.3 | SN2
46.7 | SN2
47.4 | SN2
46.6 | SN2
47.2 | SN2
47.4 | SN2
47 | SN2
47.2 | SN2
47 | SN2
46.9 | SN2
46.6 | SN2
46.9 | SN2
46.6 | SN2
46.8 | SN2
46.6 | SN2
46.5 | SN2
46.8 | SN2
46.7 | SN2
46.5 | SN2
46.5 | SN2
50.4 | SN2
50.3 | SN2
50.4 | SN2
50.8 | SN2
51 | SN2
50.5 | SN2
50.4 | SN2
49.9 | SN2
49.8 | SN2
49.4 | SN2
49.1 | SN2
49.2 | SN2
49.3 | SN2
49.1 | SN2
49.2 | SN2
48.8 | SN2
48.7 | SN2
48.8 | SN2
48.8 | SN2
48.8 | SN2
48.8 | SN2
49 | SN2
49 | SN2
48.9 | SN2
48.9 | SN2
49 | SN2
48.6 | SN2
49 | SN2
49.1 | SN2
48.9 | SN2
49.1 | SN2
49 | SN2
48.9 | SN2
49 | SN2
48.8 | SN2
49 | SN2
48.9 | SN2
48.9 | SN2
49.1 | SN2
48.9 | SN2
49.3 | SN2
49.6 | SN2
49.5 | SN2
49.7 | SN2
49.6 | SN2
50.3 | SN2
50.2 | SN2
50.5 | SN2
50.5 | SN2
50.2 | SN2
50.6 | SN2
50 | SN2
50.3 | SN2
49.2 | SN2
50.2 | SN2
48.7 | SN2
48.5 | SN2
48.7 | SN2
49 | SN2
48.9 | SN2
48.8 | SN2
48.8 | SN2
48.5 | SN2
48.6 | SN2
48.6 | SN2
48.5 | SN2
48.5 | SN2
48.4 | SN2
48.5 | SN2
48.4 | SN2
48.3 | SN2
48.5 | SN2
48.3 | SN2
48.3 | SN2
48.8 | SN2
48.5 | SN2
48.4 | SN2
48.3 | SN2
48.5 | SN2
48.1 | SN2
48 | SN2
48.1 | SN2
48.1 | SN2
48.1 | SN2
47.9 | SN2
48.2 | SN2
48.3 | SN2
48.6 | SN2
49.3 | SN2
49.2 | SN2
49.2 | SN2
49.1 | SN2
49.4 | SN2
50 | SN2
49.9 | SN2
49.9 | SN2
50.5 | SN2
50.3 | SN2
50.5 | SN2
50.3 | SN2
49.7 | SN2
49.7 | SN2
49.3 | SN2
49.4 | SN2
50.1 | SN2
50.1 | SN2
49.9 | SN2
49.9 | SN2
49.9 | SN2
49.9 | SN2
49.8 | SN2
49.6 | SN2
50 | SN2
49.7 | SN2
49.4 | SN2
49.7 | SN2
49.8 | SN2
49.8 | SN2
49.6 | SN2
49.5 | SN2
49.1 | SN2
49.4 | SN2
49.3 | SN2
49.6 | SN2
49.3 | SN2
49.3 | SN2
49.4 | SN2
49 | SN2
49.1 | SN2
49.4 | SN2
49.1 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
0 | SN2
53.9 | SN2
51.6 | SN2
50.8 | SN2
50.6 | SN2
49.9 | SN2
49.6 | SN2
49.6 | SN2
49.7 | SN2
49.5 | SN2
49.6 | SN2
49.2 | SN2
49 | SN2
48.9 | SN2
48.8 | SN2
48.8 | SN2
48.8 | SN2
49 | SN2
49.6 | SN2
51.1 | SN2
51.7 | SN2
52.5 | SN2
52.4 | SN2
53.1 | SN2
53.5 | SN2
53.3 | SN2
52.9 | SN2
52.9 | SN2
53 | SN2
52.7 | SN2
52.8 | SN2
52.5 | SN2
52.7 | SN2
52.5 | SN2
52.7 | SN2
52.7 | SN2
52.6 | SN2
52.4 | SN2
0 | SN2
53.8 | SN2
55.9 | SN2
54.8 | SN2
53.7 | SN2
52.6 | SN2
52.4 | SN2
52.4 | SN2
52.6 | SN2
52.8 | SN2
52.3 | SN2
52.1 | SN2
52.1 | SN2
51.5 | SN2
51.5 | SN2
51.2 | SN2
51.2 | SN2
50.3 | SN2
50.3 | SN2
50.1 | SN2
50.3 | SN2
50.1 | SN2
49.9 | SN2
49.6 | SN2
49.6 | SN2
49.7 | SN2
49.7 | SN2
49.7 | SN2
49.7 | SN2
49.6 | SN2
49.9 | SN2
49.9 | SN2
50.1 | SN2
50 | SN2
50.1 | SN2
49.7 | SN2
49.9 | SN2
50 | SN2
49.9 | SN2
49.8 | SN2
49.9 | SN2
49.8 | SN2
49.6 | SN2
49.9 | SN2
49.9 | SN2
49.7 | SN2
50.2 | SN2
50 | SN2
50.5 | SN2
51.3 | SN2
51 | SN2
50.9 | SN2
51.6 | SN2
51.1 | SN2
51 | SN2
51.3 | SN2
51.4 | SN2
51.3 | SN2
51.1 | SN2
50.8 | SN2
50.5 | SN2
50.5 | SN2
50.2 | SN2
50.2 | SN2
50.3 | SN2
50.5 | SN2
49.6 | SN2
49.6 | SN2
49.4 | SN2
49.5 | SN2
49.6 | SN2
49.6 | SN2
49.1 | SN2
49.4 | SN2
50.2 | SN2
51.4 | SN2
51.8 | SN2
51.9 | SN2
51.9 | SN2
51.7 | SN2
51.6 | SN2
51.7 | SN2
51.6 | SN2
51.4 | SN2
51.4 | SN2
51.2 | SN2
51.1 | SN2
51.1 | SN2
51 | SN2
50.9 | SN2
51 | SN2
51.1 | SN2
51.2 | SN2
51.2 | SN2
51.5 | SN2
51.9 | SN2
51.5 | SN2
51.9 | SN2
52 | SN2
51.6 | SN2
52 | SN2
51.8 | SN2
51.8 | SN2
52.1 | SN2
51.6 | SN2
51.7 | SN2
51.3 | SN2
50.9 | SN2
50.8 | SN2
50.9 | SN2
50.4 | SN2
50.4 | SN2
50.6 | SN2
51.2 | SN2
52.2 | SN2
52.3 | SN2
52.2 | SN2
52.1 | SN2
52 | SN2
52.1 | SN2
52.1 | SN2
52 | SN2
51.8 | SN2
51.7 | SN2
51.6 | SN2
51.4 | SN2
51.6 | SN2
51.4 | SN2
51.5 | SN2
51.3 | SN2
51.3 | SN2
51.2 | SN2
51.5 | SN2
51 | SN2
51.1 | SN2
51.1 | SN2
51.4 | SN2
51.2 | SN2
51.5 | SN2
51.7 | SN2
51.7 | SN2
51.7 | SN2
51.7 | SN2
51.6 | SN2
51.9 | SN2
51.8 | SN2
52.1 | SN2
51.5 | SN2
51.6 | SN2
51.7 | SN2
51.6 | SN2
51.4 | SN2
51.4 | SN2
51 | SN2
50.9 | SN2
50.3 | SN2
50 | SN2
50 | SN2
50.2 | SN2
49.8 | SN2
49.6 | SN2
49.7 | SN2
49.5 | SN2
49.3 | SN2
49.2 | SN2
49.4 | SN2
49.2 | SN2
49.2 | SN2
49.6 | SN2
49.3 | SN2
49.1 | SN2
49.3 | SN2
49.2 | SN2
49.3 | SN2
48.9 | SN2
49.5 | SN2
49 | SN2
48.9 | SN2
49 | SN2
49.1 | SN2
49 | SN2
48.9 | SN2
49 | SN2
48.9 | SN2
49.9 | SN2
54.6 | SN2
54.9 | SN2
55.3 | SN2
55.6 | SN2
55.9 | SN2
55.6 | SN2
56 | SN2
56.2 | SN2
56.1 | SN2
52.4 | SN2
51.8 | SN2
51.8 | SN2
51.3 | SN2
51.1 | SN2
50.4 | SN2
50.5 | SN2
49.9 | SN2
49.5 | SN2
49.1 | SN2
49.4 | SN2
49 | SN2
49 | SN2
48.7 | SN2
48.6 | SN2
48.7 | SN2
48.8 | SN2
48.5 | SN2
48.9 | SN2
48.7 | SN2
48.6 | SN2
48.6 | SN2
48.6 | SN2
48.5 | SN2
48.3 | SN2
48.4 | SN2
48.3 | SN2
48.5 | SN2
48.3 | SN2
48.4 | SN2
48.2 | SN2
48.2 | SN2
48.5 | SN2
48.3 | SN2
48.2 | SN2
48.3 | SN2
48.4 | SN2
48.5 | SN2
48.8 | SN2
49.3 | SN2
49.3 | SN2
49.4 | SN2
49.9 | SN2
50.3 | SN2
50.1 | SN2
49.9 | SN2
49.8 | SN2
49.9 | SN2
50.3 | SN2
50.2 | SN2
50 | SN2
50.2 | SN2
50.4 | SN2
49.6 | SN2
49.5 | SN2
48.9 | SN2
48.6 | SN2
48.5 | SN2
48.3 | SN2
48.2 | SN2
48.2 | SN2
48.1 | SN2
48.4 | SN2
47.8 | SN2
48 | SN2
48.1 | SN2
48 | SN2
48.2 | SN2
47.4 | SN2
48.1 | SN2
48.1 | SN2
48 | SN2
48.3 | SN2
48 | SN2
47.5 | SN2
47.6 | SN2
48 | SN2
47.5 | SN2
47.7 | SN2
47.7 | SN2
47.8 | SN2
47.5 | SN2
47.7 | SN2
48 | SN2
48.4 | SN2
48.6 | SN2
49 | SN2
49.1 | SN2
49.1 | SN2
49.7 | SN2
50.1 | SN2
50.1 | SN2
49.9 | SN2
50.2 | SN2
50.3 | SN2
49.9 | SN2
49.8 | SN2
49.4 | SN2
49.5 | SN2
49.2 | SN2
49.3 | SN2
49.2 | SN2
48.9 | SN2
48.5 | SN2
48.6 | SN2
48 | SN2
48.4 | SN2
48.3 | SN2
48.1 | SN2
48 | SN2
48.2 | SN2
48.1 | SN2
48.1 | SN2
48 | SN2
47.8 | SN2
47.8 | SN2
47.8 | SN2
47.9 | SN2
47.6 | SN2
47.8 | SN2
47.7 | SN2
47.8 | SN2
47.8 | SN2
47.7 | SN2
47.4 | SN2
47.6 | SN2
47.5 | SN2
47.7 | SN2
48 | SN2
48 | SN2
48.3 | SN2
48.8 | SN2
49.4 | SN2
49.6 | SN2
49.5 | SN2
49.6 | SN2
49.7 | SN2
49.8 | SN2
50 | SN2
50 | SN2
50.4 | SN2
49.9 | SN2
50 | SN2
49.8 | SN2
50 | SN2
49.8 | SN2
49.4 | SN2
49.5 | SN2
49.1 | SN2
49.5 | SN2
49 | SN2
48.5 | SN2
48.2 | SN2
48.1 | SN2
48 | SN2
47.9 | SN2
47.7 | SN2
47.6 | SN2
47.8 | SN2
47.7 | SN2
47.6 | SN2
47.7 | SN2
47.5 | SN2
47.7 | SN2
47.6 | SN2
47.5 | SN2
47.6 | SN2
47.5 | SN2
47.3 | SN2
47.3 | SN2
47.2 | SN2
47.4 | SN2
47.1 | SN2
47.3 | SN2
47.4 | SN2
47.9 | SN2
48 | SN2
48.2 | SN2
48.5 | SN2
48.7 | SN2
49 | SN2
49.1 | SN2
49.3 | SN2
49.3 | SN2
49.5 | SN2
49.8 | SN2
49.7 | SN2
49.7 | SN2
49.5 | SN2
49.7 | SN2
49.3 | SN2
49.3 | SN2
49 | SN2
48.9 | SN2
48.9 | SN2
48.7 | SN2
48.7 | SN2
48.2 | SN2
47.8 | SN2
47.8 | SN2
47.8 | SN2
47.5 | SN2
47.8 | SN2
47.6 | SN2
47.4 | SN2
48 | SN2
47.6 | SN2
47.3 | SN2
47.3 | SN2
47.3 | SN2
47.4 | SN2
47.1 | SN2
47.3 | SN2
47.2 | SN2
47.2 | SN2
47.5 | SN2
47.3 | SN2
47.2 | SN2
47.1 | SN2
47.2 | SN2
47.5 | SN2
47.2 | SN2
47.6 | SN2
48.5 | SN2
48.8 | SN2
48.9 | SN2
49.2 | SN2
49.3 | SN2
49 | SN2
49.1 | SN2
49.5 | SN2
49.3 | SN2
49.5 | SN2
49.5 | SN2
49.3 | SN2
49.4 | SN2
49.6 | SN2
49.2 | SN2
49 | SN2
48.7 | SN2
48.8 | SN2
48.7 | SN2
48.5 | SN2
48.2 | SN2
48.2 | SN2
47.9 | SN2
47.7 | SN2
47.9 | SN2
47.6 | SN2
47.6 | SN2
47.5 | SN2
47.6 | SN2
47.4 | SN2
47.4 | SN2
47.4 | SN2
47.3 | SN2
47.2 | SN2
47.3 | SN2
47.3 | SN2
47.3 | SN2
47.3 | SN2
47.2 | SN2
47.2 | SN2
47.3 | SN2
47.3 | SN2
47.1 | SN2
47.4 | SN2
47.5 | SN2
47.6 | SN2
48 | SN2
48.3 | SN2
48.4 | SN2
48.8 | SN2
48.8 | SN2
47.7 | SN2
48 | SN2
48.5 | SN2
48.3 | SN2
48.3 | SN2
47.9 | SN2
48 | SN2
48.2 | SN2
48.3 | SN2
48.3 | SN2
47.8 | SN2
47.7 | SN2
47.4 | SN2
47.2 | SN2
46.9 | SN2
46.5 | SN2
46.4 | SN2
46.6 | SN2
46 | SN2
46.3 | SN2
45.8 | SN2
46.1 | SN2
46.1 | SN2
47.2 | SN2
46.9 | SN2
47.1 | SN2
47 | SN2
46.8 | SN2
47 | SN2
46.9 | SN2
46.8 | SN2
46.6 | SN2
46.6 | SN2
46.5 | SN2
46.3 | SN2
46.2 | SN2
46.3 | SN2
46.8 | SN2
47.1 | SN2
46.8 | SN2
47.2 | SN2
47.1 | SN2
47.3 | SN2
47.5 | SN2
47.4 | SN2
47.3 | SN2
49.5 | SN2
49.5 | SN2
49.5 | SN2
49.6 | SN2
49.5 | SN2
49.7 | SN2
49.6 | SN2
49.3 | SN2
49.1 | SN2
48.9 | SN2
48.9 | SN2
49 | SN2
48.4 | SN2
48 | SN2
48 | SN2
47.8 | SN2
47.7 | SN2
47.6 | SN2
47.6 | SN2
47.5 | SN2
47.7 | SN2
47.8 | SN2
47.6 | SN2
47.4 | SN2
47.5 | SN2
47.6 | SN2
47.3 | SN2
47.4 | SN2
47.2 | SN2
47.2 | SN2
47.2 | SN2
47.5 | SN2
47.3 | SN2
47.4 | SN2
47.3 | SN2
47.1 | SN2
47.2 | SN2
47.5 | SN2
47.4 | SN2
47.6 | SN2
47.8 | SN2
48.3 | SN2
48.1 | SN2
48.4 | SN2
48.8 | SN2
48 | SN2
48.4 | SN2
48.6 | SN2
48.2 | SN2
48.7 | SN2
48.7 | SN2
49 | SN2
48.3 | SN2
48.2 | SN2
47.9 | SN2
47.9 | SN2
48 | SN2
47.9 | SN2
47.7 | SN2
47.3 | SN2
47.7 | SN2
47.2 | SN2
47.2 | SN2
47.5 | SN2
47.6 | SN2
47.2 | SN2
47.3 | SN2
47.3 | SN2
47.5 | SN2
47.1 | SN2
47.2 | SN2
47.1 | SN2
47.2 | SN2
47.1 | SN2
47.2 | SN2
46.9 | SN2
47.1 | SN2
46.9 | SN2
46.8 | SN2
47.1 | SN2
47.2 | SN2
47.3 | SN2
47.1 | SN2
47 | SN2
46.9 | SN2
47 | SN2
47.6 | SN2
47.7 | SN2
48 | SN2
48 | SN2
47.7 | SN2
48.1 | SN2
46.7 | SN2
46.6 | SN2
47.3 | SN2
46.9 | SN2
47 | SN2
47.2 | SN2
47.1 | SN2
47.2 | SN2
47 | SN2
47.1 | SN2
47.2 | SN2
46.5 | SN2
46.3 | SN2
46.3 | SN2
46 | SN2
46.3 | SN2
45.9 | SN2
45.8 | SN2
45.8 | SN2
45.7 | SN2
45.6 | SN2
45.6 | SN2
45.8 | SN2
45.7 | SN2
45.7 | SN2
46 | SN2
45.8 | SN2
45.6 | SN2
46 | SN2
45.6 | SN2
45.6 | SN2
45.5 | SN2
45.7 | SN2
45.5 | SN2
45.6 | SN2
45.3 | SN2
45.6 | SN2
45.7 | SN2
45.8 | SN2
45.8 | SN2
45.8 | SN2
46.7 | SN2
46.9 | SN2
47.3 | SN2
47.5 | SN2
47.5 | SN2
49 | SN2
49 | SN2
49 | SN2
49.4 | SN2
49.7 | SN2
49.3 | SN2
49.7 | SN2
49.4 | SN2
49.5 | SN2
49.2 | SN2
49.3 | SN2
49.2 | SN2
48.9 | SN2
49 | SN2
48.9 | SN2
48.4 | SN2
48 | SN2
48 | SN2
48.2 | SN2
47.6 | SN2
47.7 | SN2
47.6 | SN2
47.7 | SN2
48 | SN2
48 | SN2
47.8 | SN2
47.9 | SN2
48.1 | SN2
47.9 | SN2
48.1 | SN2
47.7 | SN2
47.9 | SN2
47.8 | SN2
47.8 | SN2
47.7 | SN2
47.8 | SN2
47.6 | SN2
47.4 | SN2
47.8 | SN2
48 | SN2
48.4 | SN2
49.3 | SN2
49 | SN2
48.9 | SN2
48.9 | SN2
48.6 | SN2
49.3 | SN2
49.2 | SN2
49.6 | SN2
50.1 | SN2
49.6 | SN2
49.8 | SN2
49.9 | SN2
49.7 | SN2
49.2 | SN2
49 | SN2
51.1 | SN2
50.4 | SN2
50.2 | SN2
50.1 | SN2
49.9 | SN2
49.7 | SN2
49.6 | SN2
49.7 | SN2
49.9 | SN2
49.6 | SN2
49.5 | SN2
49.4 | SN2
49.7 | SN2
49.4 | SN2
49.5 | SN2
49.8 | SN2
49.6 | SN2
49.6 | SN2
49.4 | SN2
49.6 | SN2
49.3 | SN2
49.5 | SN2
49.4 | SN2
49.4 | SN2
49.2 | SN2
49.1 | SN2
49.4 | SN2
49.1 | SN2
49 | SN2
49.5 | SN2
49.5 | SN2
49.8 | SN2
49.9 | SN2
49.9 | SN2
50.2 | SN2
50 | SN2
50 | SN2
49.8 | SN2
49.6 | SN2
50 | SN2
49.6 | SN2
50.1 | SN2
49.4 | SN2
48.9 | SN2
49.3 | SN2
49.2 | SN2
48.9 | SN2
48.4 | SN2
48.5 | SN2
48.3 | SN2
48.4 | SN2
48.4 | SN2
48.2 | SN2
48.1 | SN2
48.2 | SN2
48.5 | SN2
48.1 | SN2
48.3 | SN2
48.6 | SN2
48.5 | SN2
48.6 | SN2
48.7 | SN2
48.6 | SN2
48.5 | SN2
48.2 | SN2
48.6 | SN2
48.3 | SN2
48.3 | SN2
48.4 | SN2
48.3 | SN2
48.2 | SN2
48.1 | SN2
48.3 | SN2
48 | SN2
48.4 | SN2
48.1 | SN2
48 | SN2
48.7 | SN2
48.9 | SN2
49 | SN2
49.2 | SN2
49.2 | SN2
50.1 | SN2
49.9 | SN2
49.7 | SN2
49.4 | SN2
49.9 | SN2
49.9 | SN2
50.1 | SN2
49.5 | SN2
49.2 | SN2
49.1 | SN2
48.9 | SN2
48.9 | SN2
48.3 | SN2
48.1 | SN2
48.1 | SN2
48.3 | SN2
48 | SN2
48.3 | SN2
48.2 | SN2
48.1 | SN2
48 | SN2
48.3 | SN2
48.3 | SN2
47.9 | SN2
47.9 | SN2
47.8 | SN2
47.9 | SN2
48.1 | SN2
48.1 | SN2
47.7 | SN2
48 | SN2
47.9 | SN2
48.1 | SN2
48 | SN2
47.8 | SN2
47.9 | SN2
47.7 | SN2
47.8 | SN2
47.8 | SN2
48.1 | SN2
48.3 | SN2
48.3 | SN2
48.6 | SN2
48.9 | SN2
49 | SN2
49 | SN2
49.1 | SN2
47.9 | SN2
49.5 | SN2
48.3 | SN2
49.4 | SN2
49.6 | SN2
49.3 | SN2
49.5 | SN2
49.2 | SN2
49.1 | SN2
49.1 | SN2
49.1 | SN2
49 | SN2
48.9 | SN2
48.2 | SN2
47.9 | SN2
48 | SN2
47.8 | SN2
47.5 | SN2
47.6 | SN2
48 | SN2
47.6 | SN2
48.4 | SN2
48.2 | SN2
48.6 | SN2
48.7 | SN2
48.2 | SN2
48.2 | SN2
48.3 | SN2
48 | SN2
48.2 | SN2
48.2 | SN2
48.1 | SN2
47.9 | SN2
47.9 | SN2
48.2 | SN2
48.1 | SN2
47.9 | SN2
48.3 | SN2
48.2 | SN2
48.1 | SN2
48.6 | SN2
49 | SN2
48.6 | SN2
49.1 | SN2
48.9 | SN2
49.3 | SN2
49.1 | SN2
49.1 | SN2
49.3 | SN2
49.6 | SN2
49.3 | SN2
49.2 | SN2
48.8 | SN2
48.3 | SN2
48.3 | SN2
48.6 | SN2
48.2 | SN2
48 | SN2
48 | SN2
47.9 | SN2
47.4 | SN2
47.3 | SN2
47.1 | SN2
47.5 | SN2
47.1 | SN2
47.2 | SN2
47.2 | SN2
47.2 | SN2
47.3 | SN2
47.4 | SN2
47.3 | SN2
47.4 | SN2
47.1 | SN2
47.3 | SN2
47.3 | SN2
47.2 | SN2
47.2 | SN2
47 | SN2
47.2 | SN2
47.3 | SN2
47.2 | SN2
47.5 | SN2
47.1 | SN2
47.2 | SN2
47.1 | SN2
47.5 | SN2
47.4 | SN2
47.5 | SN2
47.9 | SN2
48.4 | SN2
48.3 | SN2
48.3 | SN2
48.6 | SN2
48.7 | SN2
48.7 | SN2
49.3 | SN2
49.6 | SN2
48.9 | SN2
48.8 | SN2
48.6 | SN2
49.1 | SN2
48.7 | SN2
48.1 | SN2
47.8 | SN2
48.1 | SN2
48.3 | SN2
48.2 | SN2
48.2 | SN2
48 | SN2
48 | SN2
48.1 | SN2
47.8 | SN2
48 | SN2
47.7 | SN2
47.9 | SN2
47.8 | SN2
47.9 | SN2
47.8 | SN2
48 | SN2
47.8 | SN2
48 | SN2
47.8 | SN2
47.7 | SN2
47.8 | SN2
48 | SN2
47.7 | SN2
47.6 | SN2
47.9 | SN2
47.7 | SN2
48 | SN2
47.6 | SN2
47.7 | SN2
47.6 | SN2
47.9 | SN2
48.2 | SN2
48.3 | SN2
48.4 | SN2
48.2 | SN2
48.8 | SN2
49 | SN2
49.4 | SN2
49.1 | SN2
49 | SN2
48.8 | SN2
48.8 | SN2
48.8 | SN2
48.2 | SN2
48.1 | SN2
48.4 | SN2
48 | SN2
47.9 | SN2
47.8 | SN2
47.5 | SN2
47.6 | SN2
47.5 | SN2
47.2 | SN2
47.3 | SN2
47.5 | SN2
47.3 | SN2
47.3 | SN2
47.3 | SN2
46.9 | SN2
47.2 | SN2
47.3 | SN2
47.4 | SN2
47.4 | SN2
47.3 | SN2
47 | SN2
47.1 | SN2
47.2 | SN2
47.3 | SN2
47.1 | SN2
48.3 | SN2
48.4 | SN2
48.7 | SN2
48.6 | SN2
48.8 | SN2
48.6 | SN2
48.7 | SN2
48.7 | SN2
48.8 | SN2
48.9 | SN2
48.8 | SN2
48.5 | SN2
49 | SN2
49 | SN2
49.2 | SN2
48.9 | SN2
49.4 | SN2
48.9 | SN2
49.2 | SN2
49.1 | SN2
48.8 | SN2
48.4 | SN2
48.1 | SN2
48 | SN2
47.7 | SN2
47.6 | SN2
48.1 | SN2
48.3 | SN2
48.3 | SN2
48.3 | SN2
48.4 | SN2
48.2 | SN2
48.4 | SN2
48.3 | SN2
48.7 | SN2
48.4 | SN2
48.3 | SN2
48.4 | SN2
48.3 | SN2
48.1 | SN2
48 | SN2
48.3 | SN2
48.1 | SN2
48 | SN2
48.2 | SN2
48.8 | SN2
48.5 | SN2
48.5 | SN2
48.8 | SN2
48.7 | SN2
48.4 | SN2
48.5 | SN2
48.4 | SN2
48.5 | SN2
48.5 | SN2
48.9 | SN2
49 | SN2
49.2 | SN2
49.1 | SN2
49.2 | SN2
49.3 | SN2
49.6 | SN2
49.2 | SN2
49.1 | SN2
49 | SN2
48.8 | SN2
48.2 | SN2
48.2 | SN2
48.3 | SN2
48.2 | SN2
48.4 | SN2
48 | SN2
47.7 | SN2
47.6 | SN2
47.6 | SN2
47.7 | SN2
47.6 | SN2
47.5 | SN2
47.6 | SN2
47.7 | SN2
47.5 | SN2
47.6 | SN2
47.7 | SN2
47.5 | SN2
47.4 | SN2
47.3 | SN2
47.5 | SN2
47.6 | SN2
47.4 | SN2
47.6 | SN2
47.4 | SN2
47.4 | SN2
47.3 | SN2
47.5 | SN2
47.4 | SN2
47.5 | SN2
47.6 | SN2
47.8 | SN2
53.6 | SN2
49.7 | SN2
49.2 | SN2
48 | SN2
48.2 | SN2
48.1 | SN2
47.7 | SN2
47.8 | SN2
47.8 | SN2
47.4 | SN2
47.2 | SN2
47.2 | SN2
47.8 | SN2
47.4 | SN2
47.2 | SN2
47.1 | SN2
46.9 | SN2
46.8 | SN2
46.8 | SN2
46.7 | SN2
46.6 | SN2
46.2 | SN2
46 | SN2
45.8 | SN2
45.8 | SN2
45.9 | SN2
45.9 | SN2
46.2 | SN2
46 | SN2
45.9 | SN2
45.7 | SN2
47.5 | SN2
48.2 | SN2
48 | SN2
48.1 | SN2
48.3 | SN2
48.5 | SN2
48.3 | SN2
48.3 | SN2
48.3 | SN2
48.4 | SN2
48.1 | SN2
48 | SN2
48 | SN2
47.9 | SN2
48.2 | SN2
48.3 | SN2
48.2 | SN2
48.8 | SN2
48.7 | SN2
48.5 | SN2
48.7 | SN2
49.2 | SN2
49 | SN2
49.1 | SN2
49.1 | SN2
49.3 | SN2
48.9 | SN2
49 | SN2
48.9 | SN2
49.1 | SN2
48.9 | SN2
48.7 | SN2
48.7 | SN2
48.6 | SN2
48.7 | SN2
48 | SN2
48 | SN2
48 | SN2
47.9 | SN2
48 | SN2
49.9 | SN2
50 | SN2
49.7 | SN2
50.6 | SN2
51 | SN2
50.5 | SN2
50.3 | SN2
50.8 | SN2
50.3 | SN2
50.3 | SN2
50.2 | SN2
50.1 | SN2
49.8 | SN2
49.8 | SN2
49.7 | SN2
49.7 | SN2
49.4 | SN2
49.5 | SN2
49.7 | SN2
49.6 | SN2
49.3 | SN2
49.6 | SN2
49.7 | SN2
50.1 | SN2
49.9 | SN2
50.1 | SN2
50.1 | SN2
50.3 | SN2
50.9 | SN2
50.1 | SN2
50.4 | SN2
49.8 | SN2
50.2 | SN2
50.5 | SN2
50.8 | SN2
50.3 | SN2
50.4 | SN2
50.4 | SN2
49.9 | SN2
50.1 | SN2
49.4 | SN2
49.5 | SN2
49.2 | SN2
48.8 | SN2
48.3 | SN2
48 | SN2
48.2 | SN2
48.1 | SN2
48.2 | SN2
48 | SN2
48 | SN2
48 | SN2
48.1 | SN2
47.9 | SN2
48.2 | SN2
48.1 | SN2
47.9 | SN2
47.9 | SN2
47.7 | SN2
47.7 | SN2
47.5 | SN2
47.6 | SN2
47.6 | SN2
47.3 | SN2
47.5 | SN2
47.3 | SN2
47.2 | SN2
47.3 | SN2
47.7 | SN2
48 | SN2
48.5 | SN2
48.6 | SN2
49 | SN2
48.8 | SN2
49.2 | SN2
49.7 | SN2
49.8 | SN2
49.7 | SN2
50.2 | SN2
49.4 | SN2
49.6 | SN2
50.2 | SN2
49.6 | SN2
49.1 | SN2
49.5 | SN2
49 | SN2
48.8 | SN2
48.8 | SN2
48.4 | SN2
47.9 | SN2
47.8 | SN2
47.8 | SN2
47.7 | SN2
47.7 | SN2
47.5 | SN2
47.7 | SN2
47.4 | SN2
47.5 | SN2
47.6 | SN2
47.4 | SN2
47.3 | SN2
47.4 | SN2
47.2 | SN2
47 | SN2
47.1 | SN2
47.2 | SN2
47.2 | SN2
47.1 | SN2
47.1 | SN2
47.1 | SN2
47 | SN2
46.6 | SN2
46.9 | SN2
47.5 | SN2
47.4 | SN2
47.6 | SN2
48.1 | SN2
48.6 | SN2
48.9 | SN2
49.4 | SN2
49.7 | SN2
49.8 | SN2
50.6 | SN2
50.7 | SN2
50.6 | SN2
50.4 | SN2
50.4 | SN2
50.2 | SN2
50 | SN2
50.1 | SN2
49.9 | SN2
50 | SN2
49.6 | SN2
49.5 | SN2
49.1 | SN2
48.6 | SN2
48.4 | SN2
48.4 | SN2
48.4 | SN2
48.4 | SN2
48.3 | SN2
48.3 | SN2
48.2 | SN2
48.2 | SN2
48.2 | SN2
47.9 | SN2
48 | SN2
48.1 | SN2
47.8 | SN2
47.9 | SN2
47.8 | SN2
47.7 | SN2
47.4 | SN2
47.6 | SN2
47.5 | SN2
47.2 | SN2
46.6 | SN2
46.7 | SN2
46.4 | SN2
46.3 | SN2
46.9 | SN2
47 | SN2
47 | SN2
49.5 | SN2
48.8 | SN2
48.7 | SN2
48.7 | SN2
49.3 | SN2
48.9 | SN2
49.4 | SN2
49 | SN2
49.2 | SN2
48.6 | SN2
49 | SN2
48.7 | SN2
48.6 | SN2
48.6 | SN2
47.5 | SN2
47.2 | SN2
47.2 | SN2
47 | SN2
46.9 | SN2
46.5 | SN2
46.9 | SN2
46.6 | SN2
46.6 | SN2
46.7 | SN2
46.6 | SN2
46.5 | SN2
46.4 | SN2
46.2 | SN2
46.4 | SN2
46.3 | SN2
46.3 | SN2
46.6 | SN2
46.5 | SN2
46.2 | SN2
46.2 | SN2
46.2 | SN2
46 | SN2
46.2 | SN2
46 | SN2
46.2 | SN2
45.9 | SN2
45.9 | SN2
46.2 | SN2
47 | SN2
48 | SN2
47 | SN2
48.1 | SN2
48.4 | SN2
48.2 | SN2
48.2 | SN2
48.7 | SN2
49.6 | SN2
49.8 | SN2
50 | SN2
50 | SN2
50 | SN2
49.4 | SN2
49.4 | SN2
49.1 | SN2
49.3 | SN2
49.2 | SN2
48.6 | SN2
48.6 | SN2
48.1 | SN2
47.6 | SN2
47.5 | SN2
47.1 | SN2
47.2 | SN2
47.1 | SN2
47.2 | SN2
47.1 | SN2
47 | SN2
47.1 | SN2
46.7 | SN2
47.1 | SN2
46.5 | SN2
46.8 | SN2
46.7 | SN2
46.3 | SN2
46.5 | SN2
45.9 | SN2
46.3 | SN2
45.6 | SN2
45.9 | SN2
45.6 | SN2
45.6 | SN2
44.6 | SN2
44.8 | SN2
45 | SN2
45.3 | SN2
45.2 | SN2
45.4 | SN2
47.5 | SN2
48.3 | SN2
47.9 | SN2
47.9 | SN2
48 | SN2
48.6 | SN2
48.5 | SN2
48.2 | SN2
48.2 | SN2
48.1 | SN2
47.7 | SN2
47.9 | SN2
47.7 | SN2
47.1 | SN2
47.4 | SN2
46.9 | SN2
46.6 | SN2
46 | SN2
45.8 | SN2
45.5 | SN2
45.6 | SN2
45.3 | SN2
45.4 | SN2
45.4 | SN2
45.3 | SN2
45 | SN2
45 | SN2
45.2 | SN2
44.9 | SN2
44.9 | SN2
45 | SN2
44.7 | SN2
44.9 | SN2
44.4 | SN2
44.7 | SN2
44.8 | SN2
44.6 | SN2
44.8 | SN2
44.4 | SN2
44.5 | SN2
44.7 | SN2
44.7 | SN2
45 | SN2
44.8 | SN2
45.2 | SN2
45.4 | SN2
45.6 | SN2
46.2 | SN2
46.3 | SN2
46.6 | SN2
46.8 | SN2
46.7 | SN2
46.5 | SN2
46.9 | SN2
46.6 | SN2
47 | SN2
47.1 | SN2
46.9 | SN2
47 | SN2
47 | SN2
46.5 | SN2
46.8 | SN2
46.1 | SN2
45.8 | SN2
45.8 | SN2
45.4 | SN2
45.5 | SN2
45.3 | SN2
45.2 | SN2
45.2 | SN2
45.3 | SN2
45.4 | SN2
45.8 | SN2
45.3 | SN2
45.3 | SN2
45.5 | SN2
45.3 | SN2
45 | SN2
45.4 | SN2
45.3 | SN2
45.1 | SN2
45 | SN2
45 | SN2
45 | SN2
45.2 | SN2
45.1 | SN2
44.9 | SN2
44.7 | SN2
44.8 | SN2
45.5 | SN2
46.1 | SN2
46 | SN2
46.1 | SN2
46.8 | SN2
46.2 | SN2
46.4 | SN2
46.4 | SN2
46.7 | SN2
46.1 | SN2
50.1 | SN2
48.2 | SN2
47.6 | SN2
46.5 | SN2
46.8 | SN2
46.9 | SN2
45.9 | SN2
45.3 | SN2
45.8 | SN2
45.3 | SN2
44.9 | SN2
44.5 | SN2
44.5 | SN2
45.8 | SN2
45.7 | SN2
45.7 | SN2
45.4 | SN2
45.4 | SN2
45.2 | SN2
45.6 | SN2
45.7 | SN2
45.6 | SN2
45.7 | SN2
45.6 | SN2
45.4 | SN2
45.5 | SN2
45.1 | SN2
45.1 | SN2
45.4 | SN2
45.3 | SN2
45.1 | SN2
45.3 | SN2
45 | SN2
45 | SN2
44.9 | SN2
45.2 | SN2
45.2 | SN2
45 | SN2
45.4 | SN2
45.9 | SN2
46.9 | SN2
46.9 | SN2
46.5 | SN2
47 | SN2
47.1 | SN2
47.5 | SN2
47.5 | SN2
47.4 | SN2
47.6 | SN2
47.3 | SN2
47.6 | SN2
47.6 | SN2
47 | SN2
46.6 | SN2
47 | SN2
46.5 | SN2
46.1 | SN2
46.1 | SN2
46 | SN2
46 | SN2
45.8 | SN2
45.6 | SN2
45.6 | SN2
45.7 | SN2
45.7 | SN2
46 | SN2
45.8 | SN2
45.6 | SN2
45.3 | SN2
45.7 | SN2
45.2 | SN2
44.9 | SN2
45.3 | SN2
44.7 | SN2
44.6 | SN2
44.5 | SN2
44.6 | SN2
44.5 | SN2
44.4 | SN2
44.2 | SN2
44.3 | SN2
44 | SN2
44.4 | SN2
44.4 | SN2
44.7 | SN2
44.9 | SN2
45.2 | SN2
45.5 | SN2
45.8 | SN2
46.2 | SN2
46.1 | SN2
46.2 | SN2
46.4 | SN2
46.1 | SN2
46.4 | SN2
46.4 | SN2
46.4 | SN2
45.8 | SN2
45.8 | SN2
45.6 | SN2
45.3 | SN2
45.4 | SN2
45.2 | SN2
44.5 | SN2
44.4 | SN2
44.3 | SN2
44.4 | SN2
44.1 | SN2
44.2 | SN2
44.1 | SN2
43.9 | SN2
43.9 | SN2
43.8 | SN2
43.8 | SN2
43.8 | SN2
43.8 | SN2
43.7 | SN2
43.6 | SN2
43.4 | SN2
43.5 | SN2
43.4 | SN2
43.3 | SN2
43.3 | SN2
43.1 | SN2
43.3 | SN2
43.2 | SN2
43.3 | SN2
43.2 | SN2
43.4 | SN2
43.8 | SN2
43.8 | SN2
44.1 | SN2
44.2 | SN2
44.3 | SN2
44.8 | SN2
44.9 | SN2
45.5 | SN2
45.3 | SN2
45.6 | SN2
45.3 | SN2
44.9 | SN2
45 | SN2
44.7 | SN2
44.7 | SN2
44.6 | SN2
44 | SN2
43.8 | SN2
43.9 | SN2
44 | SN2
43.3 | SN2
43.4 | SN2
42.9 | SN2
42.8 | SN2
43 | SN2
43.1 | SN2
42.9 | SN2
43.1 | SN2
43.3 | SN2
42.8 | SN2
42.8 | SN2
42.6 | SN2
42.5 | SN2
42.6 | SN2
42.4 | SN2
42.6 | SN2
42.3 | SN2
42.4 | SN2
42.5 | SN2
42.7 | SN2
42.3 | SN2
42.2 | SN2
42.6 | SN2
42.5 | SN2
42.3 | SN2
42.3 | SN2
42.5 | SN2
42.9 | SN2
43.2 | SN2
43.4 | SN2
43.3 | SN2
43.5 | SN2
43.8 | SN2
43.8 | SN2
44 | SN2
44.5 | SN2
44 | SN2
44.3 | SN2
44.2 | SN2
44.3 | SN2
44.5 | SN2
44.3 | SN2
44.1 | SN2
43.4 | SN2
43.2 | SN2
43 | SN2
42.8 | SN2
42.7 | SN2
43 | SN2
42.6 | SN2
42.5 | SN2
42.3 | SN2
42.6 | SN2
42.5 | SN2
42.5 | SN2
43 | SN2
42.7 | SN2
42.4 | SN2
42.6 | SN2
42.6 | SN2
42.5 | SN2
42.5 | SN2
42.3 | SN2
42.2 | SN2
42 | SN2
41.9 | SN2
42 | SN2
41.9 | SN2
41.8 | SN2
41.8 | SN2
42.2 | SN2
42 | SN2
42.8 | SN2
42.6 | SN2
42.9 | SN2
43.4 | SN2
43.4 | SN2
43.5 | SN2
43.6 | SN2
43.9 | SN2
43.8 | SN2
44.4 | SN2
44.6 | SN2
44.6 | SN2
44.6 | SN2
44.7 | SN2
44.1 | SN2
43.8 | SN2
43.7 | SN2
43.5 | SN2
43.5 | SN2
42.9 | SN2
42.5 | SN2
42.6 | SN2
42.5 | SN2
42.4 | SN2
42.4 | SN2
42.1 | SN2
42.3 | SN2
42.3 | SN2
42.3 | SN2
42.6 | SN2
42.6 | SN2
42.1 | SN2
42.6 | SN2
42 | SN2
42.3 | SN2
42.1 | SN2
41.9 | SN2
42.1 | SN2
42 | SN2
42.1 | SN2
41.8 | SN2
41.6 | SN2
41.6 | SN2
41.3 | SN2
41.3 | SN2
41.8 | SN2
41.8 | SN2
42.2 | SN2
42.7 | SN2
42.7 | SN2
43.3 | SN2
43.7 | SN2
43.9 | SN2
43.9 | SN2
45.4 | SN2
45.2 | SN2
45.3 | SN2
45.4 | SN2
45.3 | SN2
45.6 | SN2
45.4 | SN2
45.5 | SN2
45.6 | SN2
44.3 | SN2
44.3 | SN2
44.1 | SN2
44.1 | SN2
44.2 | SN2
44.1 | SN2
43.9 | SN2
43.8 | SN2
43.7 | SN2
43.7 | SN2
43.9 | SN2
44 | SN2
44.1 | SN2
43.9 | SN2
44 | SN2
43.5 | SN2
43.5 | SN2
43.6 | SN2
43.4 | SN2
43.6 | SN2
43.3 | SN2
43.3 | SN2
43.4 | SN2
43.3 | SN2
43.2 | SN2
43.6 | SN2
43.1 | SN2
43.1 | SN2
43.1 | SN2
43.6 | SN2
44.1 | SN2
44.3 | SN2
44.9 | SN2
44.8 | SN2
45.1 | SN2
45.8 | SN2
45.8 | SN2
46.4 | SN2
46.5 | SN2
46.8 | SN2
46.7 | SN2
46.6 | SN2
46.6 | SN2
46.6 | SN2
46.1 | SN2
46.2 | SN2
46 | SN2
45.8 | SN2
45.7 | SN2
45.3 | SN2
44.9 | SN2
45.2 | SN2
44.8 | SN2
44.8 | SN2
45.1 | SN2
45 | SN2
45.2 | SN2
44.8 | SN2
44.9 | SN2
44.8 | SN2
44.6 | SN2
44.7 | SN2
44.9 | SN2
44.7 | SN2
44.5 | SN2
44.7 | SN2
44.8 | SN2
44.5 | SN2
44.6 | SN2
44.5 | SN2
44.3 | SN2
44.4 | SN2
44.2 | SN2
44.4 | SN2
44.4 | SN2
44.8 | SN2
45.5 | SN2
45.6 | SN2
46.1 | SN2
46.3 | SN2
46.8 | SN2
46.5 | SN2
46.8 | SN2
46.6 | SN2
46.8 | SN2
47.4 | SN2
46.9 | SN2
46.9 | SN2
46.8 | SN2
47 | SN2
47 | SN2
46.9 | SN2
46.8 | SN2
46.7 | SN2
46.1 | SN2
45.9 | SN2
45.8 | SN2
45.9 | SN2
45.5 | SN2
45.7 | SN2
45.5 | SN2
45.3 | SN2
45.4 | SN2
45.4 | SN2
45.5 | SN2
45.3 | SN2
45.5 | SN2
45.1 | SN2
45.5 | SN2
45.3 | SN2
45.2 | SN2
45 | SN2
45.3 | SN2
45 | SN2
44.9 | SN2
44.9 | SN2
45 | SN2
45.1 | SN2
45 | SN2
45.2 | SN2
45.1 | SN2
44.9 | SN2
45.7 | SN2
45.9 | SN2
46.5 | SN2
46.2 | SN2
47.8 | SN2
47.8 | SN2
48.1 | SN2
47.9 | SN2
47.9 | SN2
47.8 | SN2
48 | SN2
47.9 | SN2
47.4 | SN2
47.5 | SN2
47.7 | SN2
47.4 | SN2
47.4 | SN2
47.6 | SN2
47 | SN2
46.9 | SN2
46.9 | SN2
46.7 | SN2
46.7 | SN2
46.6 | SN2
46.8 | SN2
46.6 | SN2
46.4 | SN2
46.6 | SN2
46.5 | SN2
46.8 | SN2
46.6 | SN2
46.6 | SN2
46.5 | SN2
46.7 | SN2
46.7 | SN2
46.8 | SN2
46.8 | SN2
46.6 | SN2
46.7 | SN2
46.6 | SN2
46.4 | SN2
46.2 | SN2
46.5 | SN2
46.5 | SN2
46.4 | SN2
46.8 | SN2
47.3 | SN2
46.9 | SN2
47.1 | SN2
47.4 | SN2
47.5 | SN2
47.6 | SN2
47.8 | SN2
47.4 | SN2
47.4 | SN2
47.5 | SN2
48.1 | SN2
48.8 | SN2
48.8 | SN2
48.8 | SN2
48.7 | SN2
48.3 | SN2
48.1 | SN2
48 | SN2
48.1 | SN2
48.1 | SN2
47.5 | SN2
47.6 | SN2
47.6 | SN2
47.3 | SN2
47.4 | SN2
47.8 | SN2
48 | SN2
48.1 | SN2
48 | SN2
48 | SN2
47.8 | SN2
47.7 | SN2
47.6 | SN2
47.9 | SN2
48 | SN2
47.5 | SN2
47.7 | SN2
48 | SN2
47.5 | SN2
47.4 | SN2
47.9 | SN2
47.4 | SN2
47.7 | SN2
47.5 | SN2
47.9 | SN2
47.6 | SN2
47.7 | SN2
48.1 | SN2
47.8 | SN2
48 | SN2
47.7 | SN2
48.4 | SN2
48.7 | SN2
48.5 | SN2
48.5 | SN2
48.7 | SN2
48.7 | SN2
49.1 | SN2
49 | SN2
49 | SN2
48.8 | SN2
48.6 | SN2
48.5 | SN2
48.6 | SN2
48 | SN2
47.8 | SN2
47.7 | SN2
47.5 | SN2
47.8 | SN2
47.7 | SN2
47.5 | SN2
47.5 | SN2
47.4 | SN2
47.3 | SN2
47.1 | SN2
47.4 | SN2
47.3 | SN2
47 | SN2
46.9 | SN2
47 | SN2
47.1 | SN2
47.2 | SN2
47.1 | SN2
47 | SN2
47.1 | SN2
47 | SN2
47.2 | SN2
46.9 | SN2
47.3 | SN2
46.9 | SN2
47.1 | SN2
47.2 | SN2
47.4 | SN2
47.3 | SN2
47.2 | SN2
47.9 | SN2
48.1 | SN2
48.4 | SN2
48 | SN2
47.9 | SN2
48.3 | SN2
48.6 | SN2
48.8 | SN2
48.4 | SN2
48.2 | SN2
48.2 | SN2
48 | SN2
47.5 | SN2
46.7 | SN2
46.6 | SN2
46.2 | SN2
46 | SN2
46.5 | SN2
46.3 | SN2
46.2 | SN2
46.3 | SN2
46.5 | SN2
46.1 | SN2
46.3 | SN2
46.5 | SN2
46 | SN2
46.4 | SN2
46.1 | SN2
46.3 | SN2
46 | SN2
46.1 | SN2
46 | SN2
46.1 | SN2
46 | SN2
45.9 | SN2
46 | SN2
46.1 | SN2
45.9 | SN2
45.7 | SN2
45.8 | SN2
45.5 | SN2
45.9 | SN2
46 | SN2
46.4 | SN2
46.5 | SN2
46.5 | SN2
45.9 | SN2
45.8 | SN2
46.2 | SN2
46.3 | SN2
48.8 | SN2
46.5 | SN2
49.3 | SN2
50.1 | SN2
47.7 | SN2
47.2 | SN2
49.2 | SN2
48.9 | SN2
48.7 | SN2
49 | SN2
49 | SN2
48.5 | SN2
48.5 | SN2
48.5 | SN2
48.2 | SN2
48.1 | SN2
48.1 | SN2
48 | SN2
47.9 | SN2
48.1 | SN2
47.9 | SN2
47.8 | SN2
47.8 | SN2
47.8 | SN2
47.8 | SN2
48 | SN2
47.4 | SN2
47.5 | SN2
47.2 | SN2
47.3 | SN2
47.3 | SN2
47.5 | SN2
47.3 | SN2
47.2 | SN2
47.1 | SN2
47.1 | SN2
47.2 | SN2
47.1 | SN2
47.5 | SN2
47.5 | SN2
47.5 | SN2
48.1 | SN2
47.7 | SN2
48.8 | SN2
48.6 | SN2
49.2 | SN2
48.9 | SN2
48.9 | SN2
49.1 | SN2
49.1 | SN2
49.1 | SN2
48.8 | SN2
48.9 | SN2
48.5 | SN2
48.6 | SN2
48.6 | SN2
48.4 | SN2
48.6 | SN2
48.3 | SN2
48.2 | SN2
48 | SN2
48.3 | SN2
48.2 | SN2
48 | SN2
47.8 | SN2
48.1 | SN2
48.2 | SN2
47.9 | SN2
48.1 | SN2
47.8 | SN2
48 | SN2
48.1 | SN2
47.7 | SN2
47.9 | SN2
47.9 | SN2
47.7 | SN2
47.7 | SN2
48 | SN2
48 | SN2
48 | SN2
47.9 | SN2
48 | SN2
47.7 | SN2
47.7 | SN2
47.9 | SN2
48 | SN2
48 | SN2
48.3 | SN2
48.7 | SN2
48.6 | SN2
48.9 | SN2
49.2 | SN2
49.3 | SN2
49.2 | SN2
49.7 | SN2
49.7 | SN2
49.7 | SN2
49.9 | SN2
49.6 | SN2
49.7 | SN2
51.4 | SN2
49.3 | SN2
48.7 | SN2
48.4 | SN2
48.6 | SN2
48.5 | SN2
48.3 | SN2
48 | SN2
48 | SN2
48.1 | SN2
48 | SN2
48 | SN2
48 | SN2
48.3 | SN2
48.1 | SN2
48.2 | SN2
48.3 | SN2
48 | SN2
48.1 | SN2
48.3 | SN2
48.2 | SN2
47.9 | SN2
48.1 | SN2
48.1 | SN2
48.3 | SN2
48.1 | SN2
48.2 | SN2
47.9 | SN2
47.4 | SN2
47.4 | SN2
47.8 | SN2
48.3 | SN2
48.3 | SN2
48.6 | SN2
48.9 | SN2
48.9 | SN2
49.1 | SN2
49.2 | SN2
49.5 | SN2
49.6 | SN2
49.8 | SN2
49.4 | SN2
49.9 | SN2
49.8 | SN2
49.4 | SN2
49.3 | SN2
49 | SN2
49 | SN2
48.8 | SN2
48.8 | SN2
48.6 | SN2
48.3 | SN2
48 | SN2
48.1 | SN2
47.9 | SN2
48 | SN2
47.9 | SN2
48 | SN2
47.9 | SN2
48 | SN2
48 | SN2
47.8 | SN2
47.7 | SN2
47.7 | SN2
47.8 | SN2
47.7 | SN2
47.7 | SN2
47.4 | SN2
47.4 | SN2
47.5 | SN2
47.4 | SN2
47.4 | SN2
47.4 | SN2
47.4 | SN2
47.1 | SN2
47.3 | SN2
47.1 | SN2
47.2 | SN2
47.8 | SN2
48.1 | SN2
48.4 | SN2
48.5 | SN2
49.1 | SN2
49.2 | SN2
49.2 | SN2
49.7 | SN2
49.2 | SN2
49.7 | SN2
49.5 | SN2
49.6 | SN2
49.2 | SN2
49.6 | SN2
49.6 | SN2
49.1 | SN2
48.7 | SN2
48.3 | SN2
48.5 | SN2
48.3 | SN2
48.1 | SN2
47.9 | SN2
47.9 | SN2
48 | SN2
48 | SN2
47.7 | SN2
48.2 | SN2
47.6 | SN2
47.8 | SN2
48 | SN2
47.6 | SN2
47.9 | SN2
47.6 | SN2
47.8 | SN2
47.6 | SN2
47.5 | SN2
47.5 | SN2
47.6 | SN2
47.4 | SN2
47.4 | SN2
47.5 | SN2
47.3 | SN2
47.3 | SN2
47.3 | SN2
47.3 | SN2
47.1 | SN2
47.2 | SN2
48 | SN2
48.4 | SN2
48.9 | SN2
48.8 | SN2
49.1 | SN2
49 | SN2
49.2 | SN2
49.2 | SN2
49.1 | SN2
49.5 | SN2
48.8 | SN2
49.5 | SN2
49.2 | SN2
49.1 | SN2
49.3 | SN2
48.5 | SN2
48.7 | SN2
48.3 | SN2
48.4 | SN2
48.2 | SN2
47.9 | SN2
48 | SN2
47.8 | SN2
47.8 | SN2
47.7 | SN2
47.7 | SN2
47.8 | SN2
48.1 | SN2
47.9 | SN2
48 | SN2
48 | SN2
47.7 | SN2
47.9 | SN2
47.7 | SN2
47.7 | SN2
47.7 | SN2
47.6 | SN2
47.8 | SN2
47.6 | SN2
47.4 | SN2
47.6 | SN2
47.8 | SN2
47.7 | SN2
47.4 | SN2
47.7 | SN2
48 | SN2
48.1 | SN2
47.9 | SN2
48.7 | SN2
48.7 | SN2
49.1 | SN2
48.9 | SN2
48.7 | SN2
48.8 | SN2
48.9 | SN2
49.7 | SN2
49.1 | SN2
49.9 | SN2
49.2 | SN2
49.2 | SN2
49 | SN2
49.1 | SN2
49.2 | SN2
49.3 | SN2
48.6 | SN2
48.6 | SN2
48.5 | SN2
48.4 | SN2
48.1 | SN2
48.3 | SN2
48.1 | SN2
48.3 | SN2
48 | SN2
48.3 | SN2
48.1 | SN2
48.2 | SN2
48.3 | SN2
48 | SN2
48.2 | SN2
48.1 | SN2
48.3 | SN2
48 | SN2
48.3 | SN2
48 | SN2
48 | SN2
47.9 | SN2
47.7 | SN2
48 | SN2
47.9 | SN2
48.1 | SN2
48 | SN2
48.1 | SN2
48.3 | SN2
48.5 | SN2
48.4 | SN2
49.1 | SN2
49.2 | SN2
49.5 | SN2
49.6 | SN2
49.6 | SN2
49.4 | SN2
50.1 | SN2
49.9 | SN2
50.2 | SN2
49.4 | SN2
49.3 | SN2
48.8 | SN2
48.7 | SN2
48.6 | SN2
48.5 | SN2
48.4 | SN2
48.2 | SN2
48.2 | SN2
48.3 | SN2
48.2 | SN2
48.2 | SN2
48.1 | SN2
48.2 | SN2
48.3 | SN2
48.6 | SN2
48.5 | SN2
48.5 | SN2
48.3 | SN2
48.4 | SN2
48.4 | SN2
48.3 | SN2
48.3 | SN2
48.2 | SN2
48.2 | SN2
48.1 | SN2
48.2 | SN2
47.8 | SN2
47.9 | SN2
47.9 | SN2
47.9 | SN2
48.3 | SN2
48.2 | SN2
48.3 | SN2
48.6 | SN2
48.6 | SN2
49.2 | SN2
49 | SN2
49 | SN2
49.2 | SN2
49.4 | SN2
49.4 | SN2
49.3 | SN2
49.6 | SN2
49.7 | SN2
49.6 | SN2
49.3 | SN2
49.7 | SN2
49.2 | SN2
49.2 | SN2
49.1 | SN2
49 | SN2
48.8 | SN2
48.7 | SN2
48.4 | SN2
48.5 | SN2
48.4 | SN2
48.7 | SN2
48.5 | SN2
48.4 | SN2
48.3 | SN2
48.1 | SN2
48.5 | SN2
48.3 | SN2
48.3 | SN2
48.3 | SN2
48.4 | SN2
48.2 | SN2
48.3 | SN2
48 | SN2
48 | SN2
48.1 | SN2
47.8 | SN2
48 | SN2
47.8 | SN2
48.1 | SN2
48.1 | SN2
48 | SN2
48.1 | SN2
48.1 | SN2
48.8 | SN2
48.4 | SN2
48.8 | SN2
48.5 | SN2
48.4 | SN2
48.7 | SN2
49.5 | SN2
49.5 | SN2
49.4 | SN2
49.6 | SN2
50 | SN2
49.6 | SN2
49.4 | SN2
49.2 | SN2
49.1 | SN2
49.1 | SN2
49 | SN2
48.8 | SN2
48.6 | SN2
48.6 | SN2
48.6 | SN2
48.4 | SN2
48.3 | SN2
48.2 | SN2
48.4 | SN2
48.2 | SN2
48.3 | SN2
48.3 | SN2
48.4 | SN2
48.2 | SN2
48.4 | SN2
48.3 | SN2
48.2 | SN2
48.6 | SN2
48.3 | SN2
48.3 | SN2
48.1 | SN2
48.2 | SN2
48.2 | SN2
48.1 | SN2
48.2 | SN2
48.1 | SN2
47.9 | SN2
48.2 | SN2
48 | SN2
48.4 | SN2
48.7 | SN2
48.1 | SN2
48.3 | SN2
48.8 | SN2
49.4 | SN2
49 | SN2
49.6 | SN2
49.8 | SN2
49.8 | SN2
50 | SN2
49.6 | SN2
50 | SN2
49.5 | SN2
49.6 | SN2
49.3 | SN2
49.1 | SN2
49.1 | SN2
49 | SN2
48.7 | SN2
48.7 | SN2
48.5 | SN2
48.4 | SN2
48.4 | SN2
48.2 | SN2
48.2 | SN2
48.1 | SN2
48.1 | SN2
48.2 | SN2
47.9 | SN2
47.9 | SN2
48 | SN2
48.1 | SN2
48.3 | SN2
48.2 | SN2
48.2 | SN2
48 | SN2
48.2 | SN2
47.9 | SN2
47.9 | SN2
47.9 | SN2
48 | SN2
47.9 | SN2
48 | SN2
47.6 | SN2
47.2 | SN2
47.3 | SN2
47.2 | SN2
47.4 | SN2
47.5 | SN2
47.6 | SN2
48 | SN2
47.8 | SN2
48 | SN2
48.3 | SN2
48.1 | SN2
47.5 | SN2
48.1 | SN2
48.7 | SN2
48.1 | SN2
48.4 | SN2
48.3 | SN2
48.3 | SN2
48.2 | SN2
47.9 | SN2
47.9 | SN2
47.3 | SN2
47.3 | SN2
47.5 | SN2
47.2 | SN2
47.2 | SN2
47.5 | SN2
47.2 | SN2
47.4 | SN2
47.4 | SN2
47.5 | SN2
47.6 | SN2
47.6 | SN2
47.4 | SN2
47.3 | SN2
47.1 | SN2
47.3 | SN2
47.2 | SN2
47.2 | SN2
47.2 | SN2
46.9 | SN2
47.3 | SN2
47.1 | SN2
47.2 | SN2
47 | SN2
47.1 | SN2
47.2 | SN2
47.4 | SN2
47.4 | SN2
47.4 | SN2
47.8 | SN2
47.3 | SN2
47.5 | SN2
48 | SN2
47.9 | SN2
48 | SN2
48.3 | SN2
47.9 | SN2
47.7 | SN2
47.6 | SN2
47.5 | SN2
47.8 | SN2
47.5 | SN2
47.6 | SN2
47.3 | SN2
47.5 | SN2
47.2 | SN2
50.4 | SN2
50.9 | SN2
51.2 | SN2
51.3 | SN2
52 | SN2
52.3 | SN2
52.3 | SN2
51.9 | SN2
52.3 | SN2
52.3 | SN2
52.1 | SN2
52.1 | SN2
51.8 | SN2
51.8 | SN2
51.9 | SN2
52.2 | SN2
51.8 | SN2
51.7 | SN2
51.9 | SN2
51.7 | SN2
51.5 | SN2
51.5 | SN2
51.7 | SN2
51.5 | SN2
51.5 | SN2
51.3 | SN2
51.7 | SN2
52.2 | SN2
52 | SN2
52.4 | SN2
51.8 | SN2
52.1 | SN2
52.3 | SN2
51.7 | SN2
51.7 | SN2
51.5 | SN2
51.2 | SN2
51.2 | SN2
51.3 | SN2
51.2 | SN2
50.9 | SN2
50.6 | SN2
50.2 | SN2
50.2 | SN2
49.7 | SN2
49.7 | SN2
49.8 | SN2
49.4 | SN2
49.3 | SN2
49 | SN2
49.1 | SN2
50.2 | SN2
50.6 | SN2
51 | SN2
51.2 | SN2
51.5 | SN2
51.8 | SN2
51.9 | SN2
51.9 | SN2
51.7 | SN2
51.8 | SN2
51.7 | SN2
51.6 | SN2
51.3 | SN2
51.4 | SN2
51.2 | SN2
51.1 | SN2
51 | SN2
51 | SN2
51 | SN2
51 | SN2
51.3 | SN2
51.3 | SN2
51.4 | SN2
50.8 | SN2
51.2 | SN2
51.1 | SN2
51.4 | SN2
51.4 | SN2
51.2 | SN2
51 | SN2
50.7 | SN2
50.7 | SN2
50.6 | SN2
50.8 | SN2
50.8 | SN2
50.4 | SN2
50.3 | SN2
50.5 | SN2
50.3 | SN2
49.9 | SN2
49.7 | SN2
49.5 | SN2
49.4 | SN2
49.3 | SN2
49.1 | SN2
49.2 | SN2
49 | SN2
49 | SN2
49 | SN2
49.3 | SN2
49 | SN2
49.2 | SN2
49.3 | SN2
48.8 | SN2
48.9 | SN2
48.7 | SN2
48.9 | SN2
48.6 | SN2
48.8 | SN2
48.6 | SN2
48.8 | SN2
48.6 | SN2
48.6 | SN2
48.4 | SN2
48.6 | SN2
48.5 | SN2
48.3 | SN2
48.4 | SN2
49 | SN2
49.5 | SN2
49 | SN2
49.2 | SN2
49.2 | SN2
49.6 | SN2
49.6 | SN2
49.7 | SN2
50.2 | SN2
51.3 | SN2
51.4 | SN2
50.4 | SN2
50.5 | SN2
50.8 | SN2
50.4 | SN2
50.4 | SN2
50.1 | SN2
49.9 | SN2
49.4 | SN2
49.4 | SN2
48.4 | SN2
48.4 | SN2
48.2 | SN2
48.1 | SN2
48.2 | SN2
48.3 | SN2
48.1 | SN2
48.1 | SN2
47.8 | SN2
48 | SN2
48 | SN2
47.9 | SN2
47.8 | SN2
47.7 | SN2
47.7 | SN2
47.7 | SN2
47.8 | SN2
47.7 | SN2
47.7 | SN2
47.7 | SN2
47.6 | SN2
47.8 | SN2
47.8 | SN2
47.6 | SN2
47.4 | SN2
47.9 | SN2
47.8 | SN2
47.7 | SN2
48 | SN2
48.2 | SN2
48.9 | SN2
49.6 | SN2
49.8 | SN2
49.6 | SN2
50.3 | SN2
49.8 | SN2
50.1 | SN2
50.1 | SN2
49.8 | SN2
49.4 | SN2
49.2 | SN2
49.4 | SN2
49.7 | SN2
49.4 | SN2
48.7 | SN2
48.8 | SN2
48.7 | SN2
48.3 | SN2
48 | SN2
48 | SN2
48.2 | SN2
47.6 | SN2
47.9 | SN2
47.8 | SN2
47.8 | SN2
47.7 | SN2
48 | SN2
47.7 | SN2
47.6 | SN2
47.5 | SN2
47.5 | SN2
47.6 | SN2
47.5 | SN2
47.2 | SN2
47.4 | SN2
47.3 | SN2
47.1 | SN2
47.2 | SN2
47.5 | SN2
47.3 | SN2
47.1 | SN2
47.4 | SN2
47.4 | SN2
47.8 | SN2
48.1 | SN2
1 | SN2
3.7 | SN2
7 | SN2
55.7 | SN2
51.9 | SN2
51 | SN2
50.3 | SN2
49.9 | SN2
49.7 | SN2
49.5 | SN2
49.4 | SN2
48.8 | SN2
48.5 | SN2
48 | SN2
47.9 | SN2

## POWER USE
From previous monitoring period 17-Jul06 to 17-Oct 2006
| Cumbres | kWh | tCO2e | San Nicolas | kWh | tCO2e
| 1-17 Oct | 1318.2674 | 0.7 | 1-17 Oct | 1506.5913 | 0.8
CEF
0.531
| Cumbres |  |  | San Nicolas
|  | kWh | tCO2e |  | kWh | tCO2e
| 18-31 Oct | 2177.7326 | 1.1564 | 18-31 Oct | 7037.4 | 3.7369
| Nov | 3579 | 1.9004 | Nov | 10459 | 5.5537
| Dec | 3635 | 1.9302 | Dec | 9881 | 5.2468
| Jan | 3364 | 1.7863 | Jan | 8638 | 4.5868
| Feb | 3552 | 1.8861 | Feb | 10602 | 5.6297
| Mar | 3158 | 1.6769 | Mar | 7851 | 4.1689
| Apr | 3433 | 1.8229 | Apr | 10504 | 5.5776
| May | 3051 | 1.6201 | May | 10384 | 5.5139
| June | 4047 | 2.149 | June | 14031 | 7.4505
| July | 3658 | 1.9424 | July | 11336 | 6.0194
| Ags | 3598 | 1.9105 | Ags | 11928 | 6.3338
7 | 1-7 Sept | 841.6333 | 0.44691 | 1-7 Sept | 3273.9 | 1.7384
|  | 38094.3659 | 20.2281 |  | 115925.3 | 61.5563 | MAX VALUE kWh/MONTH / 30 * 7
*Sep 0'7 not yet avAilable