## Sheet1
GACL- DAHEJ
CAPTIVE CO-GENERATION POWER PLANT
CORRECTED GAS TURBINES OUTPUT CALCULATION ON SITE CONDITION
Sr.No | Description | Corrected Output in MW | Reference
1 | At ISO condition of 15 deg C | 38.34 | GE document related PG 6541 B ; Chart No. 499HA542 , Rev C
2 | At Ambient temp of 39 Deg.Cent at Dahej SITE. | 32.2056 | GE document related PG 6541 B ; Chart No. 499HA543 , Rev A
3 | Decrease in output due to decrease in NCV | 31.0242 | L&T HMPD , GT ID No. 49
4 | Decreasein grid frequency from 50 Hz to 49.5 Hz | 30.7139 | Actual site conditions of Grid
5 | Decrease in output due to compressor fouling & Intake air filter losses 1.5% | 30.2532 | GE document related PG 6541 B ; Chart No. 499HA542 , Rev C

## Power cost
CAPTIVE CO-GENERATION POWER PLANT
GACL- DAHEJ
POWER SALE TO GEB UNIT COST CALCULATION
| Particulars | Unit | Naptha | N.Gas
| Avg.Generation | MW | 87.5 | 87.5
| Guranteed NCV of Fuel | Kcal/Kg | 9740
|  | Kcal/Sm3 |  | 8587.1973
| Sp.Fuel Consumption (based on Guarantee) | Kg/Kwh | 0.20004
|  | Sm3/Kwh |  | 0.24623
| Actual NCV of Fuel | Kcal/Kg | 10300
|  | Kcal/Sm3 |  | 8300
| Sp.Fuel Consumption (based on Actual) | Kg/Kwh | 0.18916
|  | Sm3/Kwh |  | 0.25475
| FSNL Fuel (Based on Actual) | Kg/Kwh | 0.078015
|  | Sm3/Kwh |  | 0.09808
| Incremental Fuel Consumption | Kg/Kwh | 0.11115
|  | Sm3/Kwh |  | 0.15667
| Cost of Fuel | Rs/Kg | 11.305
|  | Rs/Sm3 |  | 8.58
| Incremental Fuel Cost | Rs/Kwh | 1.2565 | 1.3442
| Revenue from GEB | Rs/Kwh | 3 | 2.25
| Net Earning on Sale to GEB | Rs/Kwh | 1.7435 | 0.90578
| Net loss in Revenue on switchover from Naptha to N.Gas |  | 0.83768

## Guarantee Sheet
GACL- DAHEJ
CAPTIVE CO-GENERATION POWER PLANT
GUARANTEE HEAT RATE CALCULATION
|  | UNIT | BASED ON HMBD SUPPLIED BY OEM (M/S.L&T) | [5 empty] | Calculation for 90 MW |  | Calculation for 87.5 MW |  | Calculation for 72 MW |  | Calculation for 63 MW
1 | FUEL |  | Naptha | Naptha | Naptha | N.gas | N.gas | N.gas | Naptha | N.gas | Naptha | N.gas | Naptha | N.gas | Naptha | N.gas
2 | Numbers of Gas Turbines |  | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
3 | Gas Turbine Power output. | KW | 33020 | 33020 | 33020 | 33670 | 33670 | 33670 | 30250 | 30250 | 29409.7222 | 29409.7222 | 24200 | 24200 | 21175 | 21175
4 | STG Power output | KW | 34870 | 32120 | 25650 | 35174 | 32880 | 26490 | 29500 | 29500 | 28680.5556 | 28680.5556 | 23600 | 23600 | 20650 | 20650
5 | Gross Power output | KW | 100910 | 98160 | 91690 | 102514 | 100220 | 93830 | 90000 | 90000 | 87500 | 87500 | 72000 | 72000 | 63000 | 63000
6 | Fuel flow per Gas Turbine. | Kg/Sec | 2.725 | 2.725 | 2.725 | 2.399 | 2.399 | 2.399 | 2.6221 | 2.2162 | 2.5687 | 2.171 | 2.2373 | 1.8909 | 2.045 | 1.7283
| FSNL Fuel/GT | Kg/Sec | 0.68 | 0.68 | 0.68 | 0.59 | 0.59323 | 0.59323 | 0.69829 | 0.59 | 0.69829 | 0.59 | 0.69829 | 0.59 | 0.69829 | 0.59
| Incremental Fuel/GT | Kg/Sec | 2.045 | 2.045 | 2.045 | 1.81 | 1.8068 | 1.8068 | 1.9238 | 1.6262 | 1.8704 | 1.581 | 1.5391 | 1.3009 | 1.3467 | 1.1383
7 | Sp.Fuel Consumption | Kg/Kwh | 0.19443 | 0.19988 | 0.21398 |  |  |  | 0.20977 |  | 0.21136
8 | Sp.Fuel Consumption | M3/Kwh. |  |  |  | 0.22496 | 0.23011 | 0.24578 |  | 0.23671 |  | 0.23851 |  | 0.25246 |  | 0.26371
9 | LHV Of Fuel | Kcal/Kg | 10001.9111 | 10001.9111 | 10001.9111 | 11464.8829 | 11464.8829 | 11464.8829 | 9740 | 11464.8829 | 9740 | 11464.8829 | 9740 | 11464.8829 | 9740 | 11464.8829
10 | Fuel heat per Gas Turbine. | Kcal/Hr | 98118748.2083 | 98118748.2083 | 98118748.2083 | 99015315.0502 | 99015315.0502 | 99015315.0502 | 91941692.6897 | 91468477.3659 | 90067886.7386 | 89604114.4216 | 78450289.8421 | 78045064.167 | 71704588.4184 | 71333357.5675
11 | Total Fuel Heat. | Kcal/Hr | 196237496.4166 | 196237496.4166 | 196237496.4166 | 198030630.1003 | 198030630.1003 | 198030630.1003 | 183883385.3794 | 182936954.7318 | 180135773.4773 | 179208228.8432 | 156900579.6843 | 156090128.3339 | 143409176.8368 | 142666715.135
12 | Process Steam Flow. | TPH | 11 | 26.1 | 60 | 11 | 26.1 | 60 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
13 | Process Steam Parameters |  |  | 13.73 bar , 204 OC
14 | Process Steam Enthalpy | Kcal/Kg | 672.24 | 672.24 | 672.24 | 672.24 | 672.24 | 672.24 | 672.24 | 672.24 | 672.24 | 672.24 | 673.24 | 674.24 | 675.24 | 676.24
15 | Heat in Process STeam | Kcal/Hr | 7394640 | 17545464 | 40334400 | 7394640 | 17545464 | 40334400 | 7394640 | 7394640 | 7394640 | 7394640 | 7405640 | 7416640 | 7427640 | 7438640
16 | Make up Water Flow. | TPH | 15 | 31 | 67 | 15 | 31 | 67 | 15 | 15 | 15 | 15 | 15 | 15 | 15 | 15
17 | Make up Water Temperature. | 0C | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31
18 | Make up Water Enthalpy. | Kcal/Kg | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31 | 31
19 | Heat in Make up Water. | Kcal/Hr | 465000 | 961000 | 2077000 | 465000 | 961000 | 2077000 | 465000 | 465000 | 465000 | 465000 | 465000 | 465000 | 465000 | 465000
20 | Heat Rate (Guarantee) | Kcal/KHr | 1876.0069 | 1830.2061 | 1722.9807 | 1864.1453 | 1810.4786 | 1702.7947
21 | Heat Rate (Calculated) | Kcal/KHr | [6 empty] | 1966.1527 | 1955.6368 | 1979.4987 | 1968.8982 | 2082.7769 | 2071.3679 | 2165.818 | 2153.8583
Note:- Sp.Fuel Consumption on Naptha (Kg/Kwh)
Sp.Fuel Consmp = Fuel flow per GT (Kg/Sec.) X 3600 (Convertion from Sec to Hr.) x 02 (Nos. of GT) / Total Power Generation Per Hour
Sp.Fuel Consumption on N.Gas (sm3/Kwh)
Sp.Fuel Consmp = Fuel flow per GT (Kg/Sec./ Density of N.gas) X 3600 (Convertion from Sec to Hr.) x 02 (Nos. of GT) / Total Power Generation Per Hour
Where Density of N.Gas at 20 deg.Centigrade is considered = 0.749 Kg/M3
| NCV of Naptha before fuel switch |  | 9740 | Kcal/Kg.
Calculation Sheet
Air Density at 0 deg. Centigrade :- 1.293 Kg/Met3.
Calculated Air density at 20 deg.Cent:- 1.293 x 273 / ( 273+20) = 1.20
Sp.Gravity of N.Gas at STP (15.5 Deg.Cent) :-0.62
Calculated density of N.Gas at 20 deg. Cent.:- 0.62 x 1.20 = 0.749
GUIDELINE FOR HEAT RATE CALCULATION :
COMBINED CYCLE HEAT RATE = ( TOTAL FUEL HEAT + HEAT IN MAKE UP WATER - HEAT IN PROCESS STEAM ) / GROSS POWER OUTPUT
Note on J15: SRATH: calculated based on the actual NCV of Naptha
Note on J16: SRATH: calculated based on the actual NCV of Naptha
Note on K16: SRATH: Back calculation is done from HMBD OF OEM.
Note on L14: SRATH: Back calculated from 90 MW.
Note on L15: SRATH: Back calculated from 90 MW.
Note on M14: SRATH: Back calculated from 90 MW.
Note on M15: SRATH: Back calculated from 90 MW.
Note on N14: SRATH: Back calculated from 90 MW.
Note on N15: SRATH: Back calculated from 90 MW.
Note on O14: SRATH: Back calculated from 90 MW.
Note on O15: SRATH: Back calculated from 90 MW.
Note on Q15: SRATH: Back calculated from 90 MW.