## Spanish Version
Calibración y Ajuste de Medidores | [5 empty] | CLB-2008-177
DATOS GENERALES
Empresa Solicitante: |  |  | Fecha: |  |  | E-MAIL |  | Número Telf:
E.E.Q.S.A. : CENTRAL HIDROELÉCTRICA |  |  | Noviembre 11, 2008
PERLAVI
Características de los Equipos de Medición
Equipo de Medición a Calibrar
Marca: |  | Tipo: |  | # de Serie: |  | Tensión Nominal (V)
MAXSYS 2510 |  | MASTER |  | 85 762 937 |  |  | 120-277
Corriente Nominal (A): |  | Kh (Wh/Pulso): |  | Ultima Calibración |  | Fecha Expiración de la presente Calibración:
5 |  | 1.8 |  |  |  |  | noviembre 11 de 2010
Equipo de Medición Patrón
Marca: |  | # de Serie: |  | Precisión: |  |  | Certificaciones:
AVO INTERNATIONAL |  | PZRJ 120 |  |  | 0.02% |  | ENERGIE-MESSTECHIK
Tablas de Porcentajes (%) de Error Obtenidos
ERROR MÁXIMO PERMITIDO EN TODAS LAS CONDICIONES: ± 0,2 %
Condición: 10% I nominal
Pulsos |  | 0 Grados |  | 30 Grados |  |  | 60 Grados
1 |  | 0.187 |  | 0.178 |  |  | 0.22
2 |  | 0.189 |  | 0.176 |  |  | 0.139
3 |  | 0.189 |  | 0.061 |  |  | 0.178
Promedio |  | 0.188 |  | 0.138 |  |  | 0.179
Condición: 50% I nominal
Pulsos |  | 0 Grados |  | 30 Grados |  |  | 60 Grados
1 |  | -0.021 |  | 0.086 |  |  | 0.04
2 |  | 0.129 |  | -0.018 |  |  | 0.053
3 |  | 0.096 |  | 0.076 |  |  | 0.061
Promedio |  | 0.058 |  | 0.048 |  |  | 0.051
Condición: 100% I nominal
Pulsos |  | 0 Grados |  | 30 Grados |  |  | 60 Grados
1 |  | 0.086 |  | 0.107 |  |  | 0.178
2 |  | 0.179 |  | 0.122 |  |  | 0.092
3 |  | 0.019 |  | -0.151 |  |  | 0.086
Promedio |  | 0.095 |  | 0.026 |  |  | 0.119
RESULTADOS VÁLIDOS POR DOS AÑOS:
EL EQUIPO CALIBRADO SI ESTA DENTRO DEL RANGO DE PRECISIÓN
EL EQUIPO CALIBRADO NO FUE PREVIAMENTE AJUSTADO.
Aceptación de los Resultados de Calibración
| POR CENACE: |  |  |  |  | POR EEQSA:
| Jorge Aguilar |  |  |  |  | Oscar Badillo

## English Version
Meter Calibration | [5 empty] | CLB-2008-177
GENERAL INFORMATION
Company requesting calibration |  |  | Date: |  |  | E-MAIL |  | Phone #
E.E.Q.S.A. : CENTRAL HIDROELÉCTRICA |  |  | 2008-11-11
PERLABI
Characteristics of the Metering Equipment
Metering Equipment to Calibrate
Make: |  | Type: |  | Serial # |  | Nominal Voltage (V):
MAXSYS 2510 |  | MASTER |  | 85 762 937 |  |  | 120-277
Nominal Current (A): |  | Kh (Wh/Pulse): |  | Last Calibration: |  | Expiration date of this calibration:
5 |  | 1.8 |  |  |  |  | 2010-11-11
Standard measuring equipment
Make: |  | Serial # |  | Accuracy: |  |  | Certification:
AVO INTERNATIONAL |  | PZRJ 120 |  |  | 0.02% |  | ENERGIE-MESSTECHIK
Table of Percentages (%) of Errors
MAXIMUM ERROR ALLOWED IN ALL CONDITIONS: ± 0,2 %
Condition: 10% nominal I
Pulses |  | 0 Degrees |  | 30 Degrees |  |  | 60 Degrees
1 |  | 0.187 |  | 0.178 |  |  | 0.22
2 |  | 0.189 |  | 0.176 |  |  | 0.139
3 |  | 0.189 |  | 0.061 |  |  | 0.178
Mean |  | 0.188 |  | 0.138 |  |  | 0.179
Condition: 50% nominal I
Pulses |  | 0 Degrees |  | 30 Degrees |  |  | 60 Degrees
1 |  | -0.021 |  | 0.086 |  |  | 0.04
2 |  | 0.129 |  | -0.018 |  |  | 0.053
3 |  | 0.096 |  | 0.076 |  |  | 0.061
Mean |  | 0.058 |  | 0.048 |  |  | 0.051
Condition: 100% nominal I
Pulses |  | 0 Degrees |  | 30 Degrees |  |  | 60 Degrees
1 |  | 0.086 |  | 0.107 |  |  | 0.178
2 |  | 0.179 |  | 0.122 |  |  | 0.092
3 |  | 0.019 |  | -0.151 |  |  | 0.086
Mean |  | 0.095 |  | 0.026 |  |  | 0.119
RESULTS GOOD FOR TWO YEARS:
THE CALIBRATED EQUIPMENT IS INDEED WITHIN THE ACCURACY RANGE
THE CALIBRATED EQUIPMENT HAS NOT BEEN PREVIOUSLY ADJUSTED
Aceptance of Calibration Results
| BY CENACE: |  |  |  |  | BY EEQSA:
| Jorge Aguilar |  |  |  |  | Oscar Badillo