## Final CER
Project data compilation sheet
Parameter | Baseline Consumption of Electricity for Auxiliary | Baseline Production of BLS for respective period | Specific Consumption of electricity in baseline | Eavg | Eine | Efelec | Prep | Srep | SSCB | Prep1 | Srep1 | SSC P | SSC diff | P act | Es | Enet | ŋboiler | Ein | EFfuels | CER1 + CER2 | CER | CER net
Description
Values which are constant through out the project crediting period | 226310 | 10337 | 21.8932 |  |  | 1274 | 10337 | 15064 | 1.4573
Months
2003-09-01 |  |  |  | 439050 | 0.092688 |  |  |  |  | 5444.91 | 4028 |  |  | 15820.54 | 2.8196 |  | 0.63169 |  | 74.7547
2003-10-01 |  |  |  | 498380 | 0.081098 |  |  |  |  | 7845.39 | 5619 |  |  | 19059.87 | 2.8233 |  | 0.61868 |  | 72.4975
2003-11-01 |  |  |  | 465256 | 0.061136 |  |  |  |  | 5457.91 | 3880 |  |  | 18458.68 | 2.7997 |  | 0.61659 |  | 75.1811
2003-12-01 |  |  |  | 482638 | 0.04821 |  |  |  |  | 6035 | 4490 |  |  | 19843.07 | 2.8151 |  | 0.62611 |  | 77.5748
Total Sep 03-Dec03 |  |  |  | 1885324 | 0.28313 |  |  |  |  | 24783.21 | 18017 | 0.72698 | 0.73031 | 73182.16 | 2.8144 | 150.4177 | 0.62327 | 241.3377 | 75.002 | 25.8515 | 18100.8178 | 18074.9663
2004-01-01 |  |  |  | 509407 | 0.073219 |  |  |  |  | 8711.32 | 6449 |  |  | 19923.43 | 2.8545 |  | 0.62769 |  | 73.2697
2004-02-01 |  |  |  | 455302 | 0.065751 |  |  |  |  | 8750.52 | 6541 |  |  | 17793.25 | 2.8141 |  | 0.63843 |  | 75.0246
2004-03-01 |  |  |  | 505469 | 0.085724 |  |  |  |  | 9350.14 | 6923 |  |  | 19172.37 | 2.8029 |  | 0.6308 |  | 79
2004-04-01 |  |  |  | 466678 | 0.057775 |  |  |  |  | 14129.49 | 10929 |  |  | 18677.15 | 2.7785 |  | 0.66 |  | 72.9105
2004-05-01 |  |  |  | 499559 | 0.061188 |  |  |  |  | 3720.76 | 2788 |  |  | 20023.17 | 2.7757 |  | 0.7378 |  | 72.7979
2004-06-01 |  |  |  | 488303 | 0.078624 |  |  |  |  | 8213.64 | 6308 |  |  | 18712.6 | 2.7757 |  | 0.73061 |  | 72.8008
2004-07-01 |  |  |  | 500076 | 0.065758 |  |  |  |  | 11235.64 | 9005 |  |  | 19838.01 | 2.7757 |  | 0.74556 |  | 78.3378
2004-08-01 |  |  |  | 481620 | 0.079902 |  |  |  |  | 15932.81 | 11588 |  |  | 18348.99 | 2.7757 |  | 0.78055 |  | 82.6693
2004-09-01 |  |  |  | 440636 | 0.087917 |  |  |  |  | 8124.34 | 6292 |  |  | 16110.9 | 2.7757 |  | 0.75717 |  | 67.8621
2004-10-01 |  |  |  | 505030 | 0.092704 |  |  |  |  | 7355.22 | 5606 |  |  | 18833.51 | 2.7757 |  | 0.73529 |  | 63.2492
2004-11-01 |  |  |  | 477670 | 0.085389 |  |  |  |  | 9379 | 6905 |  |  | 17917.94 | 2.7757 |  | 0.71912 |  | 72.6754
2004-12-01 |  |  |  | 504415 | 0.081599 |  |  |  |  | 11886.6 | 8948 |  |  | 19312.67 | 2.7757 |  | 0.75 |  | 67.3502
Total Jan 04-Dec04 |  |  |  | 5834165 | 0.91555 |  |  |  |  | 116789.48 | 88282 | 0.75591 | 0.70138 | 224663.99 | 2.788 | 439.3183 | 0.70942 | 619.2654 | 73.1623 | 54.6974 | 45306.8788 | 45252.1814
2005-01-01 |  |  |  | 523920 | 0.11815 |  |  |  |  | 13682.44 | 10106 |  |  | 18534.17 | 2.7757 |  | 0.74343 |  | 70.5384
2005-02-01 |  |  |  | 437475 | 0.10396 |  |  |  |  | 7507.7 | 5638 |  |  | 15233.77 | 2.7757 |  | 0.7674 |  | 80.179
2005-03-01 |  |  |  | 483813 | 0.04905 |  |  |  |  | 10772.2 | 7918 |  |  | 19858.37 | 2.7757 |  | 0.7324 |  | 64.8616
2005-04-01 |  |  |  | 489870 | 0.041701 |  |  |  |  | 3223.8 | 2389 |  |  | 20470.71 | 2.7757 |  | 0.70399 |  | 66.997
2005-05-01 |  |  |  | 502563 | 0.055667 |  |  |  |  | 4962.04 | 3857 |  |  | 20412.55 | 2.7757 |  | 0.69507 |  | 64.9577
2005-06-01 |  |  |  | 458060 | 0.019897 |  |  |  |  | 3812.78 | 3101 |  |  | 20013.64 | 2.7757 |  | 0.69231 |  | 64.7746
2005-07-01 |  |  |  | 474659 | 0.061499 |  |  |  |  | 10664.96 | 8259 |  |  | 18871.6 | 2.7757 |  | 0.69853 |  | 65.6751
2005-08-01 |  |  |  | 478058 | 0.065194 |  |  |  |  | 5011.21 | 3931 |  |  | 18858.09 | 2.7757 |  | 0.71211 |  | 62.2185
2005-09-01 |  |  |  | 511671 | 0.078933 |  |  |  |  | 5708.76 | 4446 |  |  | 19765.85 | 2.7757 |  | 0.68839 |  | 69.2134
2005-10-01 |  |  |  | 463991 | 0.078089 |  |  |  |  | 6294.37 | 5286 |  |  | 17626.57 | 2.7757 |  | 0.70606 |  | 74.028
2005-11-01 |  |  |  | 516455 | 0.12936 |  |  |  |  | 6283.02 | 4958 |  |  | 17681.21 | 2.7757 |  | 0.71931 |  | 68.076
2005-12-01 |  |  |  | 528355 | 0.074424 |  |  |  |  | 3747.65 | 2673 |  |  | 20733.86 | 2.7757 |  | 0.68396 |  | 65.5034
Total Jan 05-Dec05 |  |  |  | 5868890 | 0.87592 |  |  |  |  | 81670.93 | 62562 | 0.76603 | 0.69126 | 228060.39 | 2.7757 | 437.5947 | 0.71191 | 614.674 | 68.0852 | 21.0765 | 41850.2207 | 41829.1443
2006-01-01 |  |  |  | 535338 | 0.097919 |  |  |  |  | 7784.82 | 5594 |  |  | 19979.68 | 2.7757 |  | 0.69338 |  | 69.5202
2006-02-01 |  |  |  | 475603 | 0.059364 |  |  |  |  | 5288.87 | 4047 |  |  | 19012.24 | 2.7757 |  | 0.69781 |  | 67.1713
2006-03-01 |  |  |  | 502083 | 0.096459 |  |  |  |  | 3898.89 | 3280 |  |  | 18527.4 | 2.7757 |  | 0.7189 |  | 71.6383
2006-04-01 |  |  |  | 409305 | 0.044648 |  |  |  |  | 4524.39 | 3668 |  |  | 16656.18 | 2.7757 |  | 0.7161 |  | 73.1817
2006-05-01 |  |  |  | 520651 | 0.074154 |  |  |  |  | 9080.82 | 7075 |  |  | 20394.34 | 2.7757 |  | 0.69424 |  | 66.2291
2006-06-01 |  |  |  | 514762 | 0.059043 |  |  |  |  | 653.19 | 471 |  |  | 20815.54 | 2.7757 |  | 0.70597 |  | 64.7381
2006-07-01 |  |  |  | 516865 | 0.072961 |  |  |  |  | 6492.06 | 4966 |  |  | 20275.87 | 2.7757 |  | 0.70989 |  | 66.1576
2006-08-01 |  |  |  | 501132 | 0.086802 |  |  |  |  | 11051.15 | 7687 |  |  | 18925.06 | 2.7757 |  | 0.67899 |  | 65.7671
2006-09-01 |  |  |  | 524693 | 0.084023 |  |  |  |  | 5828.3 | 3781 |  |  | 20128.17 | 2.7757 |  | 0.67922 |  | 65.5741
2006-10-01 |  |  |  | 519302 | 0.046705 |  |  |  |  | 0 | 0 |  |  | 21586.46 | 2.7757 |  | 0.70174 |  | 69.3808
2006-11-01 |  |  |  | 453653 | 0.062501 |  |  |  |  | 2641.43 | 1923 |  |  | 17866.37 | 2.7757 |  | 0.74626 |  | 69.2006
2006-12-01 |  |  |  | 514639 | 0.055621 |  |  |  |  | 9811.33 | 6945 |  |  | 20966.25 | 2.7757 |  | 0.69013 |  | 67.881
Total Jan 05-Dec05 |  |  |  | 5988026 | 0.8402 |  |  |  |  | 67055.25 | 49437 | 0.73726 | 0.72003 | 235133.56 | 2.7757 | 469.9422 | 0.70272 | 668.7474 | 68.0367 | 22.1924 | 45499.3364 | 45477.144
TOTAL | [21 empty] | 150633.4359

## Summary Elec
In-house generation | Steam Energy Consumption | ng | Grid Consumption | % Grid | Eine | Act In-hous | Act Grid | EF Grid | CER1`
GWh | Mkcal | % | GWh | % | GWh | GWh | GWh | tCO2/GWh | tCO2 | Mkcal Steam | Eff boiler | Mkcal Fuel | TJ Fuel | EF Fuel | CER 2
19.2 | 102373.9626 | 16.1291 | 1.6 | 7.6923
20.9 | 105581.1825 | 17.0239 | 2.7 | 11.4407
18.14 | 99603.0395 | 15.6626 | 2.7 | 12.9559
20.5 | 107732.6553 | 16.3646 | 1.2 | 5.53
|  | 16.295 | 2.05 | 9.4047 | 0.28313 | 0.2565 | 0.026628 | 941.07 | 25.0586 | 1.5741 | 0.62327 | 2.5256 | 0.010572 | 75.002 | 0.79294 | 25.8515
20.01 | 106870.5402 | 16.1023 | 1.6 | 7.404
18.54 | 99030.5262 | 16.1005 | 1.6 | 7.9444
19.7 | 103492.3662 | 16.3703 | 1.7 | 7.9439
19.2 | 101064.3619 | 16.3381 | 1.8 | 8.5714
19.58 | 108443.7591 | 15.5277 | 2.3 | 10.5119
20.21 | 113501.5764 | 15.3131 | 1.5 | 6.9093
21.46 | 114476.1861 | 16.1218 | 0.7 | 3.1588
20.63 | 110087.3101 | 16.1161 | 1.3 | 5.928
21.12 | 109369.8584 | 16.6071 | 1.2 | 5.3763
21.67 | 113018.6857 | 16.4895 | 1.4 | 6.0685
24.08 | 116980.6914 | 17.7028 | 0.3 | 1.2305
24.84 | 121906.6528 | 17.5236 | 0.5 | 1.9732
|  | 16.3594 | 1.325 | 6.085 | 0.91555 | 0.85984 | 0.055711 | 941.07 | 52.4284 | 5.2559 | 0.70942 | 7.4088 | 0.031013 | 73.1623 | 2.269 | 54.6974
24.62 | 122992.1167 | 17.2151 | 0.5 | 1.9904
22.57 | 111921.3455 | 17.3427 | 0.8 | 3.4232
24.33 | 117173.3808 | 17.8571 | 0.3 | 1.218
24.99 | 119084.393 | 18.0472 | 0.4 | 1.5754
26.59 | 124498.6781 | 18.3676 | 0.3 | 1.1157
24.88 | 118135.7378 | 18.112 | 0.3 | 1.1914
25.16 | 120975.6516 | 17.8859 | 0.3 | 1.1783
24.51 | 118481.632 | 17.7906 | 0.5 | 1.9992
23.71 | 114135.2977 | 17.8653 | 0.8 | 3.264
23.31 | 113759.7745 | 17.6219 | 1.2 | 4.896
23.46 | 114734.6702 | 17.5846 | 1.3 | 5.2504
25.41 | 121225.6403 | 18.0264 | 0.2 | 0.78094
|  | 17.8097 | 0.575 | 2.3236 | 0.87592 | 0.85557 | 0.020353 | 941.07 | 19.1533 | 4.8039 | 0.71191 | 6.7479 | 0.028247 | 68.0852 | 1.9232 | 21.0765
24.91 | 120513.5035 | 17.7761 | 0.4 | 2.2539
21.5 | 107315.1679 | 17.2296 | 0.4 | 2.3481
25.91 | 129357.9244 | 17.2255 | 0.2 | 2.4183
27.68 | 117298.4841 | 20.2942 | 0.3 | 2.5367
26.26 | 126910.8558 | 17.7949 | 0.3 | 2.659
24.4 | 120324.4692 | 17.4395 | 0.5 | 2.7936
26.23 | 127248.1488 | 17.7274 | 0.6 | 2.8659
24.7 | 120514.7752 | 17.6261 | 0.3 | 2.8297
25.38 | 122149.259 | 17.869 | 0.4 | 2.6418
26.87 | 125996.0864 | 18.3404 | 0.9 | 2.4047
24.56 | 119958.8679 | 17.6074 | 1.3 | 2.5523
27.68 | 128081.3924 | 18.5857 | 0.3 | 2.5731
|  | 17.9596 | 0.49167 | 2.5731 | 0.8402 | 0.81858 | 0.021619 | 941.07 | 20.3452 | 4.5579 | 0.70272 | 6.4861 | 0.027151 | 68.0367 | 1.8472 | 22.1924

## Summary Boilers
Stot-in-power
Boilers | 2003-09-03 | 2003-10-01 | 2003-11-26 | 2003-12-01 | Total
CFB1 | 8289 | 3863 | 3278 | 5703
CFB2 | 8333 | 8183 | 8043 | 3542
CFB3 | 9404 | 5246 | 7489 | 11423
CFB1,2&3 | 26026 | 17292 | 18810 | 20668
CFB4 | 31764 | 30444 | 30272 | 31195
CFB5 | 49827 | 58242 | 49993 | 54700
SRB3 | 45295 | 51073 | 49408 | 54274
TOTAL | 152912 | 157051 | 167293 | 160837 | 638093
% H - BLS | 17.78% | 20.14% | 18.45% | 17.92% | 18.57%
% H - Coal | 82.22% | 79.86% | 81.55% | 82.08% | 81.43%
Boilers | 2004-01-01 | 2004-02-01 | 2004-03-01 | 2004-04-01 | 2004-05-01 | 2004-06-01 | 2004-07-01 | 2004-08-01 | 2004-09-01 | 2004-10-01 | 2004-11-01 | 2004-12-01
CFB1 | 703 | 231 | 2314 | 2383 | 2701 | 3282 | 6051 | 5596 | 3688 | 3304 | 258 | 3097
CFB2 | 7016 | 6249 | 3245 | 4828 | 6077 | 4260 | 5859 | 6894 | 1971 | 1629 | 759 | 2972
CFB3 | 9293 | 9599 | 9309 | 8620 | 1431 | 1494 |  |  |  | 596 |  | 1340
CFB1,2&3 | 17012 | 16079 | 14868 | 15831 | 10209 | 9036 | 11910 | 12490 | 5659 | 5529 | 1017 | 7409
CFB4 | 31086 | 28959 | 31516 | 29624 | 12437 | 23654 | 29296 | 13589 | 19461 | 23208 | 27878 | 24852
CFB5 | 55035 | 50697 | 54263 | 53137 | 47116 | 45339 | 21648 | 50041 | 43618 | 43114 | 43024 | 49725
CFB 6 |  |  |  |  | 35509 | 37675 | 50700 | 34557 | 45242 | 40805 | 49415 | 42621
SRB3 | 56179 | 51961 | 53529 | 52005 | 56020 | 52840 | 56805 | 52948 | 48220 | 55051 | 51896 | 56291
TOTAL | 159312 | 147696 | 154176 | 150597 | 161291 | 168544 | 170359 | 163625 | 162200 | 167707 | 173230 | 180898 | 1959635
% H - BLS | 22.1% | 20.58% | 20.78% | 19.3% | 18.01% | 17.91% | 21.35% | 23.1% | 19.57% | 22.05% | 23.94% | 22.51% | 20.93%
% H - Coal | 77.9% | 79.42% | 79.22% | 80.7% | 81.99% | 82.09% | 78.65% | 76.9% | 80.43% | 77.95% | 76.06% | 77.49% | 79.07%
Boilers | 2005-01-01 | 2005-02-01 | 2005-03-01 | 2005-04-01 | 2005-05-01 | 2005-06-01 | 2005-07-01 | 2005-08-01 | 2005-09-01 | 2005-10-01 | 2005-11-01 | 2005-12-01
CFB1 | 402 | 2640 | 2627 |  |  | 13 |  | 2017 | 1517 | 2526 | 1949
CFB2 | 5073 | 6340 | 1802 |  |  | 252 | 488 | 2617 | 1988 | 3075 | 2462
CFB3 | 2005-08-01: 312; 2005-09-01: 298; 2005-10-01: 3415; 2005-11-01: 2546
CFB1,2&3 | 5475 | 8980 | 4429 |  |  | 265 | 488 | 4946 | 3803 | 9016 | 6957
CFB4 | 14097 | 20915 | 27809 | 26143 | 28232 | 27679 | 28239 | 29390 | 22331 | 29169 | 28260 | 27557
CFB5 | 51061 | 47005 | 47053 | 45641 | 50352 | 46295 | 48833 | 39965 | 46166 | 48979 | 47279 | 47215
CFB 6 | 56781 | 43826 | 36817 | 48295 | 52597 | 47733 | 50347 | 49931 | 46739 | 33655 | 38941 | 49976
SRB3 | 55051 | 45271 | 57592 | 56289 | 53052 | 52910 | 51115 | 51420 | 50114 | 47998 | 48739 | 54721
TOTAL | 182465 | 165997 | 173700 | 176368 | 184233 | 174882 | 179022 | 175652 | 169153 | 168817 | 170176 | 179469 | 2099934
% H - BLS | 24.52% | 19.88% | 23.66% | 24.92% | 24.44% | 24.4% | 24.18% | 22.28% | 23.03% | 19.2% | 22.46% | 25.08% | 23.17%
% H - Coal | 75.48% | 80.12% | 76.34% | 75.08% | 75.56% | 75.6% | 75.82% | 77.72% | 76.97% | 80.8% | 77.54% | 74.92% | 76.83%
Boilers | 2006-01-01 | 2006-02-01 | 2006-03-01 | 2006-04-01 | 2006-05-01 | 2006-06-01 | 2006-07-01 | 2006-08-01 | 2006-09-01 | 2006-10-01 | 2006-11-01 | 2006-12-01
CFB1 | 2006-01-01: 2514; 2006-04-01: 2500; 2006-06-01: 1394; 2006-08-01: 113; 2006-10-01: 3840; 2006-11-01: 7779
CFB2 | 2437 | 3591 |  | 1061 |  | 3613 | 5946 | 156 | 1341 | 2770 | 3407
CFB3 | 2006-01-01: 1169; 2006-04-01: 502; 2006-06-01: 304; 2006-10-01: 257; 2006-11-01: 2269
CFB1,2&3 | 6120 | 3591 |  | 4063 |  | 5311 | 5946 | 269 | 1341 | 6867 | 13455
CFB4 | 30834 | 15850 | 28832 | 26078 | 28806 | 23041 | 17193 | 28799 | 28655 | 26212 | 17572 | 29970
CFB5 | 45192 | 43432 | 49224 | 47191 | 50766 | 49221 | 53706 | 48518 | 47909 | 46834 | 51433 | 47301
CFB 6 | 46893 | 46110 | 53768 | 51009 | 53510 | 44099 | 53768 | 47730 | 49669 | 49358 | 46165 | 55471
SRB3 | 49592 | 50176 | 56009 | 45368 | 54740 | 56776 | 56681 | 53044 | 53268 | 57647 | 49662 | 56886 |  | 1574045 | 306.08
TOTAL | 178631 | 159159 | 187833 | 173709 | 187822 | 178448 | 187294 | 178360 | 180842 | 186918 | 178287 | 189628 | 2166931 |  | 194.4544
% H - BLS | 22.88% | 22.88% | 24.86% | 19.88% | 24.98% | 23.65% | 24.52% | 24.24% | 23% | 23.15% | 18.59% | 25.02% | 23.14%
% H - Coal | 77.12% | 77.12% | 75.14% | 80.12% | 75.02% | 76.35% | 75.48% | 75.76% | 77% | 76.85% | 81.41% | 74.98% | 76.86%
Sep - 03 - Dec 03 | 2006-05-01: Sep-04 - Dec-04; Sep-06 - Dec-05; Sep-06 - Dec-06;
Boilers | 2006-01-01: Steam Pressure at boiler outlet; 2006-02-01: Steam Temperature at boiler outlet; 2006-03-01: Enthalpy of the steam at the boiler outlet; 2006-05-01: Boilers; 2006-06-01: Steam Pressure at boiler outlet; 2006-07-01: Steam Temperature at boiler outlet; 2006-08-01: Enthalpy of the steam at the boiler outlet
CFB1 | 2006-01-01: 42; 2006-02-01: 405; 2006-03-01: 766.5; 2006-05-01: CFB1; 2006-06-01: 42; 2006-07-01: 405; 2006-08-01: 766.5
CFB2 | 2006-01-01: 42; 2006-02-01: 405; 2006-03-01: 766.5; 2006-05-01: CFB2; 2006-06-01: 42; 2006-07-01: 405; 2006-08-01: 766.5
CFB3 | 2006-01-01: 11; 2006-02-01: 300; 2006-03-01: 727.3; 2006-05-01: CFB3; 2006-06-01: 11; 2006-07-01: 300; 2006-08-01: 727.3
CFB4 | 2006-01-01: 62.5; 2006-02-01: 480; 2006-03-01: 804.9; 2006-05-01: CFB4; 2006-06-01: 62.5; 2006-07-01: 480; 2006-08-01: 804.9
CFB5 | 2006-01-01: 62.5; 2006-02-01: 480; 2006-03-01: 804.9; 2006-05-01: CFB5; 2006-06-01: 62.5; 2006-07-01: 480; 2006-08-01: 804.9
SRB3 | 2006-01-01: 64; 2006-02-01: 460; 2006-03-01: 793.1; 2006-05-01: CFB6; 2006-06-01: 62.5; 2006-07-01: 480; 2006-08-01: 804.9
Average | 2006-03-01: 777.2; 2006-05-01: SRB3; 2006-06-01: 64; 2006-07-01: 460; 2006-08-01: 793.1
[5 empty] | Average |  |  | 781.1571

## Summary Fuels
F-tot-C
Boilers | 2003-09-03 | 2003-10-01 | 2003-11-26 | 2003-12-01 | Total
CFB1,2&3 | 5383 | 3592 | 3796 | 4293
CFB4 | 5586 | 5361 | 5298 | 5362
CFB5 | 8658 | 10439 | 8709 | 9277
TOTAL | 19627 | 19392 | 17803 | 18932 | 75754
Carbon Contain of Coal | 57.1 | 56.2 | 57.9 | 59.8 | 57.75
NCV Coal | 5398.8139 | 5322.2467 | 5398.8807 | 5439.1452 | 5389.7716
NCV BLS | 3550 |  |  |  | 3550
Boilers | 2004-01-01 | 2004-02-01 | 2004-03-01 | 2004-04-01 | 2004-05-01 | 2004-06-01 | 2004-07-01 | 2004-08-01 | 2004-09-01 | 2004-10-01 | 2004-11-01 | 2004-12-01
CFB1,2&3 | 3474 | 3235 | 3022 | 3292 | 1988 | 1964 | 2467 | 2994 | 1395 | 1322 | 271 | 1483
CFB4 | 5435 | 4971 | 5413 | 5041 | 2035 | 4083 | 5492 | 2638 | 3815 | 4387 | 5245 | 4799
CFB5 | 9417 | 8641 | 9143 | 9248 | 7704 | 7894 | 4043 | 9748 | 8310 | 8032 | 8040 | 9470
CFB 6 |  |  |  |  | 6002 | 6587 | 8937 | 6577 | 8364 | 7356 | 8988 | 7858
TOTAL | 18326 | 16847 | 17578 | 17581 | 17729 | 20528 | 20939 | 21957 | 21884 | 21097 | 22544 | 23610 | 240620
Carbon Contain of Coal | 59.4 | 60 | 60.2 | 57.4 | 56.2 | 55.2 | 59.1 | 59.1 | 45.9 | 45.9 | 54.1 | 47.5 | 55
NCV Coal | 5428.7791 | 5459.8139 | 5463.2815 | 5461.8486 | 5436.9321 | 5350.6551 | 5104.7056 | 4727.4797 | 4646.7067 | 4864.5058 | 4868.0303 | 4699.2051 | 5125.9953
NCV BLS | 2004-04-01: 3060; 2004-10-01: 3000 | 3030
Boilers | 2005-01-01 | 2005-02-01 | 2005-03-01 | 2005-04-01 | 2005-05-01 | 2005-06-01 | 2005-07-01 | 2005-08-01 | 2005-09-01 | 2005-10-01 | 2005-11-01 | 2005-12-01
CFB1,2&3 | 2754 | 4207 | 5269 |  |  | 192 | 90 | 1134 | 987 | 2270 | 1618
CFB4 | 9347 | 8787 | 8168 | 5299 | 5393 | 5218 | 5295 | 5488 | 4385 | 6215 | 5137 | 4787
CFB5 | 10014 | 7977 | 6303 | 8249 | 8794 | 8490 | 8850 | 7329 | 9150 | 10071 | 8377 | 8072
CFB 6 |  |  |  | 8493 | 9150 | 8570 | 9116 | 9087 | 8871 | 6850 | 6769 | 8454
TOTAL | 22115 | 20971 | 19740 | 22041 | 23337 | 22470 | 23351 | 23038 | 23393 | 25406 | 21901 | 21313 | 269076
Carbon Contain of Coal | 54.2 | 56.1 | 50.6 | 50.1 | 50.1 | 49.2 | 50.3 | 46.9 | 49.9 | 51.1 | 53.2 | 55.1 | 51.4
NCV Coal | 4989.1551 | 4827.3815 | 5126.2072 | 4839.6475 | 5015.6148 | 4937.2072 | 4992.2037 | 5036.8294 | 4770.8549 | 4795.1546 | 5210.4051 | 5418.0136 | 4996.5562
NCV BLS | 2005-04-01: 2838; 2005-10-01: 3000 | 2919
Boilers | 2006-01-01 | 2006-02-01 | 2006-03-01 | 2006-04-01 | 2006-05-01 | 2006-06-01 | 2006-07-01 | 2006-08-01 | 2006-09-01 | 2006-10-01 | 2006-11-01 | 2006-12-01
CFB1,2&3 | 1401 | 890 | 5189 | 936 |  | 1111 | 1197 | 220 | 449 | 1701 | 3038
CFB4 | 5484 | 2785 | 8696 | 4691 | 5186 | 4152 | 3163 | 5547 | 5474 | 4945 | 3325 | 4565.2808
CFB5 | 7853 | 7571 | 9254 | 8392 | 9025 | 8916 | 9938 | 9342 | 9181 | 8838 | 9429 | 4908.4812
CFB 6 | 8128 | 7966 |  | 8688 | 9172 | 7684 | 9580 | 8838 | 9161 | 8937 | 8157 | 5084.1806
TOTAL | 22866 | 19212 | 23139 | 22707 | 23383 | 21863 | 23878 | 23947 | 24265 | 24421 | 23949 | 14557.9426 | 268187.9426 | 0.17038
Carbon Contain of Coal | 55.2 | 55.2 | 57.9 | 55.4 | 53.4 | 51.2 | 53 | 51.5 | 49.8 | 52.8 | 50.5 | 51 | 53.075
NCV Coal | 5264.9301 | 5297.4311 | 5220.6823 | 5214.2067 | 5199.6475 | 5190.9046 | 5198.5799 | 5100.0298 | 5026.8805 | 5028.342 | 5107.5558 | 4852.6475 | 5141.8198
NCV BLS | 2006-04-01: 3000; 2006-10-01: 2970 | 2985

## SSCR
Days in M | 2003-09-03 | 2003-10-03 | 2003-11-03 | 2003-12-03 | 2004-01-03 | 2004-02-03 | 2004-03-03 | 2004-04-03 | 2004-05-03 | 2004-06-03 | 2004-07-03 | 2004-08-03 | 2004-09-03 | 2004-10-03 | 2004-11-03 | 2004-12-03 | 2005-01-03 | 2005-02-03 | 2005-03-03 | 2005-04-03 | 2005-05-03 | 2005-06-03 | 2005-07-03 | 2005-08-03 | 2005-09-03 | 2005-10-03 | 2005-11-03 | 2005-12-03 | 2006-01-03 | 2006-02-03 | 2006-03-03 | 2006-04-03 | 2006-05-03 | 2006-06-03 | 2006-07-03 | 2006-08-03 | 2006-09-03 | 2006-10-03 | 2006-11-03 | 2006-12-03
1 | 188.57 | 591.3 | 678.47 | 623.64 | 631.11 | 594.72 | 620.34 | 557.46 | 607.67 | 715.8 | 648.1 | 514.27 | 43.16 | 524.65 | 564.18 | 672.1 | 638.85 | 434.1 | 657.45 | 668.97 | 641.25 | 718.44 | 601.66 | 213.55 | 621.4 | 686.02 | 577.21 | 688.98 | 724.71 | 694.46 | 660.05 | 596.44 | 735.82 | 713.97 | 714.7 | 735.39 | 659.59 | 684.92 | 767.15 | 538.69
2 | 175.1 | 611.36 | 673.95 | 555.86 | 658.65 | 178.32 | 638.82 | 614.89 | 617.43 | 713.04 | 676.18 | 668.33 | 98.24 | 592.83 | 259.92 | 676.13 | 561.17 | 592.29 | 662.93 | 655.99 | 664.47 | 714.72 | 524.49 | 703.34 | 481.71 | 112.63 | 617.83 | 655.67 | 629.76 | 716.8 | 674.55 | 663.91 | 614.3 | 596.63 | 725.85 | 717.42 | 674.85 | 691.43 | 751.34 | 617.65
3 | 744.83 | 637.52 | 601.06 | 586.81 | 623.55 | 571.06 | 645.5 | 656.64 | 655.37 | 681.86 | 702 | 618.26 | 65.24 | 660.25 | 436.07 | 632.02 | 638.67 | 616.52 | 661.3 | 662.53 | 635.52 | 633.93 | 504.4 | 555.34 | 635.11 | 145.23 | 661.58 | 670.5 | 663.38 | 665.83 | 700.5 | 683.23 | 701.48 | 694.27 | 731.74 | 722.08 | 463.91 | 529.83 | 710.72 | 659.51
4 | 452.71 | 597.54 | 613.59 | 615.9 | 698.61 | 599.87 | 553.91 | 639.97 | 670.06 | 674.34 | 647.73 | 610.94 | 107.56 | 678.48 | 640.38 | 604.82 | 639.74 | 596.29 | 656.08 | 720.09 | 614.82 | 691.51 | 629.4 | 603.17 | 648.8 | 114.24 | 616.09 | 659.94 | 573.15 | 663.16 | 723.82 | 307.58 | 706.63 | 697.25 | 733.74 | 0 | 626.35 | 467.08 | 686.64 | 702.91
5 | 484.83 | 582.77 | 603.29 | 679.58 | 666.77 | 607.15 | 585.21 | 617.67 | 631.27 | 633.56 | 648.49 | 603.68 | 615.86 | 650.04 | 645.66 | 588.15 | 662.56 | 658 | 666.52 | 737.84 | 605.25 | 640.15 | 617.51 | 667.81 | 694.98 | 308.99 | 592.7 | 668.53 | 650.43 | 668.82 | 700.67 | 0 | 704.67 | 725.85 | 671.3 | 0 | 705.97 | 604.77 | 722.56 | 720.4
6 | 512.7 | 618.59 | 644.75 | 605.85 | 660.96 | 629.58 | 514.05 | 642.24 | 685.47 | 617.09 | 673.18 | 634.23 | 501.62 | 626.23 | 613.68 | 619.77 | 648.1 | 664.62 | 666.32 | 711.47 | 592.75 | 654.29 | 644.5 | 555.93 | 685.88 | 649.83 | 462.96 | 656.08 | 588.58 | 687.93 | 725.34 | 0 | 542.26 | 732.16 | 669.24 | 596.6 | 731.74 | 677.98 | 683.79 | 663.86
7 | 524.23 | 540.51 | 588.84 | 667.52 | 620.35 | 650.52 | 619.74 | 635.77 | 717.37 | 631.45 | 670.53 | 573.61 | 580.33 | 615.67 | 672.66 | 524.51 | 571.2 | 680.25 | 680.81 | 719.16 | 589.22 | 673.3 | 640.02 | 541.27 | 658.69 | 678.48 | 667.86 | 645.73 | 365.42 | 627.7 | 666.73 | 0 | 633.82 | 712.42 | 461.99 | 596.6 | 678.24 | 690.53 | 742.89 | 703.14
8 | 537.53 | 517.35 | 660.28 | 718.09 | 626.27 | 664.2 | 647.75 | 642.47 | 730.8 | 619.82 | 632.18 | 0 | 642.44 | 672.89 | 671.9 | 640.65 | 275.49 | 659.86 | 623.36 | 686.44 | 672.75 | 698.81 | 659.98 | 596.56 | 679.82 | 675.76 | 593.68 | 672.84 | 600.96 | 608.14 | 636.32 | 0 | 656.65 | 704.4 | 513 | 663.04 | 696.43 | 680.28 | 728.53 | 692.63
9 | 524.33 | 543.92 | 619.47 | 788.81 | 644.85 | 635.31 | 685.64 | 592.71 | 684.17 | 654.54 | 599.53 | 615.55 | 672.57 | 683.16 | 671.24 | 589.3 | 571.25 | 671.49 | 468.46 | 691.25 | 167.42 | 670.12 | 644.3 | 671.26 | 654.48 | 685.98 | 593.28 | 693.58 | 633.52 | 593.99 | 496.31 | 0 | 516.82 | 653.19 | 622.95 | 693.34 | 715.09 | 698.5 | 719.33 | 644.69
10 | 73.23 | 572.73 | 215.93 | 623.1 | 685.95 | 635.98 | 639.22 | 589.98 | 718.66 | 644.69 | 636.66 | 625.33 | 673.38 | 646.77 | 568.73 | 669.52 | 620.37 | 90.12 | 660.36 | 657.59 | 614.12 | 702.7 | 623.22 | 680.44 | 631.43 | 517.24 | 577.63 | 698.32 | 681.19 | 678.18 | 602.17 | 702.81 | 655.55 | 716.88 | 642.85 | 693.14 | 734.14 | 700 | 701.57 | 673.06
11 | 518.2 | 614.72 | 616.79 | 743.75 | 634.7 | 641.07 | 674.04 | 638.4 | 678.47 | 656.64 | 619.48 | 630.96 | 641.92 | 661.44 | 442.96 | 550.66 | 585.48 | 0 | 640.24 | 675.93 | 612.09 | 691.07 | 599.85 | 659.29 | 628.03 | 646.79 | 560.91 | 676.72 | 692.14 | 671.47 | 490.19 | 691.1 | 660.6 | 716.09 | 648.28 | 629.74 | 733.32 | 698.4 | 738.36 | 668.82
12 | 543.48 | 640.47 | 604.4 | 793.55 | 635.1 | 646.31 | 660.53 | 673.03 | 396.78 | 642.45 | 644.92 | 640.12 | 692.51 | 645.89 | 643.16 | 625.8 | 626.92 | 248.12 | 658.68 | 700.76 | 736.89 | 694.07 | 627.34 | 665.09 | 689.1 | 698.27 | 571.1 | 662.63 | 689.03 | 690.38 | 493.48 | 626.91 | 677.85 | 739.21 | 648.33 | 550.85 | 659.99 | 544.71 | 756.4 | 664.43
13 | 522.01 | 653.64 | 638.81 | 305.14 | 642.43 | 621.15 | 639.22 | 663.76 | 434.93 | 636.77 | 593.81 | 592.51 | 631.49 | 634.87 | 637.57 | 637.55 | 599.92 | 623.36 | 663.47 | 590.28 | 602.36 | 671.32 | 654.44 | 692.24 | 657.32 | 572.23 | 635.42 | 681.6 | 628.01 | 703.89 | 513.48 | 626.48 | 675.89 | 697.93 | 640.74 | 661.96 | 694.08 | 707.95 | 660.24 | 635.48
14 | 533 | 660.24 | 660.6 | 412.18 | 678.58 | 629.68 | 616.32 | 612.91 | 698.41 | 640.75 | 642.41 | 619.36 | 642.39 | 546.57 | 617.91 | 561.97 | 625.32 | 643.92 | 654.14 | 688.67 | 657.56 | 565.53 | 639.95 | 713.68 | 662.71 | 670.48 | 639.22 | 706.09 | 681.53 | 672.65 | 512.86 | 675.22 | 639.42 | 713.36 | 651.97 | 674.95 | 618.56 | 692.73 | 676.13 | 696.92
15 | 589.52 | 612.87 | 686.47 | 777.9 | 687.8 | 650.53 | 474.26 | 637.25 | 654.64 | 655.74 | 640.11 | 608.61 | 669.26 | 652.09 | 600.76 | 672.38 | 641.13 | 624.24 | 640.13 | 690.19 | 678.58 | 607.51 | 664.34 | 658.26 | 685.05 | 669.95 | 638.24 | 682.6 | 639.1 | 684.91 | 551 | 630.32 | 706.12 | 697.25 | 563.89 | 691.83 | 721.2 | 702.81 | 714.83 | 708.32
16 | 603.3 | 597.9 | 661.38 | 562.35 | 662.37 | 644.13 | 658.05 | 616.07 | 688.14 | 239.19 | 658.57 | 623.28 | 606.84 | 564.99 | 636.29 | 689.75 | 627.05 | 640.95 | 640.28 | 701.95 | 749.97 | 696.52 | 658.52 | 591.7 | 667.16 | 670.24 | 543.54 | 615.38 | 670.38 | 713.69 | 560 | 683.75 | 683.08 | 703.16 | 466.37 | 682.7 | 628.75 | 705.79 | 692.73 | 657.13
17 | 612.73 | 650.01 | 682.06 | 657.89 | 657.87 | 682.81 | 646.15 | 585.43 | 694.73 | 662.86 | 594.67 | 639.58 | 647.51 | 538.57 | 549.34 | 643.11 | 636.27 | 630.42 | 630.61 | 711.26 | 701.77 | 700.93 | 676.51 | 578.5 | 707.33 | 646.79 | 552.56 | 601.09 | 665.77 | 698.29 | 491.6 | 706.2 | 594.83 | 725.01 | 596.76 | 667.52 | 697.07 | 730.49 | 674.56 | 668.55
18 | 637.99 | 513.1 | 677.62 | 673.09 | 634.71 | 668.67 | 678.64 | 606.84 | 673.4 | 655.22 | 604.18 | 610.94 | 615.44 | 571.08 | 616.97 | 647.08 | 594.61 | 662.51 | 650.22 | 696.23 | 710.34 | 712.97 | 653.3 | 639.02 | 685.96 | 568.57 | 531.94 | 625.74 | 722.19 | 692.46 | 537.11 | 695.36 | 638.42 | 689.56 | 695.77 | 653.28 | 664.38 | 593.9 | 700.03 | 624.47
19 | 614.39 | 641.03 | 717.74 | 696.64 | 677.91 | 669.23 | 667.02 | 584.94 | 684.56 | 665.43 | 613.72 | 595.63 | 675.35 | 577.24 | 615.1 | 625.94 | 619.44 | 661.94 | 656.41 | 685.66 | 722.83 | 675.7 | 368.91 | 671.71 | 682.73 | 595.49 | 580.16 | 586.46 | 667.53 | 704.66 | 553.98 | 703.13 | 578.85 | 751.69 | 716.1 | 660.72 | 695.69 | 732.38 | 721.98 | 684.99
20 | 610.55 | 615.93 | 676.42 | 768.44 | 679.31 | 436.61 | 646.03 | 593.72 | 682.26 | 652.26 | 598.05 | 591.2 | 622.78 | 611.82 | 613.7 | 543.37 | 574.52 | 644.12 | 662.92 | 708.53 | 698.43 | 671.31 | 634.53 | 689.1 | 626.91 | 628.82 | 627.87 | 604.04 | 682.1 | 688.57 | 555.58 | 714.35 | 639.09 | 726.78 | 647.95 | 659.11 | 724.46 | 728.68 | 747.86 | 652.22
21 | 618.64 | 648.77 | 658.9 | 721.49 | 651.78 | 695.89 | 651.93 | 619.17 | 666.04 | 627.82 | 630.51 | 587.91 | 633.92 | 589.89 | 605.65 | 574.76 | 553.93 | 623.17 | 662.92 | 698.71 | 720.89 | 661.41 | 688.37 | 674.64 | 650.04 | 644.64 | 501.69 | 667.09 | 642.92 | 696.04 | 595.95 | 643.78 | 650.43 | 726.69 | 695.06 | 589.58 | 689.82 | 715.75 | 731.13 | 690.57
22 | 557.25 | 600.72 | 599.23 | 645.46 | 635.6 | 627.05 | 382.65 | 624.59 | 652.66 | 637.7 | 649.53 | 603.68 | 629.24 | 578.09 | 609.8 | 621.66 | 613.22 | 563.74 | 644.35 | 686.84 | 726.43 | 673.06 | 654.07 | 674.14 | 678.74 | 685.64 | 436.12 | 679.15 | 692.25 | 693.37 | 629.94 | 721.27 | 711.32 | 731.53 | 598.08 | 630.49 | 679.57 | 779.99 | 0 | 702.58
23 | 482.41 | 606.3 | 241.13 | 645.94 | 659.65 | 651.65 | 583.55 | 678.24 | 661.56 | 517.05 | 671.27 | 585.76 | 646.38 | 593.26 | 637.33 | 617.23 | 639.57 | 49.78 | 652.04 | 700.87 | 756.7 | 715.84 | 677.47 | 564.9 | 612.56 | 656.96 | 388.2 | 678.96 | 674.96 | 701.78 | 631.3 | 693.87 | 682.45 | 729.31 | 648.45 | 639.53 | 676.66 | 784.85 | 0 | 719.71
24 | 540.74 | 647.14 | 237.12 | 683.7 | 660.96 | 650.59 | 651.4 | 668.83 | 615.35 | 451.06 | 645.4 | 585.86 | 598.43 | 596.29 | 379.8 | 635.17 | 565.67 | 424.61 | 640.83 | 695.09 | 696.77 | 718.49 | 701.14 | 305.3 | 675 | 642.72 | 587.42 | 671.94 | 685.55 | 644.49 | 607.52 | 680.44 | 701.92 | 328.74 | 690.54 | 637.36 | 681.59 | 742.67 | 0 | 731.18
25 | 532.33 | 665.52 | 941.1 | 680.94 | 628.23 | 658.82 | 676.49 | 649.12 | 640.96 | 565.26 | 633.27 | 622.83 | 343.75 | 516.1 | 673.6 | 633.75 | 519.27 | 621.6 | 625.3 | 689.93 | 699.8 | 632.8 | 552.47 | 544.33 | 664.01 | 517.43 | 623.97 | 704.76 | 469.87 | 698.71 | 676.42 | 689.94 | 651.68 | 564.11 | 679.59 | 656.18 | 694.92 | 766.25 | 0 | 745.84
26 | 573.63 | 646.26 | 665.21 | 599.35 | 569.81 | 639.29 | 589.31 | 603.31 | 608.08 | 645.8 | 655.57 | 659.69 | 513.54 | 538.34 | 670.64 | 633.44 | 605.3 | 611.08 | 626.42 | 645.3 | 715.75 | 671.25 | 525.72 | 599.9 | 689.99 | 606.65 | 644.53 | 703.53 | 560.95 | 693.87 | 693.91 | 657.77 | 641.72 | 725.79 | 694 | 660.82 | 607.77 | 763.57 | 378.47 | 744.57
27 | 594.68 | 646.26 | 611.24 | 593.15 | 602.83 | 606.81 | 660.94 | 602.33 | 669.44 | 650.45 | 654.41 | 643.56 | 604.45 | 563.21 | 645.04 | 635.1 | 609.98 | 632.03 | 598.17 | 634.41 | 683.68 | 684.22 | 589.8 | 574.99 | 661.52 | 576.93 | 669.02 | 684.1 | 619.06 | 682.65 | 691.53 | 681.53 | 678.91 | 726.15 | 698.5 | 656.3 | 671.06 | 788.62 | 548.5 | 693.36
28 | 627.47 | 680.76 | 645.1 | 592.58 | 634.71 | 565.96 | 598.56 | 620.92 | 674.99 | 596 | 640.55 | 585.47 | 639.14 | 653.36 | 671.61 | 649.82 | 596.6 | 660.92 | 624.84 | 651.83 | 681.97 | 697.06 | 595.6 | 644.01 | 687.61 | 604.21 | 646.17 | 690.42 | 679.93 | 674.75 | 700.03 | 695.23 | 653.75 | 728.16 | 677.24 | 653.71 | 685.68 | 728.56 | 630.5 | 644.07
29 | 640.2 | 631.97 | 695.76 | 609.23 | 590.12 | 638.73 | 631.02 | 601.13 | 515.77 | 688.74 | 646.7 | 600.27 | 562.09 | 637.99 | 648.81 | 637.51 | 637.21 |  | 652.37 | 636.27 | 731.6 | 644.1 | 594.76 | 650.97 | 689.4 | 628.43 | 663.04 | 719.02 | 691.41 |  | 475.71 | 745.1 | 669.5 | 723.36 | 714.31 | 621.61 | 591.98 | 756.7 | 685.52 | 673.92
30 | 649.53 | 622.66 | 642.2 | 630.2 | 586 |  | 627.1 | 606.78 | 661.63 | 639.74 | 627.59 | 635.12 | 493.17 | 607.41 | 656.38 | 626.05 | 630.79 |  | 604.53 | 669.73 | 636.63 | 429.96 | 610.51 | 648.78 | 671.76 | 580.55 | 678.56 | 680.45 | 692.25 |  | 488.3 | 739.9 | 682.1 | 724.59 | 718.07 | 604.3 | 624.77 | 744.91 | 593.81 | 663.47
31 | 2003-10-03: 650.14; 2003-12-03: 585.39; 2004-01-03: 595.42; 2004-03-03: 607.6; 2004-05-03: 652.5; 2004-07-03: 638.6; 2004-08-03: 622.17; 2004-10-03: 603.07; 2004-12-03: 639.58; 2005-01-03: 607.9; 2005-03-03: 624.37; 2005-05-03: 693.97; 2005-07-03: 417.35; 2005-08-03: 628.8; 2005-10-03: 540.03; 2005-12-03: 700.04; 2006-01-03: 720.59; 2006-03-03: 491.43; 2006-05-03: 708.36; 2006-07-03: 698.72; 2006-08-03: 624.83; 2006-10-03: 751.15; 2006-12-03: 679.62
Annual Avg Prdn lvl | 2003-09-03: 599.8569; 2004-01-03: 613.8348; 2005-01-03: 624.8115; 2006-01-03: 644.1935
-5% of Annual Avg | 2003-10-03: 569.864; 2004-07-03: 583.1431; 2005-07-03: 593.5709; 2006-07-03: 611.9839
+5 % of Annual Avg | 2003-10-03: 629.8497; 2004-07-03: 644.5265; 2005-07-03: 656.0521; 2006-07-03: 676.4032
| 5444.91 | 7845.39 | 5457.91 | 6035 | 8711.32 | 8750.52 | 9350.14 | 14129.49 | 3720.76 | 8213.64 | 11235.64 | 15932.81 | 8124.34 | 7355.22 | 9379 | 11886.6 | 13682.44 | 7507.7 | 10772.2 | 3223.8 | 4962.04 | 3812.78 | 10664.96 | 5011.21 | 5708.76 | 6294.37 | 6283.02 | 3747.65 | 7784.82 | 5288.87 | 3898.89 | 4524.39 | 9080.82 | 653.19 | 6492.06 | 11051.15 | 5828.3 |  | 2641.43 | 9811.33
#VALUE!
STEAM
Days in M | 2003-09-03 | 2003-10-03 | 2003-11-03 | 2003-12-03 | 2004-01-03 | 2004-02-03 | 2004-03-03 | 2004-04-03 | 2004-05-03 | 2004-06-03 | 2004-07-03 | 2004-08-03 | 2004-09-03 | 2004-10-03 | 2004-11-03 | 2004-12-03 | 2005-01-03 | 2005-02-03 | 2005-03-03 | 2005-04-03 | 2005-05-03 | 2005-06-03 | 2005-07-03 | 2005-08-03 | 2005-09-03 | 2005-10-03 | 2005-11-03 | 2005-12-03 | 2006-01-03 | 2006-02-03 | 2006-03-03 | 2006-04-03 | 2006-05-03 | 2006-06-03 | 2006-07-03 | 2006-08-03 | 2006-09-03 | 2006-10-03 | 2006-11-03 | 2006-12-03
1 | 292 | 394 | 469 | 487 | 500 | 427 | 481 | 328 | 487 | 520 | 412 | 451 | 280 | 420 | 491 | 467 | 484 | 491 | 470 | 491 | 426 | 496 | 515 | 370 | 446 | 551 | 565 | 491 | 494 | 477 | 537 | 530 | 529 | 495 | 559 | 472 | 392 | 464 | 454 | 399
2 | 96 | 372 | 680 | 386 | 444 | 125 | 451 | 565 | 490 | 440 | 474 | 484 | 0 | 489 | 163 | 382 | 392 | 413 | 419 | 502 | 482 | 501 | 443 | 469 | 321 | 21 | 569 | 420 | 517 | 473 | 547 | 547 | 529 | 353 | 547 | 496 | 411 | 398 | 530 | 477
3 | 263 | 389 | 435 | 392 | 509 | 510 | 484 | 569 | 482 | 513 | 465 | 430 | 0 | 467 | 445 | 479 | 486 | 453 | 486 | 484 | 468 | 466 | 480 | 364 | 480 | 0 | 522 | 487 | 429 | 482 | 546 | 549 | 532 | 491 | 417 | 505 | 355 | 457 | 469 | 488
4 | 334 | 354 | 444 | 433 | 467 | 447 | 463 | 547 | 421 | 500 | 499 | 494 | 144 | 469 | 476 | 471 | 490 | 487 | 481 | 495 | 409 | 572 | 498 | 505 | 484 | 0 | 511 | 482 | 493 | 490 | 542 | 307 | 528 | 480 | 515 | 447 | 395 | 236 | 472 | 482
5 | 394 | 416 | 372 | 101 | 442 | 490 | 476 | 540 | 503 | 493 | 485 | 443 | 514 | 482 | 406 | 384 | 482 | 491 | 502 | 503 | 492 | 552 | 434 | 509 | 402 | 303 | 570 | 482 | 430 | 486 | 562 | 1 | 534 | 463 | 483 | 388 | 399 | 464 | 482 | 480
6 | 443 | 415 | 408 | 438 | 457 | 492 | 426 | 347 | 493 | 398 | 434 | 304 | 297 | 426 | 450 | 473 | 482 | 499 | 507 | 500 | 419 | 428 | 502 | 346 | 470 | 571 | 355 | 495 | 446 | 477 | 560 | 0 | 197 | 467 | 479 | 0 | 461 | 472 | 503 | 480
7 | 367 | 510 | 410 | 468 | 478 | 425 | 429 | 484 | 453 | 539 | 466 | 250 | 398 | 489 | 473 | 355 | 483 | 495 | 495 | 491 | 398 | 592 | 515 | 504 | 513 | 559 | 558 | 483 | 301 | 475 | 595 | 0 | 566 | 464 | 260 | 31 | 386 | 472 | 505 | 477
8 | 436 | 358 | 501 | 463 | 424 | 504 | 465 | 487 | 491 | 500 | 472 | 505 | 493 | 460 | 481 | 421 | 197 | 500 | 322 | 491 | 458 | 596 | 433 | 445 | 531 | 560 | 450 | 496 | 394 | 487 | 509 | 0 | 546 | 474 | 505 | 534 | 488 | 457 | 501 | 473
9 | 483 | 432 | 408 | 490 | 446 | 459 | 482 | 463 | 446 | 508 | 503 | 412 | 479 | 426 | 479 | 452 | 487 | 500 | 485 | 431 | 128 | 407 | 517 | 497 | 423 | 469 | 565 | 488 | 476 | 486 | 443 | 0 | 285 | 471 | 497 | 504 | 475 | 462 | 510 | 480
10 | 199 | 447 | 381 | 461 | 498 | 480 | 473 | 443 | 464 | 517 | 433 | 494 | 468 | 473 | 468 | 471 | 424 | 254 | 558 | 501 | 569 | 497 | 506 | 492 | 507 | 488 | 565 | 497 | 487 | 348 | 552 | 537 | 519 | 379 | 521 | 512 | 452 | 466 | 506 | 470
11 | 561 | 364 | 523 | 494 | 492 | 481 | 483 | 441 | 481 | 476 | 499 | 489 | 495 | 488 | 357 | 373 | 380 | 153 | 550 | 446 | 508 | 491 | 498 | 429 | 509 | 560 | 477 | 449 | 490 | 555 | 551 | 556 | 535 | 497 | 527 | 484 | 464 | 431 | 505 | 462
12 | 460 | 395 | 484 | 457 | 504 | 469 | 473 | 504 | 385 | 497 | 475 | 495 | 475 | 376 | 472 | 528 | 488 | 200 | 554 | 490 | 523 | 501 | 498 | 496 | 468 | 556 | 524 | 518 | 502 | 563 | 499 | 499 | 522 | 482 | 505 | 377 | 425 | 304 | 475 | 400
13 | 530 | 330 | 526 | 342 | 502 | 470 | 409 | 445 | 254 | 511 | 284 | 424 | 472 | 478 | 470 | 531 | 482 | 507 | 549 | 488 | 498 | 425 | 486 | 499 | 524 | 458 | 554 | 500 | 485 | 583 | 474 | 528 | 509 | 487 | 437 | 471 | 451 | 476 | 493 | 482
14 | 415 | 447 | 475 | 243 | 438 | 470 | 459 | 508 | 504 | 458 | 576 | 492 | 480 | 405 | 477 | 378 | 479 | 490 | 333 | 486 | 566 | 500 | 433 | 503 | 458 | 565 | 522 | 492 | 476 | 559 | 558 | 530 | 491 | 497 | 525 | 419 | 396 | 476 | 483 | 481
15 | 567 | 356 | 462 | 508 | 496 | 470 | 323 | 508 | 490 | 508 | 548 | 479 | 348 | 481 | 472 | 475 | 483 | 484 | 497 | 493 | 570 | 477 | 502 | 502 | 510 | 562 | 516 | 500 | 479 | 553 | 545 | 501 | 526 | 506 | 528 | 475 | 468 | 473 | 414 | 401
16 | 440 | 388 | 553 | 424 | 491 | 463 | 481 | 492 | 489 | 217 | 444 | 487 | 473 | 427 | 433 | 473 | 406 | 442 | 497 | 495 | 567 | 467 | 501 | 435 | 488 | 566 | 390 | 401 | 476 | 554 | 547 | 501 | 528 | 496 | 482 | 467 | 416 | 465 | 466 | 484
17 | 518 | 407 | 482 | 513 | 429 | 408 | 472 | 397 | 448 | 229 | 547 | 437 | 521 | 447 | 342 | 477 | 486 | 389 | 499 | 407 | 573 | 515 | 505 | 498 | 493 | 491 | 362 | 492 | 475 | 545 | 479 | 556 | 441 | 492 | 408 | 473 | 472 | 415 | 469 | 475
18 | 419 | 426 | 554 | 462 | 487 | 424 | 472 | 495 | 499 | 482 | 559 | 459 | 534 | 424 | 525 | 403 | 489 | 485 | 486 | 482 | 366 | 509 | 431 | 496 | 482 | 524 | 408 | 476 | 469 | 541 | 517 | 559 | 437 | 477 | 482 | 488 | 418 | 389 | 476 | 414
19 | 444 | 463 | 580 | 384 | 470 | 485 | 471 | 494 | 485 | 493 | 461 | 445 | 509 | 461 | 520 | 480 | 482 | 484 | 430 | 494 | 498 | 503 | 377 | 496 | 530 | 567 | 492 | 496 | 474 | 540 | 539 | 541 | 526 | 472 | 475 | 483 | 475 | 458 | 463 | 479
20 | 387 | 445 | 540 | 509 | 451 | 247 | 422 | 437 | 477 | 421 | 565 | 430 | 416 | 509 | 345 | 399 | 375 | 486 | 490 | 433 | 487 | 511 | 503 | 493 | 535 | 449 | 482 | 401 | 477 | 468 | 535 | 546 | 506 | 473 | 488 | 479 | 456 | 409 | 451 | 475
21 | 542 | 473 | 447 | 517 | 485 | 477 | 489 | 493 | 453 | 505 | 560 | 397 | 491 | 507 | 455 | 486 | 433 | 489 | 502 | 498 | 505 | 419 | 500 | 493 | 576 | 571 | 403 | 479 | 361 | 558 | 524 | 530 | 513 | 487 | 481 | 428 | 469 | 429 | 456 | 481
22 | 430 | 617 | 479 | 447 | 493 | 480 | 256 | 448 | 490 | 457 | 556 | 481 | 521 | 466 | 459 | 492 | 483 | 430 | 499 | 490 | 507 | 576 | 502 | 427 | 577 | 407 | 215 | 469 | 480 | 551 | 539 | 537 | 490 | 483 | 442 | 479 | 472 | 416 | 51 | 475
23 | 453 | 510 | 252 | 445 | 378 | 473 | 454 | 497 | 485 | 384 | 549 | 454 | 512 | 401 | 464 | 509 | 307 | 232 | 422 | 487 | 495 | 584 | 507 | 474 | 486 | 559 | 489 | 482 | 482 | 537 | 553 | 456 | 489 | 489 | 504 | 462 | 416 | 434 | 0 | 488
24 | 414 | 191 | 270 | 502 | 494 | 461 | 483 | 449 | 441 | 375 | 505 | 491 | 422 | 456 | 265 | 430 | 392 | 339 | 502 | 491 | 494 | 578 | 530 | 150 | 579 | 431 | 488 | 478 | 486 | 537 | 528 | 530 | 488 | 297 | 483 | 379 | 470 | 446 | 0 | 489
25 | 332 | 459 | 557 | 505 | 428 | 470 | 496 | 489 | 419 | 484 | 533 | 461 | 382 | 365 | 471 | 492 | 481 | 489 | 490 | 491 | 493 | 594 | 450 | 544 | 577 | 400 | 433 | 429 | 266 | 536 | 441 | 539 | 491 | 441 | 418 | 467 | 464 | 453 | 0 | 491
26 | 382 | 513 | 558 | 462 | 492 | 478 | 464 | 427 | 448 | 521 | 567 | 446 | 515 | 486 | 475 | 470 | 480 | 446 | 425 | 430 | 496 | 602 | 512 | 535 | 562 | 601 | 484 | 519 | 507 | 526 | 542 | 533 | 420 | 591 | 479 | 472 | 419 | 483 | 270 | 484
27 | 350 | 446 | 325 | 366 | 351 | 428 | 465 | 493 | 445 | 517 | 548 | 406 | 507 | 415 | 481 | 482 | 432 | 476 | 491 | 493 | 510 | 604 | 488 | 528 | 498 | 579 | 470 | 514 | 510 | 526 | 533 | 526 | 504 | 561 | 409 | 463 | 456 | 471 | 508 | 486
28 | 398 | 526 | 434 | 501 | 480 | 425 | 407 | 496 | 446 | 410 | 577 | 479 | 474 | 483 | 472 | 477 | 480 | 403 | 502 | 479 | 434 | 587 | 417 | 477 | 557 | 562 | 437 | 525 | 490 | 463 | 557 | 523 | 511 | 539 | 462 | 385 | 452 | 466 | 478 | 480
29 | 387 | 401 | 432 | 447 | 446 | 476 | 500 | 507 | 453 | 514 | 401 | 454 | 440 | 491 | 362 | 400 | 486 |  | 492 | 485 | 497 | 584 | 502 | 531 | 491 | 483 | 480 | 497 | 487 |  | 464 | 524 | 502 | 476 | 506 | 465 | 424 | 474 | 474 | 480
30 | 389 | 541 | 507 | 506 | 448 |  | 499 | 417 | 411 | 502 | 487 | 355 | 503 | 489 | 471 | 489 | 484 |  | 489 | 490 | 487 | 260 | 502 | 528 | 560 | 562 | 498 | 489 | 497 |  | 571 | 524 | 504 | 560 | 474 | 394 | 472 | 474 | 411 | 398
31 | 2003-10-03: 434; 2003-12-03: 503; 2004-01-03: 469; 2004-03-03: 497; 2004-05-03: 505; 2004-07-03: 421; 2004-08-03: 396; 2004-10-03: 495; 2004-12-03: 488; 2005-01-03: 413; 2005-03-03: 422; 2005-05-03: 474; 2005-07-03: 230; 2005-08-03: 414; 2005-10-03: 430; 2005-12-03: 492; 2006-01-03: 485; 2006-03-03: 549; 2006-05-03: 502; 2006-07-03: 442; 2006-08-03: 284; 2006-10-03: 544; 2006-12-03: 484
| 4028 | 5619 | 3880 | 4490 | 6449 | 6541 | 6923 | 10929 | 2788 | 6308 | 9005 | 11588 | 6292 | 5606 | 6905 | 8948 | 10106 | 5638 | 7918 | 2389 | 3857 | 3101 | 8259 | 3931 | 4446 | 5286 | 4958 | 2673 | 5594 | 4047 | 3280 | 3668 | 7075 | 471 | 4966 | 7687 | 3781 |  | 1923 | 6945
| 0.73977 | 0.71622 | 0.71089 | 0.74399 | 0.7403 | 0.7475 | 0.74042 | 0.77349 | 0.74931 | 0.76799 | 0.80147 | 0.7273 | 0.77446 | 0.76218 | 0.73622 | 0.75278 | 0.73861 | 0.75096 | 0.73504 | 0.74105 | 0.7773 | 0.81332 | 0.77441 | 0.78444 | 0.7788 | 0.8398 | 0.78911 | 0.71325 | 0.71858 | 0.76519 | 0.84127 | 0.81072 | 0.77911 | 0.72108 | 0.76493 | 0.69558 | 0.64873 |  | 0.72801 | 0.70786
|  |  |  | 0.72772 | [11 empty] | 0.75612 | [11 empty] | 0.76967 | [11 empty] | 0.74373
Note on M9: adipau428: no bls produced but steam consumption exist - is it taken for maintainennce
Note on N45: adipau428: data missing
Note on S12: adipau428: no bls produced but steam consumption exist - is it taken for maintainennce
Note on AG6: adipau428: data missing
Note on AG32: adipau428: data missing

## Steam
'EVAPORATOR-3' | 'STEAM' | RDNG_DATE | TCONS
EVAPORATOR-3 | STEAM | 2003-09-01 | 292
EVAPORATOR-3 | STEAM | 2003-09-02 | 96
EVAPORATOR-3 | STEAM | 2003-09-03 | 263
EVAPORATOR-3 | STEAM | 2003-09-04 | 334
EVAPORATOR-3 | STEAM | 2003-09-05 | 394
EVAPORATOR-3 | STEAM | 2003-09-06 | 443
EVAPORATOR-3 | STEAM | 2003-09-07 | 367
EVAPORATOR-3 | STEAM | 2003-09-08 | 436
EVAPORATOR-3 | STEAM | 2003-09-09 | 483
EVAPORATOR-3 | STEAM | 2003-09-10 | 199
EVAPORATOR-3 | STEAM | 2003-09-11 | 561
EVAPORATOR-3 | STEAM | 2003-09-12 | 460
EVAPORATOR-3 | STEAM | 2003-09-13 | 530
EVAPORATOR-3 | STEAM | 2003-09-14 | 415
EVAPORATOR-3 | STEAM | 2003-09-15 | 567
EVAPORATOR-3 | STEAM | 2003-09-16 | 440
EVAPORATOR-3 | STEAM | 2003-09-17 | 518
EVAPORATOR-3 | STEAM | 2003-09-18 | 419
EVAPORATOR-3 | STEAM | 2003-09-19 | 444
EVAPORATOR-3 | STEAM | 2003-09-20 | 387
EVAPORATOR-3 | STEAM | 2003-09-21 | 542
EVAPORATOR-3 | STEAM | 2003-09-22 | 430
EVAPORATOR-3 | STEAM | 2003-09-23 | 453
EVAPORATOR-3 | STEAM | 2003-09-24 | 414
EVAPORATOR-3 | STEAM | 2003-09-25 | 332
EVAPORATOR-3 | STEAM | 2003-09-26 | 382
EVAPORATOR-3 | STEAM | 2003-09-27 | 350
EVAPORATOR-3 | STEAM | 2003-09-28 | 398
EVAPORATOR-3 | STEAM | 2003-09-29 | 387
EVAPORATOR-3 | STEAM | 2003-09-30 | 389
12125
EVAPORATOR-3 | STEAM | 2003-10-01 | 394
EVAPORATOR-3 | STEAM | 2003-10-02 | 372
EVAPORATOR-3 | STEAM | 2003-10-03 | 389
EVAPORATOR-3 | STEAM | 2003-10-04 | 354
EVAPORATOR-3 | STEAM | 2003-10-05 | 416
EVAPORATOR-3 | STEAM | 2003-10-06 | 415
EVAPORATOR-3 | STEAM | 2003-10-07 | 510
EVAPORATOR-3 | STEAM | 2003-10-08 | 358
EVAPORATOR-3 | STEAM | 2003-10-09 | 432
EVAPORATOR-3 | STEAM | 2003-10-10 | 447
EVAPORATOR-3 | STEAM | 2003-10-11 | 364
EVAPORATOR-3 | STEAM | 2003-10-12 | 395
EVAPORATOR-3 | STEAM | 2003-10-13 | 330
EVAPORATOR-3 | STEAM | 2003-10-14 | 447
EVAPORATOR-3 | STEAM | 2003-10-15 | 356
EVAPORATOR-3 | STEAM | 2003-10-16 | 388
EVAPORATOR-3 | STEAM | 2003-10-17 | 407
EVAPORATOR-3 | STEAM | 2003-10-18 | 426
EVAPORATOR-3 | STEAM | 2003-10-19 | 463
EVAPORATOR-3 | STEAM | 2003-10-20 | 445
EVAPORATOR-3 | STEAM | 2003-10-21 | 473
EVAPORATOR-3 | STEAM | 2003-10-22 | 617
EVAPORATOR-3 | STEAM | 2003-10-23 | 510
EVAPORATOR-3 | STEAM | 2003-10-24 | 191
EVAPORATOR-3 | STEAM | 2003-10-25 | 459
EVAPORATOR-3 | STEAM | 2003-10-26 | 513
EVAPORATOR-3 | STEAM | 2003-10-27 | 446
EVAPORATOR-3 | STEAM | 2003-10-28 | 526
EVAPORATOR-3 | STEAM | 2003-10-29 | 401
EVAPORATOR-3 | STEAM | 2003-10-30 | 541
EVAPORATOR-3 | STEAM | 2003-10-31 | 434
13219
EVAPORATOR-3 | STEAM | 2003-11-01 | 469
EVAPORATOR-3 | STEAM | 2003-11-02 | 680
EVAPORATOR-3 | STEAM | 2003-11-03 | 435
EVAPORATOR-3 | STEAM | 2003-11-04 | 444
EVAPORATOR-3 | STEAM | 2003-11-05 | 372
EVAPORATOR-3 | STEAM | 2003-11-06 | 408
EVAPORATOR-3 | STEAM | 2003-11-07 | 410
EVAPORATOR-3 | STEAM | 2003-11-08 | 501
EVAPORATOR-3 | STEAM | 2003-11-09 | 408
EVAPORATOR-3 | STEAM | 2003-11-10 | 381
EVAPORATOR-3 | STEAM | 2003-11-11 | 523
EVAPORATOR-3 | STEAM | 2003-11-12 | 484
EVAPORATOR-3 | STEAM | 2003-11-13 | 526
EVAPORATOR-3 | STEAM | 2003-11-14 | 475
EVAPORATOR-3 | STEAM | 2003-11-15 | 462
EVAPORATOR-3 | STEAM | 2003-11-16 | 553
EVAPORATOR-3 | STEAM | 2003-11-17 | 482
EVAPORATOR-3 | STEAM | 2003-11-18 | 554
EVAPORATOR-3 | STEAM | 2003-11-19 | 580
EVAPORATOR-3 | STEAM | 2003-11-20 | 540
EVAPORATOR-3 | STEAM | 2003-11-21 | 447
EVAPORATOR-3 | STEAM | 2003-11-22 | 479
EVAPORATOR-3 | STEAM | 2003-11-23 | 252
EVAPORATOR-3 | STEAM | 2003-11-24 | 270
EVAPORATOR-3 | STEAM | 2003-11-25 | 557
EVAPORATOR-3 | STEAM | 2003-11-26 | 558
EVAPORATOR-3 | STEAM | 2003-11-27 | 325
EVAPORATOR-3 | STEAM | 2003-11-28 | 434
EVAPORATOR-3 | STEAM | 2003-11-29 | 432
EVAPORATOR-3 | STEAM | 2003-11-30 | 507
13948
EVAPORATOR-3 | STEAM | 2003-12-01 | 487
EVAPORATOR-3 | STEAM | 2003-12-02 | 386
EVAPORATOR-3 | STEAM | 2003-12-03 | 392
EVAPORATOR-3 | STEAM | 2003-12-04 | 433
EVAPORATOR-3 | STEAM | 2003-12-05 | 101
EVAPORATOR-3 | STEAM | 2003-12-06 | 438
EVAPORATOR-3 | STEAM | 2003-12-07 | 468
EVAPORATOR-3 | STEAM | 2003-12-08 | 463
EVAPORATOR-3 | STEAM | 2003-12-09 | 490
EVAPORATOR-3 | STEAM | 2003-12-10 | 461
EVAPORATOR-3 | STEAM | 2003-12-11 | 494
EVAPORATOR-3 | STEAM | 2003-12-12 | 457
EVAPORATOR-3 | STEAM | 2003-12-13 | 342
EVAPORATOR-3 | STEAM | 2003-12-14 | 243
EVAPORATOR-3 | STEAM | 2003-12-15 | 508
EVAPORATOR-3 | STEAM | 2003-12-16 | 424
EVAPORATOR-3 | STEAM | 2003-12-17 | 513
EVAPORATOR-3 | STEAM | 2003-12-18 | 462
EVAPORATOR-3 | STEAM | 2003-12-19 | 384
EVAPORATOR-3 | STEAM | 2003-12-20 | 509
EVAPORATOR-3 | STEAM | 2003-12-21 | 517
EVAPORATOR-3 | STEAM | 2003-12-22 | 447
EVAPORATOR-3 | STEAM | 2003-12-23 | 445
EVAPORATOR-3 | STEAM | 2003-12-24 | 502
EVAPORATOR-3 | STEAM | 2003-12-25 | 505
EVAPORATOR-3 | STEAM | 2003-12-26 | 462
EVAPORATOR-3 | STEAM | 2003-12-27 | 366
EVAPORATOR-3 | STEAM | 2003-12-28 | 501
EVAPORATOR-3 | STEAM | 2003-12-29 | 447
EVAPORATOR-3 | STEAM | 2003-12-30 | 506
EVAPORATOR-3 | STEAM | 2003-12-31 | 503
13656
EVAPORATOR-3 | STEAM | 2004-01-01 | 500
EVAPORATOR-3 | STEAM | 2004-01-02 | 444
EVAPORATOR-3 | STEAM | 2004-01-03 | 509
EVAPORATOR-3 | STEAM | 2004-01-04 | 467
EVAPORATOR-3 | STEAM | 2004-01-05 | 442
EVAPORATOR-3 | STEAM | 2004-01-06 | 457
EVAPORATOR-3 | STEAM | 2004-01-07 | 478
EVAPORATOR-3 | STEAM | 2004-01-08 | 424
EVAPORATOR-3 | STEAM | 2004-01-09 | 446
EVAPORATOR-3 | STEAM | 2004-01-10 | 498
EVAPORATOR-3 | STEAM | 2004-01-11 | 492
EVAPORATOR-3 | STEAM | 2004-01-12 | 504
EVAPORATOR-3 | STEAM | 2004-01-13 | 502
EVAPORATOR-3 | STEAM | 2004-01-14 | 438
EVAPORATOR-3 | STEAM | 2004-01-15 | 496
EVAPORATOR-3 | STEAM | 2004-01-16 | 491
EVAPORATOR-3 | STEAM | 2004-01-17 | 429
EVAPORATOR-3 | STEAM | 2004-01-18 | 487
EVAPORATOR-3 | STEAM | 2004-01-19 | 470
EVAPORATOR-3 | STEAM | 2004-01-20 | 451
EVAPORATOR-3 | STEAM | 2004-01-21 | 485
EVAPORATOR-3 | STEAM | 2004-01-22 | 493
EVAPORATOR-3 | STEAM | 2004-01-23 | 378
EVAPORATOR-3 | STEAM | 2004-01-24 | 494
EVAPORATOR-3 | STEAM | 2004-01-25 | 428
EVAPORATOR-3 | STEAM | 2004-01-26 | 492
EVAPORATOR-3 | STEAM | 2004-01-27 | 351
EVAPORATOR-3 | STEAM | 2004-01-28 | 480
EVAPORATOR-3 | STEAM | 2004-01-29 | 446
EVAPORATOR-3 | STEAM | 2004-01-30 | 448
EVAPORATOR-3 | STEAM | 2004-01-31 | 469
14389
EVAPORATOR-3 | STEAM | 2004-02-01 | 427
EVAPORATOR-3 | STEAM | 2004-02-02 | 125
EVAPORATOR-3 | STEAM | 2004-02-03 | 510
EVAPORATOR-3 | STEAM | 2004-02-04 | 447
EVAPORATOR-3 | STEAM | 2004-02-05 | 490
EVAPORATOR-3 | STEAM | 2004-02-06 | 492
EVAPORATOR-3 | STEAM | 2004-02-07 | 425
EVAPORATOR-3 | STEAM | 2004-02-08 | 504
EVAPORATOR-3 | STEAM | 2004-02-09 | 459
EVAPORATOR-3 | STEAM | 2004-02-10 | 480
EVAPORATOR-3 | STEAM | 2004-02-11 | 481
EVAPORATOR-3 | STEAM | 2004-02-12 | 469
EVAPORATOR-3 | STEAM | 2004-02-13 | 470
EVAPORATOR-3 | STEAM | 2004-02-14 | 470
EVAPORATOR-3 | STEAM | 2004-02-15 | 470
EVAPORATOR-3 | STEAM | 2004-02-16 | 463
EVAPORATOR-3 | STEAM | 2004-02-17 | 408
EVAPORATOR-3 | STEAM | 2004-02-18 | 424
EVAPORATOR-3 | STEAM | 2004-02-19 | 485
EVAPORATOR-3 | STEAM | 2004-02-20 | 247
EVAPORATOR-3 | STEAM | 2004-02-21 | 477
EVAPORATOR-3 | STEAM | 2004-02-22 | 480
EVAPORATOR-3 | STEAM | 2004-02-23 | 473
EVAPORATOR-3 | STEAM | 2004-02-24 | 461
EVAPORATOR-3 | STEAM | 2004-02-25 | 470
EVAPORATOR-3 | STEAM | 2004-02-26 | 478
EVAPORATOR-3 | STEAM | 2004-02-27 | 428
EVAPORATOR-3 | STEAM | 2004-02-28 | 425
EVAPORATOR-3 | STEAM | 2004-02-29 | 476
12914
EVAPORATOR-3 | STEAM | 2004-03-01 | 481
EVAPORATOR-3 | STEAM | 2004-03-02 | 451
EVAPORATOR-3 | STEAM | 2004-03-03 | 484
EVAPORATOR-3 | STEAM | 2004-03-04 | 463
EVAPORATOR-3 | STEAM | 2004-03-05 | 476
EVAPORATOR-3 | STEAM | 2004-03-06 | 426
EVAPORATOR-3 | STEAM | 2004-03-07 | 429
EVAPORATOR-3 | STEAM | 2004-03-08 | 465
EVAPORATOR-3 | STEAM | 2004-03-09 | 482
EVAPORATOR-3 | STEAM | 2004-03-10 | 473
EVAPORATOR-3 | STEAM | 2004-03-11 | 483
EVAPORATOR-3 | STEAM | 2004-03-12 | 473
EVAPORATOR-3 | STEAM | 2004-03-13 | 409
EVAPORATOR-3 | STEAM | 2004-03-14 | 459
EVAPORATOR-3 | STEAM | 2004-03-15 | 323
EVAPORATOR-3 | STEAM | 2004-03-16 | 481
EVAPORATOR-3 | STEAM | 2004-03-17 | 472
EVAPORATOR-3 | STEAM | 2004-03-18 | 472
EVAPORATOR-3 | STEAM | 2004-03-19 | 471
EVAPORATOR-3 | STEAM | 2004-03-20 | 422
EVAPORATOR-3 | STEAM | 2004-03-21 | 489
EVAPORATOR-3 | STEAM | 2004-03-22 | 256
EVAPORATOR-3 | STEAM | 2004-03-23 | 454
EVAPORATOR-3 | STEAM | 2004-03-24 | 483
EVAPORATOR-3 | STEAM | 2004-03-25 | 496
EVAPORATOR-3 | STEAM | 2004-03-26 | 464
EVAPORATOR-3 | STEAM | 2004-03-27 | 465
EVAPORATOR-3 | STEAM | 2004-03-28 | 407
EVAPORATOR-3 | STEAM | 2004-03-29 | 500
EVAPORATOR-3 | STEAM | 2004-03-30 | 499
EVAPORATOR-3 | STEAM | 2004-03-31 | 497
#VALUE!
EVAPORATOR-3 | STEAM | 2004-04-01 | 328
EVAPORATOR-3 | STEAM | 2004-04-02 | 565
EVAPORATOR-3 | STEAM | 2004-04-03 | 569
EVAPORATOR-3 | STEAM | 2004-04-04 | 547
EVAPORATOR-3 | STEAM | 2004-04-05 | 540
EVAPORATOR-3 | STEAM | 2004-04-06 | 347
EVAPORATOR-3 | STEAM | 2004-04-07 | 484
EVAPORATOR-3 | STEAM | 2004-04-08 | 487
EVAPORATOR-3 | STEAM | 2004-04-09 | 463
EVAPORATOR-3 | STEAM | 2004-04-10 | 443
EVAPORATOR-3 | STEAM | 2004-04-11 | 441
EVAPORATOR-3 | STEAM | 2004-04-12 | 504
EVAPORATOR-3 | STEAM | 2004-04-13 | 445
EVAPORATOR-3 | STEAM | 2004-04-14 | 508
EVAPORATOR-3 | STEAM | 2004-04-15 | 508
EVAPORATOR-3 | STEAM | 2004-04-16 | 492
EVAPORATOR-3 | STEAM | 2004-04-17 | 397
EVAPORATOR-3 | STEAM | 2004-04-18 | 495
EVAPORATOR-3 | STEAM | 2004-04-19 | 494
EVAPORATOR-3 | STEAM | 2004-04-20 | 437
EVAPORATOR-3 | STEAM | 2004-04-21 | 493
EVAPORATOR-3 | STEAM | 2004-04-22 | 448
EVAPORATOR-3 | STEAM | 2004-04-23 | 497
EVAPORATOR-3 | STEAM | 2004-04-24 | 449
EVAPORATOR-3 | STEAM | 2004-04-25 | 489
EVAPORATOR-3 | STEAM | 2004-04-26 | 427
EVAPORATOR-3 | STEAM | 2004-04-27 | 493
EVAPORATOR-3 | STEAM | 2004-04-28 | 496
EVAPORATOR-3 | STEAM | 2004-04-29 | 507
EVAPORATOR-3 | STEAM | 2004-04-30 | 417
#VALUE!
EVAPORATOR-3 | STEAM | 2004-05-01 | 487
EVAPORATOR-3 | STEAM | 2004-05-02 | 490
EVAPORATOR-3 | STEAM | 2004-05-03 | 482
EVAPORATOR-3 | STEAM | 2004-05-04 | 421
EVAPORATOR-3 | STEAM | 2004-05-05 | 503
EVAPORATOR-3 | STEAM | 2004-05-06 | 493
EVAPORATOR-3 | STEAM | 2004-05-07 | 453
EVAPORATOR-3 | STEAM | 2004-05-08 | 491
EVAPORATOR-3 | STEAM | 2004-05-09 | 446
EVAPORATOR-3 | STEAM | 2004-05-10 | 464
EVAPORATOR-3 | STEAM | 2004-05-11 | 481
EVAPORATOR-3 | STEAM | 2004-05-12 | 385
EVAPORATOR-3 | STEAM | 2004-05-13 | 254
EVAPORATOR-3 | STEAM | 2004-05-14 | 504
EVAPORATOR-3 | STEAM | 2004-05-15 | 490
EVAPORATOR-3 | STEAM | 2004-05-16 | 489
EVAPORATOR-3 | STEAM | 2004-05-17 | 448
EVAPORATOR-3 | STEAM | 2004-05-18 | 499
EVAPORATOR-3 | STEAM | 2004-05-19 | 485
EVAPORATOR-3 | STEAM | 2004-05-20 | 477
EVAPORATOR-3 | STEAM | 2004-05-21 | 453
EVAPORATOR-3 | STEAM | 2004-05-22 | 490
EVAPORATOR-3 | STEAM | 2004-05-23 | 485
EVAPORATOR-3 | STEAM | 2004-05-24 | 441
EVAPORATOR-3 | STEAM | 2004-05-25 | 419
EVAPORATOR-3 | STEAM | 2004-05-26 | 448
EVAPORATOR-3 | STEAM | 2004-05-27 | 445
EVAPORATOR-3 | STEAM | 2004-05-28 | 446
EVAPORATOR-3 | STEAM | 2004-05-29 | 453
EVAPORATOR-3 | STEAM | 2004-05-30 | 411
EVAPORATOR-3 | STEAM | 2004-05-31 | 505
14238
EVAPORATOR-3 | STEAM | 2004-06-01 | 520
EVAPORATOR-3 | STEAM | 2004-06-02 | 440
EVAPORATOR-3 | STEAM | 2004-06-03 | 513
EVAPORATOR-3 | STEAM | 2004-06-04 | 500
EVAPORATOR-3 | STEAM | 2004-06-05 | 493
EVAPORATOR-3 | STEAM | 2004-06-06 | 398
EVAPORATOR-3 | STEAM | 2004-06-07 | 539
EVAPORATOR-3 | STEAM | 2004-06-08 | 500
EVAPORATOR-3 | STEAM | 2004-06-09 | 508
EVAPORATOR-3 | STEAM | 2004-06-10 | 517
EVAPORATOR-3 | STEAM | 2004-06-11 | 476
EVAPORATOR-3 | STEAM | 2004-06-12 | 497
EVAPORATOR-3 | STEAM | 2004-06-13 | 511
EVAPORATOR-3 | STEAM | 2004-06-14 | 458
EVAPORATOR-3 | STEAM | 2004-06-15 | 508
EVAPORATOR-3 | STEAM | 2004-06-16 | 217
EVAPORATOR-3 | STEAM | 2004-06-17 | 229
EVAPORATOR-3 | STEAM | 2004-06-18 | 482
EVAPORATOR-3 | STEAM | 2004-06-19 | 493
EVAPORATOR-3 | STEAM | 2004-06-20 | 421
EVAPORATOR-3 | STEAM | 2004-06-21 | 505
EVAPORATOR-3 | STEAM | 2004-06-22 | 457
EVAPORATOR-3 | STEAM | 2004-06-23 | 384
EVAPORATOR-3 | STEAM | 2004-06-24 | 375
EVAPORATOR-3 | STEAM | 2004-06-25 | 484
EVAPORATOR-3 | STEAM | 2004-06-26 | 521
EVAPORATOR-3 | STEAM | 2004-06-27 | 517
EVAPORATOR-3 | STEAM | 2004-06-28 | 410
EVAPORATOR-3 | STEAM | 2004-06-29 | 514
EVAPORATOR-3 | STEAM | 2004-06-30 | 502
13889
EVAPORATOR-3 | STEAM | 2004-07-01 | 412
EVAPORATOR-3 | STEAM | 2004-07-02 | 474
EVAPORATOR-3 | STEAM | 2004-07-03 | 465
EVAPORATOR-3 | STEAM | 2004-07-04 | 499
EVAPORATOR-3 | STEAM | 2004-07-05 | 485
EVAPORATOR-3 | STEAM | 2004-07-06 | 434
EVAPORATOR-3 | STEAM | 2004-07-07 | 466
EVAPORATOR-3 | STEAM | 2004-07-08 | 472
EVAPORATOR-3 | STEAM | 2004-07-09 | 503
EVAPORATOR-3 | STEAM | 2004-07-10 | 433
EVAPORATOR-3 | STEAM | 2004-07-11 | 499
EVAPORATOR-3 | STEAM | 2004-07-12 | 475
EVAPORATOR-3 | STEAM | 2004-07-13 | 284
EVAPORATOR-3 | STEAM | 2004-07-14 | 576
EVAPORATOR-3 | STEAM | 2004-07-15 | 548
EVAPORATOR-3 | STEAM | 2004-07-16 | 444
EVAPORATOR-3 | STEAM | 2004-07-17 | 547
EVAPORATOR-3 | STEAM | 2004-07-18 | 559
EVAPORATOR-3 | STEAM | 2004-07-19 | 461
EVAPORATOR-3 | STEAM | 2004-07-20 | 565
EVAPORATOR-3 | STEAM | 2004-07-21 | 560
EVAPORATOR-3 | STEAM | 2004-07-22 | 556
EVAPORATOR-3 | STEAM | 2004-07-23 | 549
EVAPORATOR-3 | STEAM | 2004-07-24 | 505
EVAPORATOR-3 | STEAM | 2004-07-25 | 533
EVAPORATOR-3 | STEAM | 2004-07-26 | 567
EVAPORATOR-3 | STEAM | 2004-07-27 | 548
EVAPORATOR-3 | STEAM | 2004-07-28 | 577
EVAPORATOR-3 | STEAM | 2004-07-29 | 401
EVAPORATOR-3 | STEAM | 2004-07-30 | 487
EVAPORATOR-3 | STEAM | 2004-07-31 | 421
15305
EVAPORATOR-3 | STEAM | 2004-08-01 | 451
EVAPORATOR-3 | STEAM | 2004-08-02 | 484
EVAPORATOR-3 | STEAM | 2004-08-03 | 430
EVAPORATOR-3 | STEAM | 2004-08-04 | 494
EVAPORATOR-3 | STEAM | 2004-08-05 | 443
EVAPORATOR-3 | STEAM | 2004-08-06 | 304
EVAPORATOR-3 | STEAM | 2004-08-07 | 250
EVAPORATOR-3 | STEAM | 2004-08-08 | 505
EVAPORATOR-3 | STEAM | 2004-08-09 | 412
EVAPORATOR-3 | STEAM | 2004-08-10 | 494
EVAPORATOR-3 | STEAM | 2004-08-11 | 489
EVAPORATOR-3 | STEAM | 2004-08-12 | 495
EVAPORATOR-3 | STEAM | 2004-08-13 | 424
EVAPORATOR-3 | STEAM | 2004-08-14 | 492
EVAPORATOR-3 | STEAM | 2004-08-15 | 479
EVAPORATOR-3 | STEAM | 2004-08-16 | 487
EVAPORATOR-3 | STEAM | 2004-08-17 | 437
EVAPORATOR-3 | STEAM | 2004-08-18 | 459
EVAPORATOR-3 | STEAM | 2004-08-19 | 445
EVAPORATOR-3 | STEAM | 2004-08-20 | 430
EVAPORATOR-3 | STEAM | 2004-08-21 | 397
EVAPORATOR-3 | STEAM | 2004-08-22 | 481
EVAPORATOR-3 | STEAM | 2004-08-23 | 454
EVAPORATOR-3 | STEAM | 2004-08-24 | 491
EVAPORATOR-3 | STEAM | 2004-08-25 | 461
EVAPORATOR-3 | STEAM | 2004-08-26 | 446
EVAPORATOR-3 | STEAM | 2004-08-27 | 406
EVAPORATOR-3 | STEAM | 2004-08-28 | 479
EVAPORATOR-3 | STEAM | 2004-08-29 | 454
EVAPORATOR-3 | STEAM | 2004-08-30 | 355
EVAPORATOR-3 | STEAM | 2004-08-31 | 396
13724
EVAPORATOR-3 | STEAM | 2004-09-01 | 280
EVAPORATOR-3 | STEAM | 2004-09-02 | 0
EVAPORATOR-3 | STEAM | 2004-09-03 | 0
EVAPORATOR-3 | STEAM | 2004-09-04 | 144
EVAPORATOR-3 | STEAM | 2004-09-05 | 514
EVAPORATOR-3 | STEAM | 2004-09-06 | 297
EVAPORATOR-3 | STEAM | 2004-09-07 | 398
EVAPORATOR-3 | STEAM | 2004-09-08 | 493
EVAPORATOR-3 | STEAM | 2004-09-09 | 479
EVAPORATOR-3 | STEAM | 2004-09-10 | 468
EVAPORATOR-3 | STEAM | 2004-09-11 | 495
EVAPORATOR-3 | STEAM | 2004-09-12 | 475
EVAPORATOR-3 | STEAM | 2004-09-13 | 472
EVAPORATOR-3 | STEAM | 2004-09-14 | 480
EVAPORATOR-3 | STEAM | 2004-09-15 | 348
EVAPORATOR-3 | STEAM | 2004-09-16 | 473
EVAPORATOR-3 | STEAM | 2004-09-17 | 521
EVAPORATOR-3 | STEAM | 2004-09-18 | 534
EVAPORATOR-3 | STEAM | 2004-09-19 | 509
EVAPORATOR-3 | STEAM | 2004-09-20 | 416
EVAPORATOR-3 | STEAM | 2004-09-21 | 491
EVAPORATOR-3 | STEAM | 2004-09-22 | 521
EVAPORATOR-3 | STEAM | 2004-09-23 | 512
EVAPORATOR-3 | STEAM | 2004-09-24 | 422
EVAPORATOR-3 | STEAM | 2004-09-25 | 382
EVAPORATOR-3 | STEAM | 2004-09-26 | 515
EVAPORATOR-3 | STEAM | 2004-09-27 | 507
EVAPORATOR-3 | STEAM | 2004-09-28 | 474
EVAPORATOR-3 | STEAM | 2004-09-29 | 440
EVAPORATOR-3 | STEAM | 2004-09-30 | 503
12563
EVAPORATOR-3 | STEAM | 2004-10-01 | 420
EVAPORATOR-3 | STEAM | 2004-10-02 | 489
EVAPORATOR-3 | STEAM | 2004-10-03 | 467
EVAPORATOR-3 | STEAM | 2004-10-04 | 469
EVAPORATOR-3 | STEAM | 2004-10-05 | 482
EVAPORATOR-3 | STEAM | 2004-10-06 | 426
EVAPORATOR-3 | STEAM | 2004-10-07 | 489
EVAPORATOR-3 | STEAM | 2004-10-08 | 460
EVAPORATOR-3 | STEAM | 2004-10-09 | 426
EVAPORATOR-3 | STEAM | 2004-10-10 | 473
EVAPORATOR-3 | STEAM | 2004-10-11 | 488
EVAPORATOR-3 | STEAM | 2004-10-12 | 376
EVAPORATOR-3 | STEAM | 2004-10-13 | 478
EVAPORATOR-3 | STEAM | 2004-10-14 | 405
EVAPORATOR-3 | STEAM | 2004-10-15 | 481
EVAPORATOR-3 | STEAM | 2004-10-16 | 427
EVAPORATOR-3 | STEAM | 2004-10-17 | 447
EVAPORATOR-3 | STEAM | 2004-10-18 | 424
EVAPORATOR-3 | STEAM | 2004-10-19 | 461
EVAPORATOR-3 | STEAM | 2004-10-20 | 509
EVAPORATOR-3 | STEAM | 2004-10-21 | 507
EVAPORATOR-3 | STEAM | 2004-10-22 | 466
EVAPORATOR-3 | STEAM | 2004-10-23 | 401
EVAPORATOR-3 | STEAM | 2004-10-24 | 456
EVAPORATOR-3 | STEAM | 2004-10-25 | 365
EVAPORATOR-3 | STEAM | 2004-10-26 | 486
EVAPORATOR-3 | STEAM | 2004-10-27 | 415
EVAPORATOR-3 | STEAM | 2004-10-28 | 483
EVAPORATOR-3 | STEAM | 2004-10-29 | 491
EVAPORATOR-3 | STEAM | 2004-10-30 | 489
EVAPORATOR-3 | STEAM | 2004-10-31 | 495
14151
EVAPORATOR-3 | STEAM | 2004-11-01 | 491
EVAPORATOR-3 | STEAM | 2004-11-02 | 163
EVAPORATOR-3 | STEAM | 2004-11-03 | 445
EVAPORATOR-3 | STEAM | 2004-11-04 | 476
EVAPORATOR-3 | STEAM | 2004-11-05 | 406
EVAPORATOR-3 | STEAM | 2004-11-06 | 450
EVAPORATOR-3 | STEAM | 2004-11-07 | 473
EVAPORATOR-3 | STEAM | 2004-11-08 | 481
EVAPORATOR-3 | STEAM | 2004-11-09 | 479
EVAPORATOR-3 | STEAM | 2004-11-10 | 468
EVAPORATOR-3 | STEAM | 2004-11-11 | 357
EVAPORATOR-3 | STEAM | 2004-11-12 | 472
EVAPORATOR-3 | STEAM | 2004-11-13 | 470
EVAPORATOR-3 | STEAM | 2004-11-14 | 477
EVAPORATOR-3 | STEAM | 2004-11-15 | 472
EVAPORATOR-3 | STEAM | 2004-11-16 | 433
EVAPORATOR-3 | STEAM | 2004-11-17 | 342
EVAPORATOR-3 | STEAM | 2004-11-18 | 525
EVAPORATOR-3 | STEAM | 2004-11-19 | 520
EVAPORATOR-3 | STEAM | 2004-11-20 | 345
EVAPORATOR-3 | STEAM | 2004-11-21 | 455
EVAPORATOR-3 | STEAM | 2004-11-22 | 459
EVAPORATOR-3 | STEAM | 2004-11-23 | 464
EVAPORATOR-3 | STEAM | 2004-11-24 | 265
EVAPORATOR-3 | STEAM | 2004-11-25 | 471
EVAPORATOR-3 | STEAM | 2004-11-26 | 475
EVAPORATOR-3 | STEAM | 2004-11-27 | 481
EVAPORATOR-3 | STEAM | 2004-11-28 | 472
EVAPORATOR-3 | STEAM | 2004-11-29 | 362
EVAPORATOR-3 | STEAM | 2004-11-30 | 471
13120
EVAPORATOR-3 | STEAM | 2004-12-01 | 467
EVAPORATOR-3 | STEAM | 2004-12-02 | 382
EVAPORATOR-3 | STEAM | 2004-12-03 | 479
EVAPORATOR-3 | STEAM | 2004-12-04 | 471
EVAPORATOR-3 | STEAM | 2004-12-05 | 384
EVAPORATOR-3 | STEAM | 2004-12-06 | 473
EVAPORATOR-3 | STEAM | 2004-12-07 | 355
EVAPORATOR-3 | STEAM | 2004-12-08 | 421
EVAPORATOR-3 | STEAM | 2004-12-09 | 452
EVAPORATOR-3 | STEAM | 2004-12-10 | 471
EVAPORATOR-3 | STEAM | 2004-12-11 | 373
EVAPORATOR-3 | STEAM | 2004-12-12 | 528
EVAPORATOR-3 | STEAM | 2004-12-13 | 531
EVAPORATOR-3 | STEAM | 2004-12-14 | 378
EVAPORATOR-3 | STEAM | 2004-12-15 | 475
EVAPORATOR-3 | STEAM | 2004-12-16 | 473
EVAPORATOR-3 | STEAM | 2004-12-17 | 477
EVAPORATOR-3 | STEAM | 2004-12-18 | 403
EVAPORATOR-3 | STEAM | 2004-12-19 | 480
EVAPORATOR-3 | STEAM | 2004-12-20 | 399
EVAPORATOR-3 | STEAM | 2004-12-21 | 486
EVAPORATOR-3 | STEAM | 2004-12-22 | 492
EVAPORATOR-3 | STEAM | 2004-12-23 | 509
EVAPORATOR-3 | STEAM | 2004-12-24 | 430
EVAPORATOR-3 | STEAM | 2004-12-25 | 492
EVAPORATOR-3 | STEAM | 2004-12-26 | 470
EVAPORATOR-3 | STEAM | 2004-12-27 | 482
EVAPORATOR-3 | STEAM | 2004-12-28 | 477
EVAPORATOR-3 | STEAM | 2004-12-29 | 400
EVAPORATOR-3 | STEAM | 2004-12-30 | 489
EVAPORATOR-3 | STEAM | 2004-12-31 | 488
14087
EVAPORATOR-3 | STEAM | 2005-01-01 | 484
EVAPORATOR-3 | STEAM | 2005-01-02 | 392
EVAPORATOR-3 | STEAM | 2005-01-03 | 486
EVAPORATOR-3 | STEAM | 2005-01-04 | 490
EVAPORATOR-3 | STEAM | 2005-01-05 | 482
EVAPORATOR-3 | STEAM | 2005-01-06 | 482
EVAPORATOR-3 | STEAM | 2005-01-07 | 483
EVAPORATOR-3 | STEAM | 2005-01-08 | 197
EVAPORATOR-3 | STEAM | 2005-01-09 | 487
EVAPORATOR-3 | STEAM | 2005-01-10 | 424
EVAPORATOR-3 | STEAM | 2005-01-11 | 380
EVAPORATOR-3 | STEAM | 2005-01-12 | 488
EVAPORATOR-3 | STEAM | 2005-01-13 | 482
EVAPORATOR-3 | STEAM | 2005-01-14 | 479
EVAPORATOR-3 | STEAM | 2005-01-15 | 483
EVAPORATOR-3 | STEAM | 2005-01-16 | 406
EVAPORATOR-3 | STEAM | 2005-01-17 | 486
EVAPORATOR-3 | STEAM | 2005-01-18 | 489
EVAPORATOR-3 | STEAM | 2005-01-19 | 482
EVAPORATOR-3 | STEAM | 2005-01-20 | 375
EVAPORATOR-3 | STEAM | 2005-01-21 | 433
EVAPORATOR-3 | STEAM | 2005-01-22 | 483
EVAPORATOR-3 | STEAM | 2005-01-23 | 307
EVAPORATOR-3 | STEAM | 2005-01-24 | 392
EVAPORATOR-3 | STEAM | 2005-01-25 | 481
EVAPORATOR-3 | STEAM | 2005-01-26 | 480
EVAPORATOR-3 | STEAM | 2005-01-27 | 432
EVAPORATOR-3 | STEAM | 2005-01-28 | 480
EVAPORATOR-3 | STEAM | 2005-01-29 | 486
EVAPORATOR-3 | STEAM | 2005-01-30 | 484
EVAPORATOR-3 | STEAM | 2005-01-31 | 413
13828
EVAPORATOR-3 | STEAM | 2005-02-01 | 491
EVAPORATOR-3 | STEAM | 2005-02-02 | 413
EVAPORATOR-3 | STEAM | 2005-02-03 | 453
EVAPORATOR-3 | STEAM | 2005-02-04 | 487
EVAPORATOR-3 | STEAM | 2005-02-05 | 491
EVAPORATOR-3 | STEAM | 2005-02-06 | 499
EVAPORATOR-3 | STEAM | 2005-02-07 | 495
EVAPORATOR-3 | STEAM | 2005-02-08 | 500
EVAPORATOR-3 | STEAM | 2005-02-09 | 500
EVAPORATOR-3 | STEAM | 2005-02-10 | 254
EVAPORATOR-3 | STEAM | 2005-02-11 | 153
EVAPORATOR-3 | STEAM | 2005-02-12 | 200
EVAPORATOR-3 | STEAM | 2005-02-13 | 507
EVAPORATOR-3 | STEAM | 2005-02-14 | 490
EVAPORATOR-3 | STEAM | 2005-02-15 | 484
EVAPORATOR-3 | STEAM | 2005-02-16 | 442
EVAPORATOR-3 | STEAM | 2005-02-17 | 389
EVAPORATOR-3 | STEAM | 2005-02-18 | 485
EVAPORATOR-3 | STEAM | 2005-02-19 | 484
EVAPORATOR-3 | STEAM | 2005-02-20 | 486
EVAPORATOR-3 | STEAM | 2005-02-21 | 489
EVAPORATOR-3 | STEAM | 2005-02-22 | 430
EVAPORATOR-3 | STEAM | 2005-02-23 | 232
EVAPORATOR-3 | STEAM | 2005-02-24 | 339
EVAPORATOR-3 | STEAM | 2005-02-25 | 489
EVAPORATOR-3 | STEAM | 2005-02-26 | 446
EVAPORATOR-3 | STEAM | 2005-02-27 | 476
EVAPORATOR-3 | STEAM | 2005-02-28 | 403
12007
EVAPORATOR-3 | STEAM | 2005-03-01 | 470
EVAPORATOR-3 | STEAM | 2005-03-02 | 419
EVAPORATOR-3 | STEAM | 2005-03-03 | 486
EVAPORATOR-3 | STEAM | 2005-03-04 | 481
EVAPORATOR-3 | STEAM | 2005-03-05 | 502
EVAPORATOR-3 | STEAM | 2005-03-06 | 507
EVAPORATOR-3 | STEAM | 2005-03-07 | 495
EVAPORATOR-3 | STEAM | 2005-03-08 | 322
EVAPORATOR-3 | STEAM | 2005-03-09 | 485
EVAPORATOR-3 | STEAM | 2005-03-10 | 558
EVAPORATOR-3 | STEAM | 2005-03-11 | 550
EVAPORATOR-3 | STEAM | 2005-03-12 | 554
EVAPORATOR-3 | STEAM | 2005-03-13 | 549
EVAPORATOR-3 | STEAM | 2005-03-14 | 333
EVAPORATOR-3 | STEAM | 2005-03-15 | 497
EVAPORATOR-3 | STEAM | 2005-03-16 | 497
EVAPORATOR-3 | STEAM | 2005-03-17 | 499
EVAPORATOR-3 | STEAM | 2005-03-18 | 486
EVAPORATOR-3 | STEAM | 2005-03-19 | 430
EVAPORATOR-3 | STEAM | 2005-03-20 | 490
EVAPORATOR-3 | STEAM | 2005-03-21 | 502
EVAPORATOR-3 | STEAM | 2005-03-22 | 499
EVAPORATOR-3 | STEAM | 2005-03-23 | 422
EVAPORATOR-3 | STEAM | 2005-03-24 | 502
EVAPORATOR-3 | STEAM | 2005-03-25 | 490
EVAPORATOR-3 | STEAM | 2005-03-26 | 425
EVAPORATOR-3 | STEAM | 2005-03-27 | 491
EVAPORATOR-3 | STEAM | 2005-03-28 | 502
EVAPORATOR-3 | STEAM | 2005-03-29 | 492
EVAPORATOR-3 | STEAM | 2005-03-30 | 489
EVAPORATOR-3 | STEAM | 2005-03-31 | 422
14846
EVAPORATOR-3 | STEAM | 2005-04-01 | 491
EVAPORATOR-3 | STEAM | 2005-04-02 | 502
EVAPORATOR-3 | STEAM | 2005-04-03 | 484
EVAPORATOR-3 | STEAM | 2005-04-04 | 495
EVAPORATOR-3 | STEAM | 2005-04-05 | 503
EVAPORATOR-3 | STEAM | 2005-04-06 | 500
EVAPORATOR-3 | STEAM | 2005-04-07 | 491
EVAPORATOR-3 | STEAM | 2005-04-08 | 491
EVAPORATOR-3 | STEAM | 2005-04-09 | 431
EVAPORATOR-3 | STEAM | 2005-04-10 | 501
EVAPORATOR-3 | STEAM | 2005-04-11 | 446
EVAPORATOR-3 | STEAM | 2005-04-12 | 490
EVAPORATOR-3 | STEAM | 2005-04-13 | 488
EVAPORATOR-3 | STEAM | 2005-04-14 | 486
EVAPORATOR-3 | STEAM | 2005-04-15 | 493
EVAPORATOR-3 | STEAM | 2005-04-16 | 495
EVAPORATOR-3 | STEAM | 2005-04-17 | 407
EVAPORATOR-3 | STEAM | 2005-04-18 | 482
EVAPORATOR-3 | STEAM | 2005-04-19 | 494
EVAPORATOR-3 | STEAM | 2005-04-20 | 433
EVAPORATOR-3 | STEAM | 2005-04-21 | 498
EVAPORATOR-3 | STEAM | 2005-04-22 | 490
EVAPORATOR-3 | STEAM | 2005-04-23 | 487
EVAPORATOR-3 | STEAM | 2005-04-24 | 491
EVAPORATOR-3 | STEAM | 2005-04-25 | 491
EVAPORATOR-3 | STEAM | 2005-04-26 | 430
EVAPORATOR-3 | STEAM | 2005-04-27 | 493
EVAPORATOR-3 | STEAM | 2005-04-28 | 479
EVAPORATOR-3 | STEAM | 2005-04-29 | 485
EVAPORATOR-3 | STEAM | 2005-04-30 | 490
14437
EVAPORATOR-3 | STEAM | 2005-05-01 | 426
EVAPORATOR-3 | STEAM | 2005-05-02 | 482
EVAPORATOR-3 | STEAM | 2005-05-03 | 468
EVAPORATOR-3 | STEAM | 2005-05-04 | 409
EVAPORATOR-3 | STEAM | 2005-05-05 | 492
EVAPORATOR-3 | STEAM | 2005-05-06 | 419
EVAPORATOR-3 | STEAM | 2005-05-07 | 398
EVAPORATOR-3 | STEAM | 2005-05-08 | 458
EVAPORATOR-3 | STEAM | 2005-05-09 | 128
EVAPORATOR-3 | STEAM | 2005-05-10 | 569
EVAPORATOR-3 | STEAM | 2005-05-11 | 508
EVAPORATOR-3 | STEAM | 2005-05-12 | 523
EVAPORATOR-3 | STEAM | 2005-05-13 | 498
EVAPORATOR-3 | STEAM | 2005-05-14 | 566
EVAPORATOR-3 | STEAM | 2005-05-15 | 570
EVAPORATOR-3 | STEAM | 2005-05-16 | 567
EVAPORATOR-3 | STEAM | 2005-05-17 | 573
EVAPORATOR-3 | STEAM | 2005-05-18 | 366
EVAPORATOR-3 | STEAM | 2005-05-19 | 498
EVAPORATOR-3 | STEAM | 2005-05-20 | 487
EVAPORATOR-3 | STEAM | 2005-05-21 | 505
EVAPORATOR-3 | STEAM | 2005-05-22 | 507
EVAPORATOR-3 | STEAM | 2005-05-23 | 495
EVAPORATOR-3 | STEAM | 2005-05-24 | 494
EVAPORATOR-3 | STEAM | 2005-05-25 | 493
EVAPORATOR-3 | STEAM | 2005-05-26 | 496
EVAPORATOR-3 | STEAM | 2005-05-27 | 510
EVAPORATOR-3 | STEAM | 2005-05-28 | 434
EVAPORATOR-3 | STEAM | 2005-05-29 | 497
EVAPORATOR-3 | STEAM | 2005-05-30 | 487
EVAPORATOR-3 | STEAM | 2005-05-31 | 474
14797
EVAPORATOR-3 | STEAM | 2005-06-01 | 496
EVAPORATOR-3 | STEAM | 2005-06-02 | 501
EVAPORATOR-3 | STEAM | 2005-06-03 | 466
EVAPORATOR-3 | STEAM | 2005-06-04 | 572
EVAPORATOR-3 | STEAM | 2005-06-05 | 552
EVAPORATOR-3 | STEAM | 2005-06-06 | 428
EVAPORATOR-3 | STEAM | 2005-06-07 | 592
EVAPORATOR-3 | STEAM | 2005-06-08 | 596
EVAPORATOR-3 | STEAM | 2005-06-09 | 407
EVAPORATOR-3 | STEAM | 2005-06-10 | 497
EVAPORATOR-3 | STEAM | 2005-06-11 | 491
EVAPORATOR-3 | STEAM | 2005-06-12 | 501
EVAPORATOR-3 | STEAM | 2005-06-13 | 425
EVAPORATOR-3 | STEAM | 2005-06-14 | 500
EVAPORATOR-3 | STEAM | 2005-06-15 | 477
EVAPORATOR-3 | STEAM | 2005-06-16 | 467
EVAPORATOR-3 | STEAM | 2005-06-17 | 515
EVAPORATOR-3 | STEAM | 2005-06-18 | 509
EVAPORATOR-3 | STEAM | 2005-06-19 | 503
EVAPORATOR-3 | STEAM | 2005-06-20 | 511
EVAPORATOR-3 | STEAM | 2005-06-21 | 419
EVAPORATOR-3 | STEAM | 2005-06-22 | 576
EVAPORATOR-3 | STEAM | 2005-06-23 | 584
EVAPORATOR-3 | STEAM | 2005-06-24 | 578
EVAPORATOR-3 | STEAM | 2005-06-25 | 594
EVAPORATOR-3 | STEAM | 2005-06-26 | 602
EVAPORATOR-3 | STEAM | 2005-06-27 | 604
EVAPORATOR-3 | STEAM | 2005-06-28 | 587
EVAPORATOR-3 | STEAM | 2005-06-29 | 584
EVAPORATOR-3 | STEAM | 2005-06-30 | 260
15394
EVAPORATOR-3 | STEAM | 2005-07-01 | 515
EVAPORATOR-3 | STEAM | 2005-07-02 | 443
EVAPORATOR-3 | STEAM | 2005-07-03 | 480
EVAPORATOR-3 | STEAM | 2005-07-04 | 498
EVAPORATOR-3 | STEAM | 2005-07-05 | 434
EVAPORATOR-3 | STEAM | 2005-07-06 | 502
EVAPORATOR-3 | STEAM | 2005-07-07 | 515
EVAPORATOR-3 | STEAM | 2005-07-08 | 433
EVAPORATOR-3 | STEAM | 2005-07-09 | 517
EVAPORATOR-3 | STEAM | 2005-07-10 | 506
EVAPORATOR-3 | STEAM | 2005-07-11 | 498
EVAPORATOR-3 | STEAM | 2005-07-12 | 498
EVAPORATOR-3 | STEAM | 2005-07-13 | 486
EVAPORATOR-3 | STEAM | 2005-07-14 | 433
EVAPORATOR-3 | STEAM | 2005-07-15 | 502
EVAPORATOR-3 | STEAM | 2005-07-16 | 501
EVAPORATOR-3 | STEAM | 2005-07-17 | 505
EVAPORATOR-3 | STEAM | 2005-07-18 | 431
EVAPORATOR-3 | STEAM | 2005-07-19 | 377
EVAPORATOR-3 | STEAM | 2005-07-20 | 503
EVAPORATOR-3 | STEAM | 2005-07-21 | 500
EVAPORATOR-3 | STEAM | 2005-07-22 | 502
EVAPORATOR-3 | STEAM | 2005-07-23 | 507
EVAPORATOR-3 | STEAM | 2005-07-24 | 530
EVAPORATOR-3 | STEAM | 2005-07-25 | 450
EVAPORATOR-3 | STEAM | 2005-07-26 | 512
EVAPORATOR-3 | STEAM | 2005-07-27 | 488
EVAPORATOR-3 | STEAM | 2005-07-28 | 417
EVAPORATOR-3 | STEAM | 2005-07-29 | 502
EVAPORATOR-3 | STEAM | 2005-07-30 | 502
EVAPORATOR-3 | STEAM | 2005-07-31 | 230
14717
EVAPORATOR-3 | STEAM | 2005-08-01 | 370
EVAPORATOR-3 | STEAM | 2005-08-02 | 469
EVAPORATOR-3 | STEAM | 2005-08-03 | 364
EVAPORATOR-3 | STEAM | 2005-08-04 | 505
EVAPORATOR-3 | STEAM | 2005-08-05 | 509
EVAPORATOR-3 | STEAM | 2005-08-06 | 346
EVAPORATOR-3 | STEAM | 2005-08-07 | 504
EVAPORATOR-3 | STEAM | 2005-08-08 | 445
EVAPORATOR-3 | STEAM | 2005-08-09 | 497
EVAPORATOR-3 | STEAM | 2005-08-10 | 492
EVAPORATOR-3 | STEAM | 2005-08-11 | 429
EVAPORATOR-3 | STEAM | 2005-08-12 | 496
EVAPORATOR-3 | STEAM | 2005-08-13 | 499
EVAPORATOR-3 | STEAM | 2005-08-14 | 503
EVAPORATOR-3 | STEAM | 2005-08-15 | 502
EVAPORATOR-3 | STEAM | 2005-08-16 | 435
EVAPORATOR-3 | STEAM | 2005-08-17 | 498
EVAPORATOR-3 | STEAM | 2005-08-18 | 496
EVAPORATOR-3 | STEAM | 2005-08-19 | 496
EVAPORATOR-3 | STEAM | 2005-08-20 | 493
EVAPORATOR-3 | STEAM | 2005-08-21 | 493
EVAPORATOR-3 | STEAM | 2005-08-22 | 427
EVAPORATOR-3 | STEAM | 2005-08-23 | 474
EVAPORATOR-3 | STEAM | 2005-08-24 | 150
EVAPORATOR-3 | STEAM | 2005-08-25 | 544
EVAPORATOR-3 | STEAM | 2005-08-26 | 535
EVAPORATOR-3 | STEAM | 2005-08-27 | 528
EVAPORATOR-3 | STEAM | 2005-08-28 | 477
EVAPORATOR-3 | STEAM | 2005-08-29 | 531
EVAPORATOR-3 | STEAM | 2005-08-30 | 528
EVAPORATOR-3 | STEAM | 2005-08-31 | 414
14449
EVAPORATOR-3 | STEAM | 2005-09-01 | 446
EVAPORATOR-3 | STEAM | 2005-09-02 | 321
EVAPORATOR-3 | STEAM | 2005-09-03 | 480
EVAPORATOR-3 | STEAM | 2005-09-04 | 484
EVAPORATOR-3 | STEAM | 2005-09-05 | 402
EVAPORATOR-3 | STEAM | 2005-09-06 | 470
EVAPORATOR-3 | STEAM | 2005-09-07 | 513
EVAPORATOR-3 | STEAM | 2005-09-08 | 531
EVAPORATOR-3 | STEAM | 2005-09-09 | 423
EVAPORATOR-3 | STEAM | 2005-09-10 | 507
EVAPORATOR-3 | STEAM | 2005-09-11 | 509
EVAPORATOR-3 | STEAM | 2005-09-12 | 468
EVAPORATOR-3 | STEAM | 2005-09-13 | 524
EVAPORATOR-3 | STEAM | 2005-09-14 | 458
EVAPORATOR-3 | STEAM | 2005-09-15 | 510
EVAPORATOR-3 | STEAM | 2005-09-16 | 488
EVAPORATOR-3 | STEAM | 2005-09-17 | 493
EVAPORATOR-3 | STEAM | 2005-09-18 | 482
EVAPORATOR-3 | STEAM | 2005-09-19 | 530
EVAPORATOR-3 | STEAM | 2005-09-20 | 535
EVAPORATOR-3 | STEAM | 2005-09-21 | 576
EVAPORATOR-3 | STEAM | 2005-09-22 | 577
EVAPORATOR-3 | STEAM | 2005-09-23 | 486
EVAPORATOR-3 | STEAM | 2005-09-24 | 579
EVAPORATOR-3 | STEAM | 2005-09-25 | 577
EVAPORATOR-3 | STEAM | 2005-09-26 | 562
EVAPORATOR-3 | STEAM | 2005-09-27 | 498
EVAPORATOR-3 | STEAM | 2005-09-28 | 557
EVAPORATOR-3 | STEAM | 2005-09-29 | 491
EVAPORATOR-3 | STEAM | 2005-09-30 | 560
15037
EVAPORATOR-3 | STEAM | 2005-10-01 | 551
EVAPORATOR-3 | STEAM | 2005-10-02 | 21
EVAPORATOR-3 | STEAM | 2005-10-03 | 0
EVAPORATOR-3 | STEAM | 2005-10-04 | 0
EVAPORATOR-3 | STEAM | 2005-10-05 | 303
EVAPORATOR-3 | STEAM | 2005-10-06 | 571
EVAPORATOR-3 | STEAM | 2005-10-07 | 559
EVAPORATOR-3 | STEAM | 2005-10-08 | 560
EVAPORATOR-3 | STEAM | 2005-10-09 | 469
EVAPORATOR-3 | STEAM | 2005-10-10 | 488
EVAPORATOR-3 | STEAM | 2005-10-11 | 560
EVAPORATOR-3 | STEAM | 2005-10-12 | 556
EVAPORATOR-3 | STEAM | 2005-10-13 | 458
EVAPORATOR-3 | STEAM | 2005-10-14 | 565
EVAPORATOR-3 | STEAM | 2005-10-15 | 562
EVAPORATOR-3 | STEAM | 2005-10-16 | 566
EVAPORATOR-3 | STEAM | 2005-10-17 | 491
EVAPORATOR-3 | STEAM | 2005-10-18 | 524
EVAPORATOR-3 | STEAM | 2005-10-19 | 567
EVAPORATOR-3 | STEAM | 2005-10-20 | 449
EVAPORATOR-3 | STEAM | 2005-10-21 | 571
EVAPORATOR-3 | STEAM | 2005-10-22 | 407
EVAPORATOR-3 | STEAM | 2005-10-23 | 559
EVAPORATOR-3 | STEAM | 2005-10-24 | 431
EVAPORATOR-3 | STEAM | 2005-10-25 | 400
EVAPORATOR-3 | STEAM | 2005-10-26 | 601
EVAPORATOR-3 | STEAM | 2005-10-27 | 579
EVAPORATOR-3 | STEAM | 2005-10-28 | 562
EVAPORATOR-3 | STEAM | 2005-10-29 | 483
EVAPORATOR-3 | STEAM | 2005-10-30 | 562
EVAPORATOR-3 | STEAM | 2005-10-31 | 430
14405
EVAPORATOR-3 | STEAM | 2005-11-01 | 565
EVAPORATOR-3 | STEAM | 2005-11-02 | 569
EVAPORATOR-3 | STEAM | 2005-11-03 | 522
EVAPORATOR-3 | STEAM | 2005-11-04 | 511
EVAPORATOR-3 | STEAM | 2005-11-05 | 570
EVAPORATOR-3 | STEAM | 2005-11-06 | 355
EVAPORATOR-3 | STEAM | 2005-11-07 | 558
EVAPORATOR-3 | STEAM | 2005-11-08 | 450
EVAPORATOR-3 | STEAM | 2005-11-09 | 565
EVAPORATOR-3 | STEAM | 2005-11-10 | 565
EVAPORATOR-3 | STEAM | 2005-11-11 | 477
EVAPORATOR-3 | STEAM | 2005-11-12 | 524
EVAPORATOR-3 | STEAM | 2005-11-13 | 554
EVAPORATOR-3 | STEAM | 2005-11-14 | 522
EVAPORATOR-3 | STEAM | 2005-11-15 | 516
EVAPORATOR-3 | STEAM | 2005-11-16 | 390
EVAPORATOR-3 | STEAM | 2005-11-17 | 362
EVAPORATOR-3 | STEAM | 2005-11-18 | 408
EVAPORATOR-3 | STEAM | 2005-11-19 | 492
EVAPORATOR-3 | STEAM | 2005-11-20 | 482
EVAPORATOR-3 | STEAM | 2005-11-21 | 403
EVAPORATOR-3 | STEAM | 2005-11-22 | 215
EVAPORATOR-3 | STEAM | 2005-11-23 | 489
EVAPORATOR-3 | STEAM | 2005-11-24 | 488
EVAPORATOR-3 | STEAM | 2005-11-25 | 433
EVAPORATOR-3 | STEAM | 2005-11-26 | 484
EVAPORATOR-3 | STEAM | 2005-11-27 | 470
EVAPORATOR-3 | STEAM | 2005-11-28 | 437
EVAPORATOR-3 | STEAM | 2005-11-29 | 480
EVAPORATOR-3 | STEAM | 2005-11-30 | 498
14354
EVAPORATOR-3 | STEAM | 2005-12-01 | 491
EVAPORATOR-3 | STEAM | 2005-12-02 | 420
EVAPORATOR-3 | STEAM | 2005-12-03 | 487
EVAPORATOR-3 | STEAM | 2005-12-04 | 482
EVAPORATOR-3 | STEAM | 2005-12-05 | 482
EVAPORATOR-3 | STEAM | 2005-12-06 | 495
EVAPORATOR-3 | STEAM | 2005-12-07 | 483
EVAPORATOR-3 | STEAM | 2005-12-08 | 496
EVAPORATOR-3 | STEAM | 2005-12-09 | 488
EVAPORATOR-3 | STEAM | 2005-12-10 | 497
EVAPORATOR-3 | STEAM | 2005-12-11 | 449
EVAPORATOR-3 | STEAM | 2005-12-12 | 518
EVAPORATOR-3 | STEAM | 2005-12-13 | 500
EVAPORATOR-3 | STEAM | 2005-12-14 | 492
EVAPORATOR-3 | STEAM | 2005-12-15 | 500
EVAPORATOR-3 | STEAM | 2005-12-16 | 401
EVAPORATOR-3 | STEAM | 2005-12-17 | 492
EVAPORATOR-3 | STEAM | 2005-12-18 | 476
EVAPORATOR-3 | STEAM | 2005-12-19 | 496
EVAPORATOR-3 | STEAM | 2005-12-20 | 401
EVAPORATOR-3 | STEAM | 2005-12-21 | 479
EVAPORATOR-3 | STEAM | 2005-12-22 | 469
EVAPORATOR-3 | STEAM | 2005-12-23 | 482
EVAPORATOR-3 | STEAM | 2005-12-24 | 478
EVAPORATOR-3 | STEAM | 2005-12-25 | 429
EVAPORATOR-3 | STEAM | 2005-12-26 | 519
EVAPORATOR-3 | STEAM | 2005-12-27 | 514
EVAPORATOR-3 | STEAM | 2005-12-28 | 525
EVAPORATOR-3 | STEAM | 2005-12-29 | 497
EVAPORATOR-3 | STEAM | 2005-12-30 | 489
EVAPORATOR-3 | STEAM | 2005-12-31 | 492
14919
EVAPORATOR-3 | STEAM | 2006-01-01 | 494
EVAPORATOR-3 | STEAM | 2006-01-02 | 517
EVAPORATOR-3 | STEAM | 2006-01-03 | 429
EVAPORATOR-3 | STEAM | 2006-01-04 | 493
EVAPORATOR-3 | STEAM | 2006-01-05 | 430
EVAPORATOR-3 | STEAM | 2006-01-06 | 446
EVAPORATOR-3 | STEAM | 2006-01-07 | 301
EVAPORATOR-3 | STEAM | 2006-01-08 | 394
EVAPORATOR-3 | STEAM | 2006-01-09 | 476
EVAPORATOR-3 | STEAM | 2006-01-10 | 487
EVAPORATOR-3 | STEAM | 2006-01-11 | 490
EVAPORATOR-3 | STEAM | 2006-01-12 | 502
EVAPORATOR-3 | STEAM | 2006-01-13 | 485
EVAPORATOR-3 | STEAM | 2006-01-14 | 476
EVAPORATOR-3 | STEAM | 2006-01-15 | 479
EVAPORATOR-3 | STEAM | 2006-01-16 | 476
EVAPORATOR-3 | STEAM | 2006-01-17 | 475
EVAPORATOR-3 | STEAM | 2006-01-18 | 469
EVAPORATOR-3 | STEAM | 2006-01-19 | 474
EVAPORATOR-3 | STEAM | 2006-01-20 | 477
EVAPORATOR-3 | STEAM | 2006-01-21 | 361
EVAPORATOR-3 | STEAM | 2006-01-22 | 480
EVAPORATOR-3 | STEAM | 2006-01-23 | 482
EVAPORATOR-3 | STEAM | 2006-01-24 | 486
EVAPORATOR-3 | STEAM | 2006-01-25 | 266
EVAPORATOR-3 | STEAM | 2006-01-26 | 507
EVAPORATOR-3 | STEAM | 2006-01-27 | 510
EVAPORATOR-3 | STEAM | 2006-01-28 | 490
EVAPORATOR-3 | STEAM | 2006-01-29 | 487
EVAPORATOR-3 | STEAM | 2006-01-30 | 497
EVAPORATOR-3 | STEAM | 2006-01-31 | 485
14321
EVAPORATOR-3 | STEAM | 2006-02-01 | 477
EVAPORATOR-3 | STEAM | 2006-02-02 | 473
EVAPORATOR-3 | STEAM | 2006-02-03 | 482
EVAPORATOR-3 | STEAM | 2006-02-04 | 490
EVAPORATOR-3 | STEAM | 2006-02-05 | 486
EVAPORATOR-3 | STEAM | 2006-02-06 | 477
EVAPORATOR-3 | STEAM | 2006-02-07 | 475
EVAPORATOR-3 | STEAM | 2006-02-08 | 487
EVAPORATOR-3 | STEAM | 2006-02-09 | 486
EVAPORATOR-3 | STEAM | 2006-02-10 | 348
EVAPORATOR-3 | STEAM | 2006-02-11 | 555
EVAPORATOR-3 | STEAM | 2006-02-12 | 563
EVAPORATOR-3 | STEAM | 2006-02-13 | 583
EVAPORATOR-3 | STEAM | 2006-02-14 | 559
EVAPORATOR-3 | STEAM | 2006-02-15 | 553
EVAPORATOR-3 | STEAM | 2006-02-16 | 554
EVAPORATOR-3 | STEAM | 2006-02-17 | 545
EVAPORATOR-3 | STEAM | 2006-02-18 | 541
EVAPORATOR-3 | STEAM | 2006-02-19 | 540
EVAPORATOR-3 | STEAM | 2006-02-20 | 468
EVAPORATOR-3 | STEAM | 2006-02-21 | 558
EVAPORATOR-3 | STEAM | 2006-02-22 | 551
EVAPORATOR-3 | STEAM | 2006-02-23 | 537
EVAPORATOR-3 | STEAM | 2006-02-24 | 537
EVAPORATOR-3 | STEAM | 2006-02-25 | 536
EVAPORATOR-3 | STEAM | 2006-02-26 | 526
EVAPORATOR-3 | STEAM | 2006-02-27 | 526
EVAPORATOR-3 | STEAM | 2006-02-28 | 463
14376
EVAPORATOR-3 | STEAM | 2006-03-01 | 537
EVAPORATOR-3 | STEAM | 2006-03-02 | 547
EVAPORATOR-3 | STEAM | 2006-03-03 | 546
EVAPORATOR-3 | STEAM | 2006-03-04 | 542
EVAPORATOR-3 | STEAM | 2006-03-05 | 562
EVAPORATOR-3 | STEAM | 2006-03-06 | 560
EVAPORATOR-3 | STEAM | 2006-03-07 | 595
EVAPORATOR-3 | STEAM | 2006-03-08 | 509
EVAPORATOR-3 | STEAM | 2006-03-09 | 443
EVAPORATOR-3 | STEAM | 2006-03-10 | 552
EVAPORATOR-3 | STEAM | 2006-03-11 | 551
EVAPORATOR-3 | STEAM | 2006-03-12 | 499
EVAPORATOR-3 | STEAM | 2006-03-13 | 474
EVAPORATOR-3 | STEAM | 2006-03-14 | 558
EVAPORATOR-3 | STEAM | 2006-03-15 | 545
EVAPORATOR-3 | STEAM | 2006-03-16 | 547
EVAPORATOR-3 | STEAM | 2006-03-17 | 479
EVAPORATOR-3 | STEAM | 2006-03-18 | 517
EVAPORATOR-3 | STEAM | 2006-03-19 | 539
EVAPORATOR-3 | STEAM | 2006-03-20 | 535
EVAPORATOR-3 | STEAM | 2006-03-21 | 524
EVAPORATOR-3 | STEAM | 2006-03-22 | 539
EVAPORATOR-3 | STEAM | 2006-03-23 | 553
EVAPORATOR-3 | STEAM | 2006-03-24 | 528
EVAPORATOR-3 | STEAM | 2006-03-25 | 441
EVAPORATOR-3 | STEAM | 2006-03-26 | 542
EVAPORATOR-3 | STEAM | 2006-03-27 | 533
EVAPORATOR-3 | STEAM | 2006-03-28 | 557
EVAPORATOR-3 | STEAM | 2006-03-29 | 464
EVAPORATOR-3 | STEAM | 2006-03-30 | 571
EVAPORATOR-3 | STEAM | 2006-03-31 | 549
16438
EVAPORATOR-3 | STEAM | 2006-04-01 | 530
EVAPORATOR-3 | STEAM | 2006-04-02 | 547
EVAPORATOR-3 | STEAM | 2006-04-03 | 549
EVAPORATOR-3 | STEAM | 2006-04-04 | 307
EVAPORATOR-3 | STEAM | 2006-04-05 | 1
EVAPORATOR-3 | STEAM | 2006-04-06 | 0
EVAPORATOR-3 | STEAM | 2006-04-07 | 0
EVAPORATOR-3 | STEAM | 2006-04-08 | 0
EVAPORATOR-3 | STEAM | 2006-04-09 | 0
EVAPORATOR-3 | STEAM | 2006-04-10 | 537
EVAPORATOR-3 | STEAM | 2006-04-11 | 556
EVAPORATOR-3 | STEAM | 2006-04-12 | 499
EVAPORATOR-3 | STEAM | 2006-04-13 | 528
EVAPORATOR-3 | STEAM | 2006-04-14 | 530
EVAPORATOR-3 | STEAM | 2006-04-15 | 501
EVAPORATOR-3 | STEAM | 2006-04-16 | 501
EVAPORATOR-3 | STEAM | 2006-04-17 | 556
EVAPORATOR-3 | STEAM | 2006-04-18 | 559
EVAPORATOR-3 | STEAM | 2006-04-19 | 541
EVAPORATOR-3 | STEAM | 2006-04-20 | 546
EVAPORATOR-3 | STEAM | 2006-04-21 | 530
EVAPORATOR-3 | STEAM | 2006-04-22 | 537
EVAPORATOR-3 | STEAM | 2006-04-23 | 456
EVAPORATOR-3 | STEAM | 2006-04-24 | 530
EVAPORATOR-3 | STEAM | 2006-04-25 | 539
EVAPORATOR-3 | STEAM | 2006-04-26 | 533
EVAPORATOR-3 | STEAM | 2006-04-27 | 526
EVAPORATOR-3 | STEAM | 2006-04-28 | 523
EVAPORATOR-3 | STEAM | 2006-04-29 | 524
EVAPORATOR-3 | STEAM | 2006-04-30 | 524
13010
EVAPORATOR-3 | STEAM | 2006-05-01 | 529
EVAPORATOR-3 | STEAM | 2006-05-02 | 529
EVAPORATOR-3 | STEAM | 2006-05-03 | 532
EVAPORATOR-3 | STEAM | 2006-05-04 | 528
EVAPORATOR-3 | STEAM | 2006-05-05 | 534
EVAPORATOR-3 | STEAM | 2006-05-06 | 197
EVAPORATOR-3 | STEAM | 2006-05-07 | 566
EVAPORATOR-3 | STEAM | 2006-05-08 | 546
EVAPORATOR-3 | STEAM | 2006-05-09 | 285
EVAPORATOR-3 | STEAM | 2006-05-10 | 519
EVAPORATOR-3 | STEAM | 2006-05-11 | 535
EVAPORATOR-3 | STEAM | 2006-05-12 | 522
EVAPORATOR-3 | STEAM | 2006-05-13 | 509
EVAPORATOR-3 | STEAM | 2006-05-14 | 491
EVAPORATOR-3 | STEAM | 2006-05-15 | 526
EVAPORATOR-3 | STEAM | 2006-05-16 | 528
EVAPORATOR-3 | STEAM | 2006-05-17 | 441
EVAPORATOR-3 | STEAM | 2006-05-18 | 437
EVAPORATOR-3 | STEAM | 2006-05-19 | 526
EVAPORATOR-3 | STEAM | 2006-05-20 | 506
EVAPORATOR-3 | STEAM | 2006-05-21 | 513
EVAPORATOR-3 | STEAM | 2006-05-22 | 490
EVAPORATOR-3 | STEAM | 2006-05-23 | 489
EVAPORATOR-3 | STEAM | 2006-05-24 | 488
EVAPORATOR-3 | STEAM | 2006-05-25 | 491
EVAPORATOR-3 | STEAM | 2006-05-26 | 420
EVAPORATOR-3 | STEAM | 2006-05-27 | 504
EVAPORATOR-3 | STEAM | 2006-05-28 | 511
EVAPORATOR-3 | STEAM | 2006-05-29 | 502
EVAPORATOR-3 | STEAM | 2006-05-30 | 504
EVAPORATOR-3 | STEAM | 2006-05-31 | 502
15200
EVAPORATOR-3 | STEAM | 2006-06-01 | 495
EVAPORATOR-3 | STEAM | 2006-06-02 | 353
EVAPORATOR-3 | STEAM | 2006-06-03 | 491
EVAPORATOR-3 | STEAM | 2006-06-04 | 480
EVAPORATOR-3 | STEAM | 2006-06-05 | 463
EVAPORATOR-3 | STEAM | 2006-06-06 | 467
EVAPORATOR-3 | STEAM | 2006-06-07 | 464
EVAPORATOR-3 | STEAM | 2006-06-08 | 474
EVAPORATOR-3 | STEAM | 2006-06-09 | 471
EVAPORATOR-3 | STEAM | 2006-06-10 | 379
EVAPORATOR-3 | STEAM | 2006-06-11 | 497
EVAPORATOR-3 | STEAM | 2006-06-12 | 482
EVAPORATOR-3 | STEAM | 2006-06-13 | 487
EVAPORATOR-3 | STEAM | 2006-06-14 | 497
EVAPORATOR-3 | STEAM | 2006-06-15 | 506
EVAPORATOR-3 | STEAM | 2006-06-16 | 496
EVAPORATOR-3 | STEAM | 2006-06-17 | 492
EVAPORATOR-3 | STEAM | 2006-06-18 | 477
EVAPORATOR-3 | STEAM | 2006-06-19 | 472
EVAPORATOR-3 | STEAM | 2006-06-20 | 473
EVAPORATOR-3 | STEAM | 2006-06-21 | 487
EVAPORATOR-3 | STEAM | 2006-06-22 | 483
EVAPORATOR-3 | STEAM | 2006-06-23 | 489
EVAPORATOR-3 | STEAM | 2006-06-24 | 297
EVAPORATOR-3 | STEAM | 2006-06-25 | 441
EVAPORATOR-3 | STEAM | 2006-06-26 | 591
EVAPORATOR-3 | STEAM | 2006-06-27 | 561
EVAPORATOR-3 | STEAM | 2006-06-28 | 539
EVAPORATOR-3 | STEAM | 2006-06-29 | 476
EVAPORATOR-3 | STEAM | 2006-06-30 | 560
14340
EVAPORATOR-3 | STEAM | 2006-07-01 | 559
EVAPORATOR-3 | STEAM | 2006-07-02 | 547
EVAPORATOR-3 | STEAM | 2006-07-03 | 417
EVAPORATOR-3 | STEAM | 2006-07-04 | 515
EVAPORATOR-3 | STEAM | 2006-07-05 | 483
EVAPORATOR-3 | STEAM | 2006-07-06 | 479
EVAPORATOR-3 | STEAM | 2006-07-07 | 260
EVAPORATOR-3 | STEAM | 2006-07-08 | 505
EVAPORATOR-3 | STEAM | 2006-07-09 | 497
EVAPORATOR-3 | STEAM | 2006-07-10 | 521
EVAPORATOR-3 | STEAM | 2006-07-11 | 527
EVAPORATOR-3 | STEAM | 2006-07-12 | 505
EVAPORATOR-3 | STEAM | 2006-07-13 | 437
EVAPORATOR-3 | STEAM | 2006-07-14 | 525
EVAPORATOR-3 | STEAM | 2006-07-15 | 528
EVAPORATOR-3 | STEAM | 2006-07-16 | 482
EVAPORATOR-3 | STEAM | 2006-07-17 | 408
EVAPORATOR-3 | STEAM | 2006-07-18 | 482
EVAPORATOR-3 | STEAM | 2006-07-19 | 475
EVAPORATOR-3 | STEAM | 2006-07-20 | 488
EVAPORATOR-3 | STEAM | 2006-07-21 | 481
EVAPORATOR-3 | STEAM | 2006-07-22 | 442
EVAPORATOR-3 | STEAM | 2006-07-23 | 504
EVAPORATOR-3 | STEAM | 2006-07-24 | 483
EVAPORATOR-3 | STEAM | 2006-07-25 | 418
EVAPORATOR-3 | STEAM | 2006-07-26 | 479
EVAPORATOR-3 | STEAM | 2006-07-27 | 409
EVAPORATOR-3 | STEAM | 2006-07-28 | 462
EVAPORATOR-3 | STEAM | 2006-07-29 | 506
EVAPORATOR-3 | STEAM | 2006-07-30 | 474
EVAPORATOR-3 | STEAM | 2006-07-31 | 442
14740
EVAPORATOR-3 | STEAM | 2006-08-01 | 472
EVAPORATOR-3 | STEAM | 2006-08-02 | 496
EVAPORATOR-3 | STEAM | 2006-08-03 | 505
EVAPORATOR-3 | STEAM | 2006-08-04 | 447
EVAPORATOR-3 | STEAM | 2006-08-05 | 388
EVAPORATOR-3 | STEAM | 2006-08-06 | 0
EVAPORATOR-3 | STEAM | 2006-08-07 | 31
EVAPORATOR-3 | STEAM | 2006-08-08 | 534
EVAPORATOR-3 | STEAM | 2006-08-09 | 504
EVAPORATOR-3 | STEAM | 2006-08-10 | 512
EVAPORATOR-3 | STEAM | 2006-08-11 | 484
EVAPORATOR-3 | STEAM | 2006-08-12 | 377
EVAPORATOR-3 | STEAM | 2006-08-13 | 471
EVAPORATOR-3 | STEAM | 2006-08-14 | 419
EVAPORATOR-3 | STEAM | 2006-08-15 | 475
EVAPORATOR-3 | STEAM | 2006-08-16 | 467
EVAPORATOR-3 | STEAM | 2006-08-17 | 473
EVAPORATOR-3 | STEAM | 2006-08-18 | 488
EVAPORATOR-3 | STEAM | 2006-08-19 | 483
EVAPORATOR-3 | STEAM | 2006-08-20 | 479
EVAPORATOR-3 | STEAM | 2006-08-21 | 428
EVAPORATOR-3 | STEAM | 2006-08-22 | 479
EVAPORATOR-3 | STEAM | 2006-08-23 | 462
EVAPORATOR-3 | STEAM | 2006-08-24 | 379
EVAPORATOR-3 | STEAM | 2006-08-25 | 467
EVAPORATOR-3 | STEAM | 2006-08-26 | 472
EVAPORATOR-3 | STEAM | 2006-08-27 | 463
EVAPORATOR-3 | STEAM | 2006-08-28 | 385
EVAPORATOR-3 | STEAM | 2006-08-29 | 465
EVAPORATOR-3 | STEAM | 2006-08-30 | 394
EVAPORATOR-3 | STEAM | 2006-08-31 | 284
13183
EVAPORATOR-3 | STEAM | 2006-09-01 | 392
EVAPORATOR-3 | STEAM | 2006-09-02 | 411
EVAPORATOR-3 | STEAM | 2006-09-03 | 355
EVAPORATOR-3 | STEAM | 2006-09-04 | 395
EVAPORATOR-3 | STEAM | 2006-09-05 | 399
EVAPORATOR-3 | STEAM | 2006-09-06 | 461
EVAPORATOR-3 | STEAM | 2006-09-07 | 386
EVAPORATOR-3 | STEAM | 2006-09-08 | 488
EVAPORATOR-3 | STEAM | 2006-09-09 | 475
EVAPORATOR-3 | STEAM | 2006-09-10 | 452
EVAPORATOR-3 | STEAM | 2006-09-11 | 464
EVAPORATOR-3 | STEAM | 2006-09-12 | 425
EVAPORATOR-3 | STEAM | 2006-09-13 | 451
EVAPORATOR-3 | STEAM | 2006-09-14 | 396
EVAPORATOR-3 | STEAM | 2006-09-15 | 468
EVAPORATOR-3 | STEAM | 2006-09-16 | 416
EVAPORATOR-3 | STEAM | 2006-09-17 | 472
EVAPORATOR-3 | STEAM | 2006-09-18 | 418
EVAPORATOR-3 | STEAM | 2006-09-19 | 475
EVAPORATOR-3 | STEAM | 2006-09-20 | 456
EVAPORATOR-3 | STEAM | 2006-09-21 | 469
EVAPORATOR-3 | STEAM | 2006-09-22 | 472
EVAPORATOR-3 | STEAM | 2006-09-23 | 416
EVAPORATOR-3 | STEAM | 2006-09-24 | 470
EVAPORATOR-3 | STEAM | 2006-09-25 | 464
EVAPORATOR-3 | STEAM | 2006-09-26 | 419
EVAPORATOR-3 | STEAM | 2006-09-27 | 456
EVAPORATOR-3 | STEAM | 2006-09-28 | 452
EVAPORATOR-3 | STEAM | 2006-09-29 | 424
EVAPORATOR-3 | STEAM | 2006-09-30 | 472
13169
EVAPORATOR-3 | STEAM | 2006-10-01 | 464
EVAPORATOR-3 | STEAM | 2006-10-02 | 398
EVAPORATOR-3 | STEAM | 2006-10-03 | 457
EVAPORATOR-3 | STEAM | 2006-10-04 | 236
EVAPORATOR-3 | STEAM | 2006-10-05 | 464
EVAPORATOR-3 | STEAM | 2006-10-06 | 472
EVAPORATOR-3 | STEAM | 2006-10-07 | 472
EVAPORATOR-3 | STEAM | 2006-10-08 | 457
EVAPORATOR-3 | STEAM | 2006-10-09 | 462
EVAPORATOR-3 | STEAM | 2006-10-10 | 466
EVAPORATOR-3 | STEAM | 2006-10-11 | 431
EVAPORATOR-3 | STEAM | 2006-10-12 | 304
EVAPORATOR-3 | STEAM | 2006-10-13 | 476
EVAPORATOR-3 | STEAM | 2006-10-14 | 476
EVAPORATOR-3 | STEAM | 2006-10-15 | 473
EVAPORATOR-3 | STEAM | 2006-10-16 | 465
EVAPORATOR-3 | STEAM | 2006-10-17 | 415
EVAPORATOR-3 | STEAM | 2006-10-18 | 389
EVAPORATOR-3 | STEAM | 2006-10-19 | 458
EVAPORATOR-3 | STEAM | 2006-10-20 | 409
EVAPORATOR-3 | STEAM | 2006-10-21 | 429
EVAPORATOR-3 | STEAM | 2006-10-22 | 416
EVAPORATOR-3 | STEAM | 2006-10-23 | 434
EVAPORATOR-3 | STEAM | 2006-10-24 | 446
EVAPORATOR-3 | STEAM | 2006-10-25 | 453
EVAPORATOR-3 | STEAM | 2006-10-26 | 483
EVAPORATOR-3 | STEAM | 2006-10-27 | 471
EVAPORATOR-3 | STEAM | 2006-10-28 | 466
EVAPORATOR-3 | STEAM | 2006-10-29 | 474
EVAPORATOR-3 | STEAM | 2006-10-30 | 474
EVAPORATOR-3 | STEAM | 2006-10-31 | 544
13734
EVAPORATOR-3 | STEAM | 2006-11-01 | 454
EVAPORATOR-3 | STEAM | 2006-11-02 | 530
EVAPORATOR-3 | STEAM | 2006-11-03 | 469
EVAPORATOR-3 | STEAM | 2006-11-04 | 472
EVAPORATOR-3 | STEAM | 2006-11-05 | 482
EVAPORATOR-3 | STEAM | 2006-11-06 | 503
EVAPORATOR-3 | STEAM | 2006-11-07 | 505
EVAPORATOR-3 | STEAM | 2006-11-08 | 501
EVAPORATOR-3 | STEAM | 2006-11-09 | 510
EVAPORATOR-3 | STEAM | 2006-11-10 | 506
EVAPORATOR-3 | STEAM | 2006-11-11 | 505
EVAPORATOR-3 | STEAM | 2006-11-12 | 475
EVAPORATOR-3 | STEAM | 2006-11-13 | 493
EVAPORATOR-3 | STEAM | 2006-11-14 | 483
EVAPORATOR-3 | STEAM | 2006-11-15 | 414
EVAPORATOR-3 | STEAM | 2006-11-16 | 466
EVAPORATOR-3 | STEAM | 2006-11-17 | 469
EVAPORATOR-3 | STEAM | 2006-11-18 | 476
EVAPORATOR-3 | STEAM | 2006-11-19 | 463
EVAPORATOR-3 | STEAM | 2006-11-20 | 451
EVAPORATOR-3 | STEAM | 2006-11-21 | 456
EVAPORATOR-3 | STEAM | 2006-11-22 | 51
EVAPORATOR-3 | STEAM | 2006-11-23 | 0
EVAPORATOR-3 | STEAM | 2006-11-24 | 0
EVAPORATOR-3 | STEAM | 2006-11-25 | 0
EVAPORATOR-3 | STEAM | 2006-11-26 | 270
EVAPORATOR-3 | STEAM | 2006-11-27 | 508
EVAPORATOR-3 | STEAM | 2006-11-28 | 478
EVAPORATOR-3 | STEAM | 2006-11-29 | 474
EVAPORATOR-3 | STEAM | 2006-11-30 | 411
12275
EVAPORATOR-3 | STEAM | 2006-12-01 | 399
EVAPORATOR-3 | STEAM | 2006-12-02 | 477
EVAPORATOR-3 | STEAM | 2006-12-03 | 488
EVAPORATOR-3 | STEAM | 2006-12-04 | 482
EVAPORATOR-3 | STEAM | 2006-12-05 | 480
EVAPORATOR-3 | STEAM | 2006-12-06 | 480
EVAPORATOR-3 | STEAM | 2006-12-07 | 477
EVAPORATOR-3 | STEAM | 2006-12-08 | 473
EVAPORATOR-3 | STEAM | 2006-12-09 | 480
EVAPORATOR-3 | STEAM | 2006-12-10 | 470
EVAPORATOR-3 | STEAM | 2006-12-11 | 462
EVAPORATOR-3 | STEAM | 2006-12-12 | 400
EVAPORATOR-3 | STEAM | 2006-12-13 | 482
EVAPORATOR-3 | STEAM | 2006-12-14 | 481
EVAPORATOR-3 | STEAM | 2006-12-15 | 401
EVAPORATOR-3 | STEAM | 2006-12-16 | 484
EVAPORATOR-3 | STEAM | 2006-12-17 | 475
EVAPORATOR-3 | STEAM | 2006-12-18 | 414
EVAPORATOR-3 | STEAM | 2006-12-19 | 479
EVAPORATOR-3 | STEAM | 2006-12-20 | 475
EVAPORATOR-3 | STEAM | 2006-12-21 | 481
EVAPORATOR-3 | STEAM | 2006-12-22 | 475
EVAPORATOR-3 | STEAM | 2006-12-23 | 488
EVAPORATOR-3 | STEAM | 2006-12-24 | 489
EVAPORATOR-3 | STEAM | 2006-12-25 | 491
EVAPORATOR-3 | STEAM | 2006-12-26 | 484
EVAPORATOR-3 | STEAM | 2006-12-27 | 486
EVAPORATOR-3 | STEAM | 2006-12-28 | 480
EVAPORATOR-3 | STEAM | 2006-12-29 | 480
EVAPORATOR-3 | STEAM | 2006-12-30 | 398
EVAPORATOR-3 | STEAM | 2006-12-31 | 484
14495

## BLS
TRN_DT | DATA_FOR | VAL
2003-09-01 | BLS FIRED | 188.57
2003-09-02 | BLS FIRED | 175.1
2003-09-03 | BLS FIRED | 744.83
2003-09-04 | BLS FIRED | 452.71
2003-09-05 | BLS FIRED | 484.83
2003-09-06 | BLS FIRED | 512.7
2003-09-07 | BLS FIRED | 524.23
2003-09-08 | BLS FIRED | 537.53
2003-09-09 | BLS FIRED | 524.33
2003-09-10 | BLS FIRED | 73.23
2003-09-11 | BLS FIRED | 518.2
2003-09-12 | BLS FIRED | 543.48
2003-09-13 | BLS FIRED | 522.01
2003-09-14 | BLS FIRED | 533
2003-09-15 | BLS FIRED | 589.52
2003-09-16 | BLS FIRED | 603.3
2003-09-17 | BLS FIRED | 612.73
2003-09-18 | BLS FIRED | 637.99
2003-09-19 | BLS FIRED | 614.39
2003-09-20 | BLS FIRED | 610.55
2003-09-21 | BLS FIRED | 618.64
2003-09-22 | BLS FIRED | 557.25
2003-09-23 | BLS FIRED | 482.41
2003-09-24 | BLS FIRED | 540.74
2003-09-25 | BLS FIRED | 532.33
2003-09-26 | BLS FIRED | 573.63
2003-09-27 | BLS FIRED | 594.68
2003-09-28 | BLS FIRED | 627.47
2003-09-29 | BLS FIRED | 640.2
2003-09-30 | BLS FIRED | 649.53
15820.11
2003-10-01 | BLS FIRED | 591.3
2003-10-02 | BLS FIRED | 611.36
2003-10-03 | BLS FIRED | 637.52
2003-10-04 | BLS FIRED | 597.54
2003-10-05 | BLS FIRED | 582.77
2003-10-06 | BLS FIRED | 618.59
2003-10-07 | BLS FIRED | 540.51
2003-10-08 | BLS FIRED | 517.35
2003-10-09 | BLS FIRED | 543.92
2003-10-10 | BLS FIRED | 572.73
2003-10-11 | BLS FIRED | 614.72
2003-10-12 | BLS FIRED | 640.47
2003-10-13 | BLS FIRED | 653.64
2003-10-14 | BLS FIRED | 660.24
2003-10-15 | BLS FIRED | 612.87
2003-10-16 | BLS FIRED | 597.9
2003-10-17 | BLS FIRED | 650.01
2003-10-18 | BLS FIRED | 513.1
2003-10-19 | BLS FIRED | 641.03
2003-10-20 | BLS FIRED | 615.93
2003-10-21 | BLS FIRED | 648.77
2003-10-22 | BLS FIRED | 600.72
2003-10-23 | BLS FIRED | 606.3
2003-10-24 | BLS FIRED | 647.14
2003-10-25 | BLS FIRED | 665.52
2003-10-26 | BLS FIRED | 646.26
2003-10-27 | BLS FIRED | 646.26
2003-10-28 | BLS FIRED | 680.76
2003-10-29 | BLS FIRED | 631.97
2003-10-30 | BLS FIRED | 622.66
2003-10-31 | BLS FIRED | 650.14
19060
2003-11-01 | BLS FIRED | 678.47
2003-11-02 | BLS FIRED | 673.95
2003-11-03 | BLS FIRED | 601.06
2003-11-04 | BLS FIRED | 613.59
2003-11-05 | BLS FIRED | 603.29
2003-11-06 | BLS FIRED | 644.75
2003-11-07 | BLS FIRED | 588.84
2003-11-08 | BLS FIRED | 660.28
2003-11-09 | BLS FIRED | 619.47
2003-11-10 | BLS FIRED | 215.93
2003-11-11 | BLS FIRED | 616.79
2003-11-12 | BLS FIRED | 604.4
2003-11-13 | BLS FIRED | 638.81
2003-11-14 | BLS FIRED | 660.6
2003-11-15 | BLS FIRED | 686.47
2003-11-16 | BLS FIRED | 661.38
2003-11-17 | BLS FIRED | 682.06
2003-11-18 | BLS FIRED | 677.62
2003-11-19 | BLS FIRED | 717.74
2003-11-20 | BLS FIRED | 676.42
2003-11-21 | BLS FIRED | 658.9
2003-11-22 | BLS FIRED | 599.23
2003-11-23 | BLS FIRED | 241.13
2003-11-24 | BLS FIRED | 237.12
2003-11-25 | BLS FIRED | 941.1
2003-11-26 | BLS FIRED | 665.21
2003-11-27 | BLS FIRED | 611.24
2003-11-28 | BLS FIRED | 645.1
2003-11-29 | BLS FIRED | 695.76
2003-11-30 | BLS FIRED | 642.2
18458.91
2003-12-01 | BLS FIRED | 623.64
2003-12-02 | BLS FIRED | 555.86
2003-12-03 | BLS FIRED | 586.81
2003-12-04 | BLS FIRED | 615.9
2003-12-05 | BLS FIRED | 679.58
2003-12-06 | BLS FIRED | 605.85
2003-12-07 | BLS FIRED | 667.52
2003-12-08 | BLS FIRED | 718.09
2003-12-09 | BLS FIRED | 788.81
2003-12-10 | BLS FIRED | 623.1
2003-12-11 | BLS FIRED | 743.75
2003-12-12 | BLS FIRED | 793.55
2003-12-13 | BLS FIRED | 305.14
2003-12-14 | BLS FIRED | 412.18
2003-12-15 | BLS FIRED | 777.9
2003-12-16 | BLS FIRED | 562.35
2003-12-17 | BLS FIRED | 657.89
2003-12-18 | BLS FIRED | 673.09
2003-12-19 | BLS FIRED | 696.64
2003-12-20 | BLS FIRED | 768.44
2003-12-21 | BLS FIRED | 721.49
2003-12-22 | BLS FIRED | 645.46
2003-12-23 | BLS FIRED | 645.94
2003-12-24 | BLS FIRED | 683.7
2003-12-25 | BLS FIRED | 680.94
2003-12-26 | BLS FIRED | 599.35
2003-12-27 | BLS FIRED | 593.15
2003-12-28 | BLS FIRED | 592.58
2003-12-29 | BLS FIRED | 609.23
2003-12-30 | BLS FIRED | 630.2
2003-12-31 | BLS FIRED | 585.39
19843.52
2004-01-01 | BLS FIRED | 631.11
2004-01-02 | BLS FIRED | 658.65
2004-01-03 | BLS FIRED | 623.55
2004-01-04 | BLS FIRED | 698.61
2004-01-05 | BLS FIRED | 666.77
2004-01-06 | BLS FIRED | 660.96
2004-01-07 | BLS FIRED | 620.35
2004-01-08 | BLS FIRED | 626.27
2004-01-09 | BLS FIRED | 644.85
2004-01-10 | BLS FIRED | 685.95
2004-01-11 | BLS FIRED | 634.7
2004-01-12 | BLS FIRED | 635.1
2004-01-13 | BLS FIRED | 642.43
2004-01-14 | BLS FIRED | 678.58
2004-01-15 | BLS FIRED | 687.8
2004-01-16 | BLS FIRED | 662.37
2004-01-17 | BLS FIRED | 657.87
2004-01-18 | BLS FIRED | 634.71
2004-01-19 | BLS FIRED | 677.91
2004-01-20 | BLS FIRED | 679.31
2004-01-21 | BLS FIRED | 651.78
2004-01-22 | BLS FIRED | 635.6
2004-01-23 | BLS FIRED | 659.65
2004-01-24 | BLS FIRED | 660.96
2004-01-25 | BLS FIRED | 628.23
2004-01-26 | BLS FIRED | 569.81
2004-01-27 | BLS FIRED | 602.83
2004-01-28 | BLS FIRED | 634.71
2004-01-29 | BLS FIRED | 590.12
2004-01-30 | BLS FIRED | 586
2004-01-31 | BLS FIRED | 595.42
19922.96
2004-02-01 | BLS FIRED | 594.72
2004-02-02 | BLS FIRED | 178.32
2004-02-03 | BLS FIRED | 571.06
2004-02-04 | BLS FIRED | 599.87
2004-02-05 | BLS FIRED | 607.15
2004-02-06 | BLS FIRED | 629.58
2004-02-07 | BLS FIRED | 650.52
2004-02-08 | BLS FIRED | 664.2
2004-02-09 | BLS FIRED | 635.31
2004-02-10 | BLS FIRED | 635.98
2004-02-11 | BLS FIRED | 641.07
2004-02-12 | BLS FIRED | 646.31
2004-02-13 | BLS FIRED | 621.15
2004-02-14 | BLS FIRED | 629.68
2004-02-15 | BLS FIRED | 650.53
2004-02-16 | BLS FIRED | 644.13
2004-02-17 | BLS FIRED | 682.81
2004-02-18 | BLS FIRED | 668.67
2004-02-19 | BLS FIRED | 669.23
2004-02-20 | BLS FIRED | 436.61
2004-02-21 | BLS FIRED | 695.89
2004-02-22 | BLS FIRED | 627.05
2004-02-23 | BLS FIRED | 651.65
2004-02-24 | BLS FIRED | 650.59
2004-02-25 | BLS FIRED | 658.82
2004-02-26 | BLS FIRED | 639.29
2004-02-27 | BLS FIRED | 606.81
2004-02-28 | BLS FIRED | 565.96
2004-02-29 | BLS FIRED | 638.73
17791.69
2004-03-01 | BLS FIRED | 620.34
2004-03-02 | BLS FIRED | 638.82
2004-03-03 | BLS FIRED | 645.5
2004-03-04 | BLS FIRED | 553.91
2004-03-05 | BLS FIRED | 585.21
2004-03-06 | BLS FIRED | 514.05
2004-03-07 | BLS FIRED | 619.74
2004-03-08 | BLS FIRED | 647.75
2004-03-09 | BLS FIRED | 685.64
2004-03-10 | BLS FIRED | 639.22
2004-03-11 | BLS FIRED | 674.04
2004-03-12 | BLS FIRED | 660.53
2004-03-13 | BLS FIRED | 639.22
2004-03-14 | BLS FIRED | 616.32
2004-03-15 | BLS FIRED | 474.26
2004-03-16 | BLS FIRED | 658.05
2004-03-17 | BLS FIRED | 646.15
2004-03-18 | BLS FIRED | 678.64
2004-03-19 | BLS FIRED | 667.02
2004-03-20 | BLS FIRED | 646.03
2004-03-21 | BLS FIRED | 651.93
2004-03-22 | BLS FIRED | 382.65
2004-03-23 | BLS FIRED | 583.55
2004-03-24 | BLS FIRED | 651.4
2004-03-25 | BLS FIRED | 676.49
2004-03-26 | BLS FIRED | 589.31
2004-03-27 | BLS FIRED | 660.94
2004-03-28 | BLS FIRED | 598.56
2004-03-29 | BLS FIRED | 631.02
2004-03-30 | BLS FIRED | 627.1
2004-03-31 | BLS FIRED | 607.6
19170.99
2004-04-01 | BLS FIRED | 557.46
2004-04-02 | BLS FIRED | 614.89
2004-04-03 | BLS FIRED | 656.64
2004-04-04 | BLS FIRED | 639.97
2004-04-05 | BLS FIRED | 617.67
2004-04-06 | BLS FIRED | 642.24
2004-04-07 | BLS FIRED | 635.77
2004-04-08 | BLS FIRED | 642.47
2004-04-09 | BLS FIRED | 592.71
2004-04-10 | BLS FIRED | 589.98
2004-04-11 | BLS FIRED | 638.4
2004-04-12 | BLS FIRED | 673.03
2004-04-13 | BLS FIRED | 663.76
2004-04-14 | BLS FIRED | 612.91
2004-04-15 | BLS FIRED | 637.25
2004-04-16 | BLS FIRED | 616.07
2004-04-17 | BLS FIRED | 585.43
2004-04-18 | BLS FIRED | 606.84
2004-04-19 | BLS FIRED | 584.94
2004-04-20 | BLS FIRED | 593.72
2004-04-21 | BLS FIRED | 619.17
2004-04-22 | BLS FIRED | 624.59
2004-04-23 | BLS FIRED | 678.24
2004-04-24 | BLS FIRED | 668.83
2004-04-25 | BLS FIRED | 649.12
2004-04-26 | BLS FIRED | 603.31
2004-04-27 | BLS FIRED | 602.33
2004-04-28 | BLS FIRED | 620.92
2004-04-29 | BLS FIRED | 601.13
2004-04-30 | BLS FIRED | 606.78
18676.57
2004-05-01 | BLS FIRED | 607.67
2004-05-02 | BLS FIRED | 617.43
2004-05-03 | BLS FIRED | 655.37
2004-05-04 | BLS FIRED | 670.06
2004-05-05 | BLS FIRED | 631.27
2004-05-06 | BLS FIRED | 685.47
2004-05-07 | BLS FIRED | 717.37
2004-05-08 | BLS FIRED | 730.8
2004-05-09 | BLS FIRED | 684.17
2004-05-10 | BLS FIRED | 718.66
2004-05-11 | BLS FIRED | 678.47
2004-05-12 | BLS FIRED | 396.78
2004-05-13 | BLS FIRED | 434.93
2004-05-14 | BLS FIRED | 698.41
2004-05-15 | BLS FIRED | 654.64
2004-05-16 | BLS FIRED | 688.14
2004-05-17 | BLS FIRED | 694.73
2004-05-18 | BLS FIRED | 673.4
2004-05-19 | BLS FIRED | 684.56
2004-05-20 | BLS FIRED | 682.26
2004-05-21 | BLS FIRED | 666.04
2004-05-22 | BLS FIRED | 652.66
2004-05-23 | BLS FIRED | 661.56
2004-05-24 | BLS FIRED | 615.35
2004-05-25 | BLS FIRED | 640.96
2004-05-26 | BLS FIRED | 608.08
2004-05-27 | BLS FIRED | 669.44
2004-05-28 | BLS FIRED | 674.99
2004-05-29 | BLS FIRED | 515.77
2004-05-30 | BLS FIRED | 661.63
2004-05-31 | BLS FIRED | 652.5
20023.57
2004-06-01 | BLS FIRED | 715.8
2004-06-02 | BLS FIRED | 713.04
2004-06-03 | BLS FIRED | 681.86
2004-06-04 | BLS FIRED | 674.34
2004-06-05 | BLS FIRED | 633.56
2004-06-06 | BLS FIRED | 617.09
2004-06-07 | BLS FIRED | 631.45
2004-06-08 | BLS FIRED | 619.82
2004-06-09 | BLS FIRED | 654.54
2004-06-10 | BLS FIRED | 644.69
2004-06-11 | BLS FIRED | 656.64
2004-06-12 | BLS FIRED | 642.45
2004-06-13 | BLS FIRED | 636.77
2004-06-14 | BLS FIRED | 640.75
2004-06-15 | BLS FIRED | 655.74
2004-06-16 | BLS FIRED | 239.19
2004-06-17 | BLS FIRED | 662.86
2004-06-18 | BLS FIRED | 655.22
2004-06-19 | BLS FIRED | 665.43
2004-06-20 | BLS FIRED | 652.26
2004-06-21 | BLS FIRED | 627.82
2004-06-22 | BLS FIRED | 637.7
2004-06-23 | BLS FIRED | 517.05
2004-06-24 | BLS FIRED | 451.06
2004-06-25 | BLS FIRED | 565.26
2004-06-26 | BLS FIRED | 645.8
2004-06-27 | BLS FIRED | 650.45
2004-06-28 | BLS FIRED | 596
2004-06-29 | BLS FIRED | 688.74
2004-06-30 | BLS FIRED | 639.74
18713.12
2004-07-01 | BLS FIRED | 648.1
2004-07-02 | BLS FIRED | 676.18
2004-07-03 | BLS FIRED | 702
2004-07-04 | BLS FIRED | 647.73
2004-07-05 | BLS FIRED | 648.49
2004-07-06 | BLS FIRED | 673.18
2004-07-07 | BLS FIRED | 670.53
2004-07-08 | BLS FIRED | 632.18
2004-07-09 | BLS FIRED | 599.53
2004-07-10 | BLS FIRED | 636.66
2004-07-11 | BLS FIRED | 619.48
2004-07-12 | BLS FIRED | 644.92
2004-07-13 | BLS FIRED | 593.81
2004-07-14 | BLS FIRED | 642.41
2004-07-15 | BLS FIRED | 640.11
2004-07-16 | BLS FIRED | 658.57
2004-07-17 | BLS FIRED | 594.67
2004-07-18 | BLS FIRED | 604.18
2004-07-19 | BLS FIRED | 613.72
2004-07-20 | BLS FIRED | 598.05
2004-07-21 | BLS FIRED | 630.51
2004-07-22 | BLS FIRED | 649.53
2004-07-23 | BLS FIRED | 671.27
2004-07-24 | BLS FIRED | 645.4
2004-07-25 | BLS FIRED | 633.27
2004-07-26 | BLS FIRED | 655.57
2004-07-27 | BLS FIRED | 654.41
2004-07-28 | BLS FIRED | 640.55
2004-07-29 | BLS FIRED | 646.7
2004-07-30 | BLS FIRED | 627.59
2004-07-31 | BLS FIRED | 638.6
19837.9
2004-08-01 | BLS FIRED | 514.27
2004-08-02 | BLS FIRED | 668.33
2004-08-03 | BLS FIRED | 618.26
2004-08-04 | BLS FIRED | 610.94
2004-08-05 | BLS FIRED | 603.68
2004-08-06 | BLS FIRED | 634.23
2004-08-07 | BLS FIRED | 573.61
2004-08-09 | BLS FIRED | 615.55
2004-08-10 | BLS FIRED | 625.33
2004-08-11 | BLS FIRED | 630.96
2004-08-12 | BLS FIRED | 640.12
2004-08-13 | BLS FIRED | 592.51
2004-08-14 | BLS FIRED | 619.36
2004-08-15 | BLS FIRED | 608.61
2004-08-16 | BLS FIRED | 623.28
2004-08-17 | BLS FIRED | 639.58
2004-08-18 | BLS FIRED | 610.94
2004-08-19 | BLS FIRED | 595.63
2004-08-20 | BLS FIRED | 591.2
2004-08-21 | BLS FIRED | 587.91
2004-08-22 | BLS FIRED | 603.68
2004-08-23 | BLS FIRED | 585.76
2004-08-24 | BLS FIRED | 585.86
2004-08-25 | BLS FIRED | 622.83
2004-08-26 | BLS FIRED | 659.69
2004-08-27 | BLS FIRED | 643.56
2004-08-28 | BLS FIRED | 585.47
2004-08-29 | BLS FIRED | 600.27
2004-08-30 | BLS FIRED | 635.12
2004-08-31 | BLS FIRED | 622.17
18348.71
2004-09-01 | BLS FIRED | 43.16
2004-09-02 | BLS FIRED | 98.24
2004-09-03 | BLS FIRED | 65.24
2004-09-04 | BLS FIRED | 107.56
2004-09-05 | BLS FIRED | 615.86
2004-09-06 | BLS FIRED | 501.62
2004-09-07 | BLS FIRED | 580.33
2004-09-08 | BLS FIRED | 642.44
2004-09-09 | BLS FIRED | 672.57
2004-09-10 | BLS FIRED | 673.38
2004-09-11 | BLS FIRED | 641.92
2004-09-12 | BLS FIRED | 692.51
2004-09-13 | BLS FIRED | 631.49
2004-09-14 | BLS FIRED | 642.39
2004-09-15 | BLS FIRED | 669.26
2004-09-16 | BLS FIRED | 606.84
2004-09-17 | BLS FIRED | 647.51
2004-09-18 | BLS FIRED | 615.44
2004-09-19 | BLS FIRED | 675.35
2004-09-20 | BLS FIRED | 622.78
2004-09-21 | BLS FIRED | 633.92
2004-09-22 | BLS FIRED | 629.24
2004-09-23 | BLS FIRED | 646.38
2004-09-24 | BLS FIRED | 598.43
2004-09-25 | BLS FIRED | 343.75
2004-09-26 | BLS FIRED | 513.54
2004-09-27 | BLS FIRED | 604.45
2004-09-28 | BLS FIRED | 639.14
2004-09-29 | BLS FIRED | 562.09
2004-09-30 | BLS FIRED | 493.17
16110
2004-10-01 | BLS FIRED | 524.65
2004-10-02 | BLS FIRED | 592.83
2004-10-03 | BLS FIRED | 660.25
2004-10-04 | BLS FIRED | 678.48
2004-10-05 | BLS FIRED | 650.04
2004-10-06 | BLS FIRED | 626.23
2004-10-07 | BLS FIRED | 615.67
2004-10-08 | BLS FIRED | 672.89
2004-10-09 | BLS FIRED | 683.16
2004-10-10 | BLS FIRED | 646.77
2004-10-11 | BLS FIRED | 661.44
2004-10-12 | BLS FIRED | 645.89
2004-10-13 | BLS FIRED | 634.87
2004-10-14 | BLS FIRED | 546.57
2004-10-15 | BLS FIRED | 652.09
2004-10-16 | BLS FIRED | 564.99
2004-10-17 | BLS FIRED | 538.57
2004-10-18 | BLS FIRED | 571.08
2004-10-19 | BLS FIRED | 577.24
2004-10-20 | BLS FIRED | 611.82
2004-10-21 | BLS FIRED | 589.89
2004-10-22 | BLS FIRED | 578.09
2004-10-23 | BLS FIRED | 593.26
2004-10-24 | BLS FIRED | 596.29
2004-10-25 | BLS FIRED | 516.1
2004-10-26 | BLS FIRED | 538.34
2004-10-27 | BLS FIRED | 563.21
2004-10-28 | BLS FIRED | 653.36
2004-10-29 | BLS FIRED | 637.99
2004-10-30 | BLS FIRED | 607.41
2004-10-31 | BLS FIRED | 603.07
18832.54
2004-11-01 | BLS FIRED | 564.18
2004-11-02 | BLS FIRED | 259.92
2004-11-03 | BLS FIRED | 436.07
2004-11-04 | BLS FIRED | 640.38
2004-11-05 | BLS FIRED | 645.66
2004-11-06 | BLS FIRED | 613.68
2004-11-07 | BLS FIRED | 672.66
2004-11-08 | BLS FIRED | 671.9
2004-11-09 | BLS FIRED | 671.24
2004-11-10 | BLS FIRED | 568.73
2004-11-11 | BLS FIRED | 442.96
2004-11-12 | BLS FIRED | 643.16
2004-11-13 | BLS FIRED | 637.57
2004-11-14 | BLS FIRED | 617.91
2004-11-15 | BLS FIRED | 600.76
2004-11-16 | BLS FIRED | 636.29
2004-11-17 | BLS FIRED | 549.34
2004-11-18 | BLS FIRED | 616.97
2004-11-19 | BLS FIRED | 615.1
2004-11-20 | BLS FIRED | 613.7
2004-11-21 | BLS FIRED | 605.65
2004-11-22 | BLS FIRED | 609.8
2004-11-23 | BLS FIRED | 637.33
2004-11-24 | BLS FIRED | 379.8
2004-11-25 | BLS FIRED | 673.6
2004-11-26 | BLS FIRED | 670.64
2004-11-27 | BLS FIRED | 645.04
2004-11-28 | BLS FIRED | 671.61
2004-11-29 | BLS FIRED | 648.81
2004-11-30 | BLS FIRED | 656.38
17916.84
2004-12-01 | BLS FIRED | 672.1
2004-12-02 | BLS FIRED | 676.13
2004-12-03 | BLS FIRED | 632.02
2004-12-04 | BLS FIRED | 604.82
2004-12-05 | BLS FIRED | 588.15
2004-12-06 | BLS FIRED | 619.77
2004-12-07 | BLS FIRED | 524.51
2004-12-08 | BLS FIRED | 640.65
2004-12-09 | BLS FIRED | 589.3
2004-12-10 | BLS FIRED | 669.52
2004-12-11 | BLS FIRED | 550.66
2004-12-12 | BLS FIRED | 625.8
2004-12-13 | BLS FIRED | 637.55
2004-12-14 | BLS FIRED | 561.97
2004-12-15 | BLS FIRED | 672.38
2004-12-16 | BLS FIRED | 689.75
2004-12-17 | BLS FIRED | 643.11
2004-12-18 | BLS FIRED | 647.08
2004-12-19 | BLS FIRED | 625.94
2004-12-20 | BLS FIRED | 543.37
2004-12-21 | BLS FIRED | 574.76
2004-12-22 | BLS FIRED | 621.66
2004-12-23 | BLS FIRED | 617.23
2004-12-24 | BLS FIRED | 635.17
2004-12-25 | BLS FIRED | 633.75
2004-12-26 | BLS FIRED | 633.44
2004-12-27 | BLS FIRED | 635.1
2004-12-28 | BLS FIRED | 649.82
2004-12-29 | BLS FIRED | 637.51
2004-12-30 | BLS FIRED | 626.05
2004-12-31 | BLS FIRED | 639.58
19318.65
2005-01-01 | BLS FIRED | 638.85
2005-01-02 | BLS FIRED | 561.17
2005-01-03 | BLS FIRED | 638.67
2005-01-04 | BLS FIRED | 639.74
2005-01-05 | BLS FIRED | 662.56
2005-01-06 | BLS FIRED | 648.1
2005-01-07 | BLS FIRED | 571.2
2005-01-08 | BLS FIRED | 275.49
2005-01-09 | BLS FIRED | 571.25
2005-01-10 | BLS FIRED | 620.37
2005-01-11 | BLS FIRED | 585.48
2005-01-12 | BLS FIRED | 626.92
2005-01-13 | BLS FIRED | 599.92
2005-01-14 | BLS FIRED | 625.32
2005-01-15 | BLS FIRED | 641.13
2005-01-16 | BLS FIRED | 627.05
2005-01-17 | BLS FIRED | 636.27
2005-01-18 | BLS FIRED | 594.61
2005-01-19 | BLS FIRED | 619.44
2005-01-20 | BLS FIRED | 574.52
2005-01-21 | BLS FIRED | 553.93
2005-01-22 | BLS FIRED | 613.22
2005-01-23 | BLS FIRED | 639.57
2005-01-24 | BLS FIRED | 565.67
2005-01-25 | BLS FIRED | 519.27
2005-01-26 | BLS FIRED | 605.3
2005-01-27 | BLS FIRED | 609.98
2005-01-28 | BLS FIRED | 596.6
2005-01-29 | BLS FIRED | 637.21
2005-01-30 | BLS FIRED | 630.79
2005-01-31 | BLS FIRED | 607.9
18537.5
2005-02-01 | BLS FIRED | 434.1
2005-02-02 | BLS FIRED | 592.29
2005-02-03 | BLS FIRED | 616.52
2005-02-04 | BLS FIRED | 596.29
2005-02-05 | BLS FIRED | 658
2005-02-06 | BLS FIRED | 664.62
2005-02-07 | BLS FIRED | 680.25
2005-02-08 | BLS FIRED | 659.86
2005-02-09 | BLS FIRED | 671.49
2005-02-10 | BLS FIRED | 90.12
2005-02-12 | BLS FIRED | 248.12
2005-02-13 | BLS FIRED | 623.36
2005-02-14 | BLS FIRED | 643.92
2005-02-15 | BLS FIRED | 624.24
2005-02-16 | BLS FIRED | 640.95
2005-02-17 | BLS FIRED | 630.42
2005-02-18 | BLS FIRED | 662.51
2005-02-19 | BLS FIRED | 661.94
2005-02-20 | BLS FIRED | 644.12
2005-02-21 | BLS FIRED | 623.17
2005-02-22 | BLS FIRED | 563.74
2005-02-23 | BLS FIRED | 49.78
2005-02-24 | BLS FIRED | 424.61
2005-02-25 | BLS FIRED | 621.6
2005-02-26 | BLS FIRED | 611.08
2005-02-27 | BLS FIRED | 632.03
2005-02-28 | BLS FIRED | 660.92
15230.05
2005-03-01 | BLS FIRED | 657.45
2005-03-02 | BLS FIRED | 662.93
2005-03-03 | BLS FIRED | 661.3
2005-03-04 | BLS FIRED | 656.08
2005-03-05 | BLS FIRED | 666.52
2005-03-06 | BLS FIRED | 666.32
2005-03-07 | BLS FIRED | 680.81
2005-03-08 | BLS FIRED | 623.36
2005-03-09 | BLS FIRED | 468.46
2005-03-10 | BLS FIRED | 660.36
2005-03-11 | BLS FIRED | 640.24
2005-03-12 | BLS FIRED | 658.68
2005-03-13 | BLS FIRED | 663.47
2005-03-14 | BLS FIRED | 654.14
2005-03-15 | BLS FIRED | 640.13
2005-03-16 | BLS FIRED | 640.28
2005-03-17 | BLS FIRED | 630.61
2005-03-18 | BLS FIRED | 650.22
2005-03-19 | BLS FIRED | 656.41
2005-03-20 | BLS FIRED | 662.92
2005-03-21 | BLS FIRED | 662.92
2005-03-22 | BLS FIRED | 644.35
2005-03-23 | BLS FIRED | 652.04
2005-03-24 | BLS FIRED | 640.83
2005-03-25 | BLS FIRED | 625.3
2005-03-26 | BLS FIRED | 626.42
2005-03-27 | BLS FIRED | 598.17
2005-03-28 | BLS FIRED | 624.84
2005-03-29 | BLS FIRED | 652.37
2005-03-30 | BLS FIRED | 604.53
2005-03-31 | BLS FIRED | 624.37
19856.83
2005-04-01 | BLS FIRED | 668.97
2005-04-02 | BLS FIRED | 655.99
2005-04-03 | BLS FIRED | 662.53
2005-04-04 | BLS FIRED | 720.09
2005-04-05 | BLS FIRED | 737.84
2005-04-06 | BLS FIRED | 711.47
2005-04-07 | BLS FIRED | 719.16
2005-04-08 | BLS FIRED | 686.44
2005-04-09 | BLS FIRED | 691.25
2005-04-10 | BLS FIRED | 657.59
2005-04-11 | BLS FIRED | 675.93
2005-04-12 | BLS FIRED | 700.76
2005-04-13 | BLS FIRED | 590.28
2005-04-14 | BLS FIRED | 688.67
2005-04-15 | BLS FIRED | 690.19
2005-04-16 | BLS FIRED | 701.95
2005-04-17 | BLS FIRED | 711.26
2005-04-18 | BLS FIRED | 696.23
2005-04-19 | BLS FIRED | 685.66
2005-04-20 | BLS FIRED | 708.53
2005-04-21 | BLS FIRED | 698.71
2005-04-22 | BLS FIRED | 686.84
2005-04-23 | BLS FIRED | 700.87
2005-04-24 | BLS FIRED | 695.09
2005-04-25 | BLS FIRED | 689.93
2005-04-26 | BLS FIRED | 645.3
2005-04-27 | BLS FIRED | 634.41
2005-04-28 | BLS FIRED | 651.83
2005-04-29 | BLS FIRED | 636.27
2005-04-30 | BLS FIRED | 669.73
20469.77
2005-05-01 | BLS FIRED | 641.25
2005-05-02 | BLS FIRED | 664.47
2005-05-03 | BLS FIRED | 635.52
2005-05-04 | BLS FIRED | 614.82
2005-05-05 | BLS FIRED | 605.25
2005-05-06 | BLS FIRED | 592.75
2005-05-07 | BLS FIRED | 589.22
2005-05-08 | BLS FIRED | 672.75
2005-05-09 | BLS FIRED | 167.42
2005-05-10 | BLS FIRED | 614.12
2005-05-11 | BLS FIRED | 612.09
2005-05-12 | BLS FIRED | 736.89
2005-05-13 | BLS FIRED | 602.36
2005-05-14 | BLS FIRED | 657.56
2005-05-15 | BLS FIRED | 678.58
2005-05-16 | BLS FIRED | 749.97
2005-05-17 | BLS FIRED | 701.77
2005-05-18 | BLS FIRED | 710.34
2005-05-19 | BLS FIRED | 722.83
2005-05-20 | BLS FIRED | 698.43
2005-05-21 | BLS FIRED | 720.89
2005-05-22 | BLS FIRED | 726.43
2005-05-23 | BLS FIRED | 756.7
2005-05-24 | BLS FIRED | 696.77
2005-05-25 | BLS FIRED | 699.8
2005-05-26 | BLS FIRED | 715.75
2005-05-27 | BLS FIRED | 683.68
2005-05-28 | BLS FIRED | 681.97
2005-05-29 | BLS FIRED | 731.6
2005-05-30 | BLS FIRED | 636.63
2005-05-31 | BLS FIRED | 693.97
20412.58
2005-06-01 | BLS FIRED | 718.44
2005-06-02 | BLS FIRED | 714.72
2005-06-03 | BLS FIRED | 633.93
2005-06-04 | BLS FIRED | 691.51
2005-06-05 | BLS FIRED | 640.15
2005-06-06 | BLS FIRED | 654.29
2005-06-07 | BLS FIRED | 673.3
2005-06-08 | BLS FIRED | 698.81
2005-06-09 | BLS FIRED | 670.12
2005-06-10 | BLS FIRED | 702.7
2005-06-11 | BLS FIRED | 691.07
2005-06-12 | BLS FIRED | 694.07
2005-06-13 | BLS FIRED | 671.32
2005-06-14 | BLS FIRED | 565.53
2005-06-15 | BLS FIRED | 607.51
2005-06-16 | BLS FIRED | 696.52
2005-06-17 | BLS FIRED | 700.93
2005-06-18 | BLS FIRED | 712.97
2005-06-19 | BLS FIRED | 675.7
2005-06-20 | BLS FIRED | 671.31
2005-06-21 | BLS FIRED | 661.41
2005-06-22 | BLS FIRED | 673.06
2005-06-23 | BLS FIRED | 715.84
2005-06-24 | BLS FIRED | 718.49
2005-06-25 | BLS FIRED | 632.8
2005-06-26 | BLS FIRED | 671.25
2005-06-27 | BLS FIRED | 684.22
2005-06-28 | BLS FIRED | 697.06
2005-06-29 | BLS FIRED | 644.1
2005-06-30 | BLS FIRED | 429.96
20013.09
2005-07-01 | BLS FIRED | 601.66
2005-07-02 | BLS FIRED | 524.49
2005-07-03 | BLS FIRED | 504.4
2005-07-04 | BLS FIRED | 629.4
2005-07-05 | BLS FIRED | 617.51
2005-07-06 | BLS FIRED | 644.5
2005-07-07 | BLS FIRED | 640.02
2005-07-08 | BLS FIRED | 659.98
2005-07-09 | BLS FIRED | 644.3
2005-07-10 | BLS FIRED | 623.22
2005-07-11 | BLS FIRED | 599.85
2005-07-12 | BLS FIRED | 627.34
2005-07-13 | BLS FIRED | 654.44
2005-07-14 | BLS FIRED | 639.95
2005-07-15 | BLS FIRED | 664.34
2005-07-16 | BLS FIRED | 658.52
2005-07-17 | BLS FIRED | 676.51
2005-07-18 | BLS FIRED | 653.3
2005-07-19 | BLS FIRED | 368.91
2005-07-20 | BLS FIRED | 634.53
2005-07-21 | BLS FIRED | 688.37
2005-07-22 | BLS FIRED | 654.07
2005-07-23 | BLS FIRED | 677.47
2005-07-24 | BLS FIRED | 701.14
2005-07-25 | BLS FIRED | 552.47
2005-07-26 | BLS FIRED | 525.72
2005-07-27 | BLS FIRED | 589.8
2005-07-28 | BLS FIRED | 595.6
2005-07-29 | BLS FIRED | 594.76
2005-07-30 | BLS FIRED | 610.51
2005-07-31 | BLS FIRED | 417.35
18874.43
2005-08-01 | BLS FIRED | 213.55
2005-08-02 | BLS FIRED | 703.34
2005-08-03 | BLS FIRED | 555.34
2005-08-04 | BLS FIRED | 603.17
2005-08-05 | BLS FIRED | 667.81
2005-08-06 | BLS FIRED | 555.93
2005-08-07 | BLS FIRED | 541.27
2005-08-08 | BLS FIRED | 596.56
2005-08-09 | BLS FIRED | 671.26
2005-08-10 | BLS FIRED | 680.44
2005-08-11 | BLS FIRED | 659.29
2005-08-12 | BLS FIRED | 665.09
2005-08-13 | BLS FIRED | 692.24
2005-08-14 | BLS FIRED | 713.68
2005-08-15 | BLS FIRED | 658.26
2005-08-16 | BLS FIRED | 591.7
2005-08-17 | BLS FIRED | 578.5
2005-08-18 | BLS FIRED | 639.02
2005-08-19 | BLS FIRED | 671.71
2005-08-20 | BLS FIRED | 689.1
2005-08-21 | BLS FIRED | 674.64
2005-08-22 | BLS FIRED | 674.14
2005-08-23 | BLS FIRED | 564.9
2005-08-24 | BLS FIRED | 305.3
2005-08-25 | BLS FIRED | 544.33
2005-08-26 | BLS FIRED | 599.9
2005-08-27 | BLS FIRED | 574.99
2005-08-28 | BLS FIRED | 644.01
2005-08-29 | BLS FIRED | 650.97
2005-08-30 | BLS FIRED | 648.78
2005-08-31 | BLS FIRED | 628.8
18858.02
2005-09-01 | BLS FIRED | 621.4
2005-09-02 | BLS FIRED | 481.71
2005-09-03 | BLS FIRED | 635.11
2005-09-04 | BLS FIRED | 648.8
2005-09-05 | BLS FIRED | 694.98
2005-09-06 | BLS FIRED | 685.88
2005-09-07 | BLS FIRED | 658.69
2005-09-08 | BLS FIRED | 679.82
2005-09-09 | BLS FIRED | 654.48
2005-09-10 | BLS FIRED | 631.43
2005-09-11 | BLS FIRED | 628.03
2005-09-12 | BLS FIRED | 689.1
2005-09-13 | BLS FIRED | 657.32
2005-09-14 | BLS FIRED | 662.71
2005-09-15 | BLS FIRED | 685.05
2005-09-16 | BLS FIRED | 667.16
2005-09-17 | BLS FIRED | 707.33
2005-09-18 | BLS FIRED | 685.96
2005-09-19 | BLS FIRED | 682.73
2005-09-20 | BLS FIRED | 626.91
2005-09-21 | BLS FIRED | 650.04
2005-09-22 | BLS FIRED | 678.74
2005-09-23 | BLS FIRED | 612.56
2005-09-24 | BLS FIRED | 675
2005-09-25 | BLS FIRED | 664.01
2005-09-26 | BLS FIRED | 689.99
2005-09-27 | BLS FIRED | 661.52
2005-09-28 | BLS FIRED | 687.61
2005-09-29 | BLS FIRED | 689.4
2005-09-30 | BLS FIRED | 671.76
19765.23
2005-10-01 | BLS FIRED | 686.02
2005-10-02 | BLS FIRED | 112.63
2005-10-03 | BLS FIRED | 145.23
2005-10-04 | BLS FIRED | 114.24
2005-10-05 | BLS FIRED | 308.99
2005-10-06 | BLS FIRED | 649.83
2005-10-07 | BLS FIRED | 678.48
2005-10-08 | BLS FIRED | 675.76
2005-10-09 | BLS FIRED | 685.98
2005-10-10 | BLS FIRED | 517.24
2005-10-11 | BLS FIRED | 646.79
2005-10-12 | BLS FIRED | 698.27
2005-10-13 | BLS FIRED | 572.23
2005-10-14 | BLS FIRED | 670.48
2005-10-15 | BLS FIRED | 669.95
2005-10-16 | BLS FIRED | 670.24
2005-10-17 | BLS FIRED | 646.79
2005-10-18 | BLS FIRED | 568.57
2005-10-19 | BLS FIRED | 595.49
2005-10-20 | BLS FIRED | 628.82
2005-10-21 | BLS FIRED | 644.64
2005-10-22 | BLS FIRED | 685.64
2005-10-23 | BLS FIRED | 656.96
2005-10-24 | BLS FIRED | 642.72
2005-10-25 | BLS FIRED | 517.43
2005-10-26 | BLS FIRED | 606.65
2005-10-27 | BLS FIRED | 576.93
2005-10-28 | BLS FIRED | 604.21
2005-10-29 | BLS FIRED | 628.43
2005-10-30 | BLS FIRED | 580.55
2005-10-31 | BLS FIRED | 540.03
17626.22
2005-11-01 | BLS FIRED | 577.21
2005-11-02 | BLS FIRED | 617.83
2005-11-03 | BLS FIRED | 661.58
2005-11-04 | BLS FIRED | 616.09
2005-11-05 | BLS FIRED | 592.7
2005-11-06 | BLS FIRED | 462.96
2005-11-07 | BLS FIRED | 667.86
2005-11-08 | BLS FIRED | 593.68
2005-11-09 | BLS FIRED | 593.28
2005-11-10 | BLS FIRED | 577.63
2005-11-11 | BLS FIRED | 560.91
2005-11-12 | BLS FIRED | 571.1
2005-11-13 | BLS FIRED | 635.42
2005-11-14 | BLS FIRED | 639.22
2005-11-15 | BLS FIRED | 638.24
2005-11-16 | BLS FIRED | 543.54
2005-11-17 | BLS FIRED | 552.56
2005-11-18 | BLS FIRED | 531.94
2005-11-19 | BLS FIRED | 580.16
2005-11-20 | BLS FIRED | 627.87
2005-11-21 | BLS FIRED | 501.69
2005-11-22 | BLS FIRED | 436.12
2005-11-23 | BLS FIRED | 388.2
2005-11-24 | BLS FIRED | 587.42
2005-11-25 | BLS FIRED | 623.97
2005-11-26 | BLS FIRED | 644.53
2005-11-27 | BLS FIRED | 669.02
2005-11-28 | BLS FIRED | 646.17
2005-11-29 | BLS FIRED | 663.04
2005-11-30 | BLS FIRED | 678.56
17680.5
2005-12-01 | BLS FIRED | 688.98
2005-12-02 | BLS FIRED | 655.67
2005-12-03 | BLS FIRED | 670.5
2005-12-04 | BLS FIRED | 659.94
2005-12-05 | BLS FIRED | 668.53
2005-12-06 | BLS FIRED | 656.08
2005-12-07 | BLS FIRED | 645.73
2005-12-08 | BLS FIRED | 672.84
2005-12-09 | BLS FIRED | 693.58
2005-12-10 | BLS FIRED | 698.32
2005-12-11 | BLS FIRED | 676.72
2005-12-12 | BLS FIRED | 662.63
2005-12-13 | BLS FIRED | 681.6
2005-12-14 | BLS FIRED | 706.09
2005-12-15 | BLS FIRED | 682.6
2005-12-16 | BLS FIRED | 615.38
2005-12-17 | BLS FIRED | 601.09
2005-12-18 | BLS FIRED | 625.74
2005-12-19 | BLS FIRED | 586.46
2005-12-20 | BLS FIRED | 604.04
2005-12-21 | BLS FIRED | 667.09
2005-12-22 | BLS FIRED | 679.15
2005-12-23 | BLS FIRED | 678.96
2005-12-24 | BLS FIRED | 671.94
2005-12-25 | BLS FIRED | 704.76
2005-12-26 | BLS FIRED | 703.53
2005-12-27 | BLS FIRED | 684.1
2005-12-28 | BLS FIRED | 690.42
2005-12-29 | BLS FIRED | 719.02
2005-12-30 | BLS FIRED | 680.45
2005-12-31 | BLS FIRED | 700.04
20731.98
2006-01-01 | BLS FIRED | 724.71
2006-01-02 | BLS FIRED | 629.76
2006-01-03 | BLS FIRED | 663.38
2006-01-04 | BLS FIRED | 573.15
2006-01-05 | BLS FIRED | 650.43
2006-01-06 | BLS FIRED | 588.58
2006-01-07 | BLS FIRED | 365.42
2006-01-08 | BLS FIRED | 600.96
2006-01-09 | BLS FIRED | 633.52
2006-01-10 | BLS FIRED | 681.19
2006-01-11 | BLS FIRED | 692.14
2006-01-12 | BLS FIRED | 689.03
2006-01-13 | BLS FIRED | 628.01
2006-01-14 | BLS FIRED | 681.53
2006-01-15 | BLS FIRED | 639.1
2006-01-16 | BLS FIRED | 670.38
2006-01-17 | BLS FIRED | 665.77
2006-01-18 | BLS FIRED | 722.19
2006-01-19 | BLS FIRED | 667.53
2006-01-20 | BLS FIRED | 682.1
2006-01-21 | BLS FIRED | 642.92
2006-01-22 | BLS FIRED | 692.25
2006-01-23 | BLS FIRED | 674.96
2006-01-24 | BLS FIRED | 685.55
2006-01-25 | BLS FIRED | 469.87
2006-01-26 | BLS FIRED | 560.95
2006-01-27 | BLS FIRED | 619.06
2006-01-28 | BLS FIRED | 679.93
2006-01-29 | BLS FIRED | 691.41
2006-01-30 | BLS FIRED | 692.25
2006-01-31 | BLS FIRED | 720.59
19978.62
2006-02-01 | BLS FIRED | 694.46
2006-02-02 | BLS FIRED | 716.8
2006-02-03 | BLS FIRED | 665.83
2006-02-04 | BLS FIRED | 663.16
2006-02-05 | BLS FIRED | 668.82
2006-02-06 | BLS FIRED | 687.93
2006-02-07 | BLS FIRED | 627.7
2006-02-08 | BLS FIRED | 608.14
2006-02-09 | BLS FIRED | 593.99
2006-02-10 | BLS FIRED | 678.18
2006-02-11 | BLS FIRED | 671.47
2006-02-12 | BLS FIRED | 690.38
2006-02-13 | BLS FIRED | 703.89
2006-02-14 | BLS FIRED | 672.65
2006-02-15 | BLS FIRED | 684.91
2006-02-16 | BLS FIRED | 713.69
2006-02-17 | BLS FIRED | 698.29
2006-02-18 | BLS FIRED | 692.46
2006-02-19 | BLS FIRED | 704.66
2006-02-20 | BLS FIRED | 688.57
2006-02-21 | BLS FIRED | 696.04
2006-02-22 | BLS FIRED | 693.37
2006-02-23 | BLS FIRED | 701.78
2006-02-24 | BLS FIRED | 644.49
2006-02-25 | BLS FIRED | 698.71
2006-02-26 | BLS FIRED | 693.87
2006-02-27 | BLS FIRED | 682.65
2006-02-28 | BLS FIRED | 674.75
19011.64
2006-03-01 | BLS FIRED | 660.05
2006-03-02 | BLS FIRED | 674.55
2006-03-03 | BLS FIRED | 700.5
2006-03-04 | BLS FIRED | 723.82
2006-03-05 | BLS FIRED | 700.67
2006-03-06 | BLS FIRED | 725.34
2006-03-07 | BLS FIRED | 666.73
2006-03-08 | BLS FIRED | 636.32
2006-03-09 | BLS FIRED | 496.31
2006-03-10 | BLS FIRED | 602.17
2006-03-11 | BLS FIRED | 490.19
2006-03-12 | BLS FIRED | 493.48
2006-03-13 | BLS FIRED | 513.48
2006-03-14 | BLS FIRED | 512.86
2006-03-15 | BLS FIRED | 551
2006-03-16 | BLS FIRED | 560
2006-03-17 | BLS FIRED | 491.6
2006-03-18 | BLS FIRED | 537.11
2006-03-19 | BLS FIRED | 553.98
2006-03-20 | BLS FIRED | 555.58
2006-03-21 | BLS FIRED | 595.95
2006-03-22 | BLS FIRED | 629.94
2006-03-23 | BLS FIRED | 631.3
2006-03-24 | BLS FIRED | 607.52
2006-03-25 | BLS FIRED | 676.42
2006-03-26 | BLS FIRED | 693.91
2006-03-27 | BLS FIRED | 691.53
2006-03-28 | BLS FIRED | 700.03
2006-03-29 | BLS FIRED | 475.71
2006-03-30 | BLS FIRED | 488.3
2006-03-31 | BLS FIRED | 491.43
18527.78
2006-04-01 | BLS FIRED | 596.44
2006-04-02 | BLS FIRED | 663.91
2006-04-03 | BLS FIRED | 683.23
2006-04-04 | BLS FIRED | 307.58
2006-04-10 | BLS FIRED | 702.81
2006-04-11 | BLS FIRED | 691.1
2006-04-12 | BLS FIRED | 626.91
2006-04-13 | BLS FIRED | 626.48
2006-04-14 | BLS FIRED | 675.22
2006-04-15 | BLS FIRED | 630.32
2006-04-16 | BLS FIRED | 683.75
2006-04-17 | BLS FIRED | 706.2
2006-04-18 | BLS FIRED | 695.36
2006-04-19 | BLS FIRED | 703.13
2006-04-20 | BLS FIRED | 714.35
2006-04-21 | BLS FIRED | 643.78
2006-04-22 | BLS FIRED | 721.27
2006-04-23 | BLS FIRED | 693.87
2006-04-24 | BLS FIRED | 680.44
2006-04-25 | BLS FIRED | 689.94
2006-04-26 | BLS FIRED | 657.77
2006-04-27 | BLS FIRED | 681.53
2006-04-28 | BLS FIRED | 695.23
2006-04-29 | BLS FIRED | 745.1
2006-04-30 | BLS FIRED | 739.9
16655.62
2006-05-01 | BLS FIRED | 735.82
2006-05-02 | BLS FIRED | 614.3
2006-05-03 | BLS FIRED | 701.48
2006-05-04 | BLS FIRED | 706.63
2006-05-05 | BLS FIRED | 704.67
2006-05-06 | BLS FIRED | 542.26
2006-05-07 | BLS FIRED | 633.82
2006-05-08 | BLS FIRED | 656.65
2006-05-09 | BLS FIRED | 516.82
2006-05-10 | BLS FIRED | 655.55
2006-05-11 | BLS FIRED | 660.6
2006-05-12 | BLS FIRED | 677.85
2006-05-13 | BLS FIRED | 675.89
2006-05-14 | BLS FIRED | 639.42
2006-05-15 | BLS FIRED | 706.12
2006-05-16 | BLS FIRED | 683.08
2006-05-17 | BLS FIRED | 594.83
2006-05-18 | BLS FIRED | 638.42
2006-05-19 | BLS FIRED | 578.85
2006-05-20 | BLS FIRED | 639.09
2006-05-21 | BLS FIRED | 650.43
2006-05-22 | BLS FIRED | 711.32
2006-05-23 | BLS FIRED | 682.45
2006-05-24 | BLS FIRED | 701.92
2006-05-25 | BLS FIRED | 651.68
2006-05-26 | BLS FIRED | 641.72
2006-05-27 | BLS FIRED | 678.91
2006-05-28 | BLS FIRED | 653.75
2006-05-29 | BLS FIRED | 669.5
2006-05-30 | BLS FIRED | 682.1
2006-05-31 | BLS FIRED | 708.36
20394.29
2006-06-01 | BLS FIRED | 713.97
2006-06-02 | BLS FIRED | 596.63
2006-06-03 | BLS FIRED | 694.27
2006-06-04 | BLS FIRED | 697.25
2006-06-05 | BLS FIRED | 725.85
2006-06-06 | BLS FIRED | 732.16
2006-06-07 | BLS FIRED | 712.42
2006-06-08 | BLS FIRED | 704.4
2006-06-09 | BLS FIRED | 653.19
2006-06-10 | BLS FIRED | 716.88
2006-06-11 | BLS FIRED | 716.09
2006-06-12 | BLS FIRED | 739.21
2006-06-13 | BLS FIRED | 697.93
2006-06-14 | BLS FIRED | 713.36
2006-06-15 | BLS FIRED | 697.25
2006-06-16 | BLS FIRED | 703.16
2006-06-17 | BLS FIRED | 725.01
2006-06-18 | BLS FIRED | 689.56
2006-06-19 | BLS FIRED | 751.69
2006-06-20 | BLS FIRED | 726.78
2006-06-21 | BLS FIRED | 726.69
2006-06-22 | BLS FIRED | 731.53
2006-06-23 | BLS FIRED | 729.31
2006-06-24 | BLS FIRED | 328.74
2006-06-25 | BLS FIRED | 564.11
2006-06-26 | BLS FIRED | 725.79
2006-06-27 | BLS FIRED | 726.15
2006-06-28 | BLS FIRED | 728.16
2006-06-29 | BLS FIRED | 723.36
2006-06-30 | BLS FIRED | 724.59
20815.49
2006-07-01 | BLS FIRED | 714.7
2006-07-02 | BLS FIRED | 725.85
2006-07-03 | BLS FIRED | 731.74
2006-07-04 | BLS FIRED | 733.74
2006-07-05 | BLS FIRED | 671.3
2006-07-06 | BLS FIRED | 669.24
2006-07-07 | BLS FIRED | 461.99
2006-07-08 | BLS FIRED | 513
2006-07-09 | BLS FIRED | 622.95
2006-07-10 | BLS FIRED | 642.85
2006-07-11 | BLS FIRED | 648.28
2006-07-12 | BLS FIRED | 648.33
2006-07-13 | BLS FIRED | 640.74
2006-07-14 | BLS FIRED | 651.97
2006-07-15 | BLS FIRED | 563.89
2006-07-16 | BLS FIRED | 466.37
2006-07-17 | BLS FIRED | 596.76
2006-07-18 | BLS FIRED | 695.77
2006-07-19 | BLS FIRED | 716.1
2006-07-20 | BLS FIRED | 647.95
2006-07-21 | BLS FIRED | 695.06
2006-07-22 | BLS FIRED | 598.08
2006-07-23 | BLS FIRED | 648.45
2006-07-24 | BLS FIRED | 690.54
2006-07-25 | BLS FIRED | 679.59
2006-07-26 | BLS FIRED | 694
2006-07-27 | BLS FIRED | 698.5
2006-07-28 | BLS FIRED | 677.24
2006-07-29 | BLS FIRED | 714.31
2006-07-30 | BLS FIRED | 718.07
2006-07-31 | BLS FIRED | 698.72
20276.08
2006-08-01 | BLS FIRED | 735.39
2006-08-02 | BLS FIRED | 717.42
2006-08-03 | BLS FIRED | 722.08
2006-08-04 | BLS FIRED | 0
2006-08-05 | BLS FIRED | 0
2006-08-06 | BLS FIRED | 596.6
2006-08-07 | BLS FIRED | 596.6
2006-08-08 | BLS FIRED | 663.04
2006-08-09 | BLS FIRED | 693.34
2006-08-10 | BLS FIRED | 693.14
2006-08-11 | BLS FIRED | 629.74
2006-08-12 | BLS FIRED | 550.85
2006-08-13 | BLS FIRED | 661.96
2006-08-14 | BLS FIRED | 674.95
2006-08-15 | BLS FIRED | 691.83
2006-08-16 | BLS FIRED | 682.7
2006-08-17 | BLS FIRED | 667.52
2006-08-18 | BLS FIRED | 653.28
2006-08-19 | BLS FIRED | 660.72
2006-08-20 | BLS FIRED | 659.11
2006-08-21 | BLS FIRED | 589.58
2006-08-22 | BLS FIRED | 630.49
2006-08-23 | BLS FIRED | 639.53
2006-08-24 | BLS FIRED | 637.36
2006-08-25 | BLS FIRED | 656.18
2006-08-26 | BLS FIRED | 660.82
2006-08-27 | BLS FIRED | 656.3
2006-08-28 | BLS FIRED | 653.71
2006-08-29 | BLS FIRED | 621.61
2006-08-30 | BLS FIRED | 604.3
2006-08-31 | BLS FIRED | 624.83
18924.98
2006-09-01 | BLS FIRED | 659.59
2006-09-02 | BLS FIRED | 674.85
2006-09-03 | BLS FIRED | 463.91
2006-09-04 | BLS FIRED | 626.35
2006-09-05 | BLS FIRED | 705.97
2006-09-06 | BLS FIRED | 731.74
2006-09-07 | BLS FIRED | 678.24
2006-09-08 | BLS FIRED | 696.43
2006-09-09 | BLS FIRED | 715.09
2006-09-10 | BLS FIRED | 734.14
2006-09-11 | BLS FIRED | 733.32
2006-09-12 | BLS FIRED | 659.99
2006-09-13 | BLS FIRED | 694.08
2006-09-14 | BLS FIRED | 618.56
2006-09-15 | BLS FIRED | 721.2
2006-09-16 | BLS FIRED | 628.75
2006-09-17 | BLS FIRED | 697.07
2006-09-18 | BLS FIRED | 664.38
2006-09-19 | BLS FIRED | 695.69
2006-09-20 | BLS FIRED | 724.46
2006-09-21 | BLS FIRED | 689.82
2006-09-22 | BLS FIRED | 679.57
2006-09-23 | BLS FIRED | 676.66
2006-09-24 | BLS FIRED | 681.59
2006-09-25 | BLS FIRED | 694.92
2006-09-26 | BLS FIRED | 607.77
2006-09-27 | BLS FIRED | 671.06
2006-09-28 | BLS FIRED | 685.68
2006-09-29 | BLS FIRED | 591.98
2006-09-30 | BLS FIRED | 624.77
20127.63
2006-10-01 | BLS FIRED | 684.92
2006-10-02 | BLS FIRED | 691.43
2006-10-03 | BLS FIRED | 529.83
2006-10-04 | BLS FIRED | 467.08
2006-10-05 | BLS FIRED | 604.77
2006-10-06 | BLS FIRED | 677.98
2006-10-07 | BLS FIRED | 690.53
2006-10-08 | BLS FIRED | 680.28
2006-10-09 | BLS FIRED | 698.5
2006-10-10 | BLS FIRED | 700
2006-10-11 | BLS FIRED | 698.4
2006-10-12 | BLS FIRED | 544.71
2006-10-13 | BLS FIRED | 707.95
2006-10-14 | BLS FIRED | 692.73
2006-10-15 | BLS FIRED | 702.81
2006-10-16 | BLS FIRED | 705.79
2006-10-17 | BLS FIRED | 730.49
2006-10-18 | BLS FIRED | 593.9
2006-10-19 | BLS FIRED | 732.38
2006-10-20 | BLS FIRED | 728.68
2006-10-21 | BLS FIRED | 715.75
2006-10-22 | BLS FIRED | 779.99
2006-10-23 | BLS FIRED | 784.85
2006-10-24 | BLS FIRED | 742.67
2006-10-25 | BLS FIRED | 766.25
2006-10-26 | BLS FIRED | 763.57
2006-10-27 | BLS FIRED | 788.62
2006-10-28 | BLS FIRED | 728.56
2006-10-29 | BLS FIRED | 756.7
2006-10-30 | BLS FIRED | 744.91
2006-10-31 | BLS FIRED | 751.15
21586.18
2006-11-01 | BLS FIRED | 767.15
2006-11-02 | BLS FIRED | 751.34
2006-11-03 | BLS FIRED | 710.72
2006-11-04 | BLS FIRED | 686.64
2006-11-05 | BLS FIRED | 722.56
2006-11-06 | BLS FIRED | 683.79
2006-11-07 | BLS FIRED | 742.89
2006-11-08 | BLS FIRED | 728.53
2006-11-09 | BLS FIRED | 719.33
2006-11-10 | BLS FIRED | 701.57
2006-11-11 | BLS FIRED | 738.36
2006-11-12 | BLS FIRED | 756.4
2006-11-13 | BLS FIRED | 660.24
2006-11-14 | BLS FIRED | 676.13
2006-11-15 | BLS FIRED | 714.83
2006-11-16 | BLS FIRED | 692.73
2006-11-17 | BLS FIRED | 674.56
2006-11-18 | BLS FIRED | 700.03
2006-11-19 | BLS FIRED | 721.98
2006-11-20 | BLS FIRED | 747.86
2006-11-21 | BLS FIRED | 731.13
2006-11-22 | BLS FIRED | 0
2006-11-23 | BLS FIRED | 0
2006-11-24 | BLS FIRED | 0
2006-11-25 | BLS FIRED | 0
2006-11-26 | BLS FIRED | 378.47
2006-11-27 | BLS FIRED | 548.5
2006-11-28 | BLS FIRED | 630.5
2006-11-29 | BLS FIRED | 685.52
2006-11-30 | BLS FIRED | 593.81
17865.57
2006-12-01 | BLS FIRED | 538.69
2006-12-02 | BLS FIRED | 617.65
2006-12-03 | BLS FIRED | 659.51
2006-12-04 | BLS FIRED | 702.91
2006-12-05 | BLS FIRED | 720.4
2006-12-06 | BLS FIRED | 663.86
2006-12-07 | BLS FIRED | 703.14
2006-12-08 | BLS FIRED | 692.63
2006-12-09 | BLS FIRED | 644.69
2006-12-10 | BLS FIRED | 673.06
2006-12-11 | BLS FIRED | 668.82
2006-12-12 | BLS FIRED | 664.43
2006-12-13 | BLS FIRED | 635.48
2006-12-14 | BLS FIRED | 696.92
2006-12-15 | BLS FIRED | 708.32
2006-12-16 | BLS FIRED | 657.13
2006-12-17 | BLS FIRED | 668.55
2006-12-18 | BLS FIRED | 624.47
2006-12-19 | BLS FIRED | 684.99
2006-12-20 | BLS FIRED | 652.22
2006-12-21 | BLS FIRED | 690.57
2006-12-22 | BLS FIRED | 702.58
2006-12-23 | BLS FIRED | 719.71
2006-12-24 | BLS FIRED | 731.18
2006-12-25 | BLS FIRED | 745.84
2006-12-26 | BLS FIRED | 744.57
2006-12-27 | BLS FIRED | 693.36
2006-12-28 | BLS FIRED | 644.07
2006-12-29 | BLS FIRED | 673.92
2006-12-30 | BLS FIRED | 663.47
2006-12-31 | BLS FIRED | 679.62
20966.76

## Sep 03
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Stot-in-power | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy | Total feed water consumed in the month | Net Enthalpy at the boiler End | Fuel Cons. | Net Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for the Fuel mix used
Description | Total Steam Generaed by the boilwer for power generation | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | L | M | N=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 8289 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 5358.8385 |  |  | 57.1 | 600
CFB2 | 8333 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 5387.2845 |  |  | 57.1 | 482
CFB3 | 9404 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 5711.0492 |  |  | 57.1 | 612
CFB1,2&3 | 26026 | [6 empty] | 5383 | 5415.1806 | 16457.1722 | 29149.9172 |  | 57.1 |  | 90.6451
CFB4 | 31764 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5586 | 5401.1806 | 21755.1636 | 30170.9948 |  | 57.1 | 720 | 90.8801
CFB5 | 49827 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8658 | 5380.0804 | 34126.5123 | 46580.7361 |  | 57.1 | 638 | 91.2365
SRB3 | 45295 | 64 | 460 | 793.1 | 130 |  | 663.1 | 15820.54 | 3550 | 30035.1145 | 56162.917 |  |  | 660
TOTAL | 152912 |  |  | 777.2 | 121.6667 | 130244 | 673.5695 |  |  | 102373.9626 | 162064.5651 | 63.1686 |  | 0.1778 | 90.9206
[9 empty] | 5398.8139 | [5 empty] | 74.7547

## Oct 03
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy | Total feed water consumed in the month | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 3863 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 2497.4295 | 0 |  | 56.2 | 490 | 0
CFB2 | 8183 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 5290.3095 | 0 |  | 56.2 | 638 | 0
CFB3 | 5246 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 3185.8958 | 0 |  | 56.2 | 315 | 0
CFB1,2&3 | 17292 | [6 empty] | 3592 | 5362.1806 | 10973.6348 | 19260.9527 |  | 56.2 |  | 90.0982
CFB4 | 30444 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5361 | 5310.88 | 20851.0956 | 28471.6277 |  | 56.2 | 736 | 90.9685
CFB5 | 58242 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 10439 | 5293.6796 | 39889.9458 | 55260.7213 |  | 56.2 | 744 | 91.2641
SRB3 | 51073 | 64 | 460 | 793.1 | 130 |  | 663.1 | 19059.87 | 3550 | 33866.5063 | 67662.5385 |  |  | 737
TOTAL | 157051 |  |  | 777.2 | 121.6667 | 132622 | 674.4584 |  |  | 105581.1825 | 170655.8402 | 61.8679 |  | 0.20137 | 90.7769
[9 empty] | 5322.2467 | [5 empty] | 72.4975

## Nov 03
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy | Total feed water consumed in the month | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 3278 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 2119.227 | 0 |  | 57.9 | 357 | 0
CFB2 | 8043 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 5199.7995 | 0 |  | 57.9 | 705 | 0
CFB3 | 7489 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 4548.0697 | 0 |  | 57.9 | 518 | 0
CFB1,2&3 | 18810 | [6 empty] | 3796 | 5432.6816 | 11867.0962 | 20622.4594 |  | 57.9 |  | 91.619
CFB4 | 30272 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5298 | 5381.0804 | 20733.2928 | 28508.964 |  | 57.9 | 720 | 92.4976
CFB5 | 49993 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8709 | 5382.88 | 34240.2057 | 46879.5019 |  | 57.9 | 720 | 92.4666
SRB3 | 49408 | 64 | 460 | 793.1 | 130 |  | 663.1 | 18458.68 | 3550 | 32762.4448 | 65528.314 |  |  | 683.42
TOTAL | 148483 |  |  | 777.2 | 121.6667 | 132260 | 668.8264 |  |  | 99603.0395 | 161539.2392 | 61.6587 |  | 0.18454 | 92.1944
[9 empty] | 5398.8807 | [5 empty] | 75.1811

## Dec 03
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy | Total feed water consumed in the month | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | L | M | N=(L*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 5703 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 3686.9895 |  |  | 59.8 | 484
CFB2 | 3542 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 2289.903 |  |  | 59.8 | 387
CFB3 | 11423 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 6937.1879 |  |  | 59.8 | 718
CFB1,2&3 | 20668 | [6 empty] | 4293 | 5456.2788 | 12914.0804 | 23423.8049 |  | 59.8 |  | 94.2163
CFB4 | 31195 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5362 | 5436.0784 | 21365.4555 | 29148.2524 |  | 59.8 | 740 | 94.5664
CFB5 | 54700 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 9277 | 5425.0784 | 37464.03 | 50328.4523 |  | 59.8 | 744 | 94.7581
SRB3 | 54274 | 64 | 460 | 793.1 | 130 |  | 663.1 | 19483.07 | 3550 | 35989.0894 | 69164.8985 |  |  | 671
TOTAL | 160837 |  |  | 777.2 | 121.6667 | 138390 | 672.5136 |  |  | 107732.6553 | 172065.4081 | 62.6115 |  | 0.17922 | 94.5136
[9 empty] | 5439.1452 | [5 empty] | 77.5748

## Jan 04
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 703 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 454.4895 |  |  | 59.4 | 95 | 0
CFB2 | 7016 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 4535.844 |  |  | 59.4 | 525 | 0
CFB3 | 9293 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 5643.6389 |  |  | 59.4 | 514 | 0
CFB1,2&3 | 17012 | [6 empty] | 3474 | 5424.2788 | 10633.9724 | 18843.9446 |  | 59.4 |  | 94.1382
CFB4 | 31086 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5435 | 5424.6796 | 21290.8014 | 29483.1336 |  | 59.4 | 744 | 94.1312
CFB5 | 55035 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 9417 | 5437.379 | 37693.4715 | 51203.798 |  | 59.4 | 744 | 93.9113
SRB3 | 56179 | 64 | 460 | 793.1 | 130 |  | 663.1 | 19923.43 | 3550 | 37252.2949 | 70728.1765 |  |  | 744
TOTAL | 159312 |  |  | 777.2 | 121.6667 | 124752 | 681.9268 |  |  | 106870.5402 | 170259.0527 | 62.7694 |  | 0.22103 | 94.0602
[9 empty] | 5428.7791 | [5 empty] | 73.2697

## Feb 04
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 231 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 149.3415 | 0 |  | 60 | 16 | 0
CFB2 | 6249 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 4039.9785 | 0 |  | 60 | 546 | 0
CFB3 | 9599 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 5829.4727 | 0 |  | 60 | 630 | 0
CFB1,2&3 | 16079 | [6 empty] | 3235 | 5469.2808 | 10018.7927 | 17693.1234 |  | 60 |  | 94.3066
CFB4 | 28959 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 4971 | 5454.0804 | 19834.0191 | 27112.2337 |  | 60 | 696 | 94.5695
CFB5 | 50697 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8641 | 5456.0804 | 34722.3753 | 47145.9907 |  | 60 | 696 | 94.5348
SRB3 | 51961 | 64 | 460 | 793.1 | 130 |  | 663.1 | 17793 | 3550 | 34455.3391 | 63165.15 |  |  | 669.75
TOTAL | 147696 |  |  | 777.2 | 121.6667 | 127388 | 672.2623 |  |  | 99030.5262 | 155116.4978 | 63.8427 |  | 0.20584 | 94.4703
[9 empty] | 5459.8139 | [5 empty] | 75.0246

## Mar 04
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 2314 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1496.001 |  |  | 60.2 | 368 | 0
CFB2 | 3245 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 2097.8925 |  |  | 60.2 | 317 | 0
CFB3 | 9309 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 5653.3557 |  |  | 60.2 | 603 | 0
CFB1,2&3 | 14868 | [6 empty] | 3022 | 5468.7818 | 9247.2492 | 16526.6586 |  | 60.2 |  | 94.6296
CFB4 | 31516 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5413 | 5462.6816 | 21585.3084 | 29569.4955 |  | 60.2 | 744 | 94.7353
CFB5 | 54263 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 9143 | 5458.381 | 37164.7287 | 49905.9775 |  | 60.2 | 744 | 94.8099
SRB3 | 53529 | 64 | 460 | 793.1 | 130 |  | 663.1 | 19172.37 | 3550 | 35495.0799 | 68061.9135 |  |  | 728.17
TOTAL | 154176 |  |  | 777.2 | 121.6667 | 136369 | 669.5856 |  |  | 103492.3662 | 164064.0451 | 63.0805 |  | 0.2078 | 94.725
[9 empty] | 5463.2815 | [5 empty] | 75.041

## Apr 04
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Net Output Energy | Fuel Cons. | Calorific value | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy |  | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | C | M | M,C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  |  | Monthly |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | I=A*F | G | H | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | Mkcal | MT | Kcal/kg | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES |  | UTR004 | CLR012 |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | ENCON | UTY S/I | C.LAB | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 2383 | 42 | 405 | 766.5 | 120 |  | 646.5 | 1540.6095 |  |  | 0 |  | 57.4 | 445 | 0
CFB2 | 4828 | 42 | 405 | 766.5 | 120 |  | 646.5 | 3121.302 |  |  | 0 |  | 57.4 | 617 | 0
CFB3 | 8620 | 11 | 300 | 727.3 | 120 |  | 607.3 | 5234.926 |  |  | 0 |  | 57.4 | 508 | 0
CFB1,2&3 | 15831 | [6 empty] | 9896.8375 | 3292 | 5464.7818 | 17990.0617 |  | 57.4 |  | 90.2943
CFB4 | 29624 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 20289.4776 | 5041 | 5468.9822 | 27569.1393 |  | 57.4 | 720 | 90.2249
CFB5 | 53137 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 36393.5313 | 9248 | 5451.7818 | 50418.0781 |  | 57.4 | 720 | 90.5096
SRB3 | 52005 | 64 | 460 | 793.1 | 130 |  | 663.1 | 34484.5155 | 18677 | 3060 | 57151.62 |  |  | 719.67
TOTAL | 150597 |  |  | 777.2 | 121.6667 | 140428 | 663.7488 | 101064.3619 |  |  | 153128.899 | 65.9995 |  | 0.19296 | 90.3429
[10 empty] | 5461.8486 |  |  |  |  | 72.9105

## May 04
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Net Output Energy | Fuel Cons. | Calorific value | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy |  | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | C | M | M,C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  |  | Monthly |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | I=A*F | G | H | J=G*H | K=I/J | L | M | N=(O*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | Mkcal | MT | Kcal/kg | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES |  | UTR004 | CLR012 |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | ENCON | UTY S/I | C.LAB | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 2701 | 42 | 405 | 766.5 | 120 |  | 646.5 | 1746.1965 |  |  | 0 |  | 56.2 | 528
CFB2 | 6077 | 42 | 405 | 766.5 | 120 |  | 646.5 | 3928.7805 |  |  | 0 |  | 56.2 | 689
CFB3 | 1431 | 11 | 300 | 727.3 | 120 |  | 607.3 | 869.0463 |  |  | 0 |  | 56.2 | 116
CFB1,2&3 | 10209 | [6 empty] | 6544.0233 | 1988 | 5423.9822 | 10782.8766
CFB4 | 12437 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8518.1013 | 2035 | 5430.0824 | 11050.2177 |  | 56.2 | 495 | 88.9715
CFB5 | 47116 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 32269.7484 | 7704 | 5451.7818 | 42000.527 |  | 56.2 | 744 | 88.6174
CFB6 | 35509 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 23965.0241 | 6002 | 5441.882 | 32662.1758 |  | 56.2 | 615 | 88.7786
SRB3 | 56020 | 64 | 460 | 793.1 | 130 |  | 663.1 | 37146.862 | 20023 | 3060 | 61270.38 |  |  | 700.08
TOTAL | 161291 |  |  | 781.1571 | 122.8571 | 140818 | 673.8945 | 108443.7591 |  |  | 146983.3004 | 73.7796 |  | 0.1801 | 88.7892
[10 empty] | 5436.9321 |  |  |  |  | 72.7979

## Jun 04
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Net Output Energy | Fuel Cons. | Calorific value | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy |  | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | C | M | M,C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  |  | Monthly |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | I=A*F | G | H | J=G*H | K=I/J | L | M | N=(O*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | Mkcal | MT | Kcal/kg | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES |  | UTR004 | CLR012 |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | ENCON | UTY S/I | C.LAB | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 3282 | 42 | 405 | 766.5 | 120 |  | 646.5 | 2121.813 |  |  |  |  | 55.2 | 483
CFB2 | 4260 | 42 | 405 | 766.5 | 120 |  | 646.5 | 2754.09 |  |  |  |  | 55.2 | 495
CFB3 | 1494 | 11 | 300 | 727.3 | 120 |  | 607.3 | 907.3062 |  |  |  |  | 55.2 | 189
CFB1,2&3 | 9036 | [6 empty] | 5783.2092 | 1964 | 5365.7798 | 10538.3915 |  | 55.2 |  | 88.4357
CFB4 | 23654 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 16200.6246 | 4083 | 5353.9802 | 21860.3012 |  | 55.2 | 676 | 88.6306
CFB5 | 45339 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 31052.6811 | 7894 | 5346.9802 | 42209.0617 |  | 55.2 | 720 | 88.7466
CFB6 | 37675 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 25426.8575 | 6587 | 5335.88 | 35147.4416 |  | 55.2 | 655 | 88.9312
SRB3 | 52840 | 64 | 460 | 793.1 | 130 |  | 663.1 | 35038.204 | 18712 | 3000 | 56136 |  |  | 702.17
TOTAL | 168544 |  |  | 781.1571 | 122.8571 | 144601 | 675.7528 | 113501.5764 |  |  | 155352.8044 | 73.0605 |  | 0.17912 | 88.686
[10 empty] | 5350.6551 |  |  |  |  | 72.8008

## July 04
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Net Output Energy | Fuel Cons. | Calorific value | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy |  | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | C | M | M,C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  |  | Monthly |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | I=A*F | G | H | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | Mkcal | MT | Kcal/kg | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES |  | UTR004 | CLR012 |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | ENCON | UTY S/I | C.LAB | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 6051 | 42 | 405 | 766.5 | 120 |  | 646.5 | 3911.9715 |  |  | 0 |  | 59.1 | 471
CFB2 | 5859 | 42 | 405 | 766.5 | 120 |  | 646.5 | 3787.8435 |  |  | 0 |  | 59.1 | 424
CFB3
CFB1,2&3 | 11910 | [6 empty] | 7699.815 | 2467 | 5260.1806 | 12976.8655 |  | 59.1 |  | 96.5846
CFB4 | 29296 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 20064.8304 | 5492 | 4954.9802 | 27212.7513 |  | 59.1 | 744 | 102.5337
CFB5 | 21648 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 14826.7152 | 4043 | 4980.381 | 20135.6804 |  | 59.1 | 358 | 102.0108
CFB6 | 50700 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 34217.43 | 8937 | 5223.2808 | 46680.4605 |  | 59.1 | 744 | 97.267
SRB3 | 56805 | 64 | 460 | 793.1 | 130 |  | 663.1 | 37667.3955 | 19838.01 | 3000 | 59514.03 |  |  | 743.92
TOTAL | 170359 |  |  | 790.1333 | 123.3333 | 148762 | 682.4354 | 114476.1861 |  | 116259.0112 | 153542.9222 | 74.5565 |  | 0.21347 | 99.599
[10 empty] | 5104.7056 |  |  |  |  | 78.3378

## Aug 04
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Net Output Energy | Fuel Cons. | Calorific value | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy |  | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | C | M | M,C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  |  | Monthly |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | I=A*F | G | H | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | Mkcal | MT | Kcal/kg | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES |  | UTR004 | CLR012 |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | ENCON | UTY S/I | C.LAB | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 5596 | 42 | 405 | 766.5 | 120 |  | 646.5 | 3617.814 |  |  | 0 |  | 59.1 | 403
CFB2 | 6894 | 42 | 405 | 766.5 | 120 |  | 646.5 | 4456.971 |  |  | 0 |  | 59.1 | 480
CFB3
CFB1,2&3 | 12490 | [6 empty] | 8074.785 | 2994 | 4850.4792 | 14522.3347 |  | 59.1 |  | 104.7428
CFB4 | 13589 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 9307.1061 | 2638 | 4638.88 | 12237.3654 |  | 59.1 | 341 | 109.5205
CFB5 | 50041 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 34273.0809 | 9748 | 4654.88 | 45375.7702 |  | 59.1 | 744 | 109.1441
CFB6 | 34557 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 23322.5193 | 6577 | 4765.6796 | 31343.8747 |  | 59.1 | 507 | 106.6065
SRB3 | 52948 | 64 | 460 | 793.1 | 130 |  | 663.1 | 35109.8188 | 18348.99 | 2838.35 | 52080.8558 |  |  | 743.5
TOTAL | 163625 |  |  | 790.1333 | 123.3333 | 161932 | 668.0761 | 110087.3101 |  | 109313.9533 | 141037.8662 | 78.0551 |  | 0.23101 | 107.5035
[10 empty] | 4727.4797 |  |  |  |  | 82.6693

## Sep 04
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Net Output Energy | Fuel Cons. | Calorific value | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy |  | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | C | M | M,C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  |  | Monthly |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | I=A*F | G | H | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | Mkcal | MT | Kcal/kg | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES |  | UTR004 | CLR012 |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | ENCON | UTY S/I | C.LAB | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 3688 | 42 | 405 | 766.5 | 120 |  | 646.5 | 2384.292 |  |  |  |  | 45.6 | 386
CFB2 | 1971 | 42 | 405 | 766.5 | 120 |  | 646.5 | 1274.2515 |  |  |  |  | 45.6 | 202
CFB3 | [12 empty] | 45.6
CFB1,2&3 | 5659 | [6 empty] | 3658.5435 | 1395 | 4565.1806 | 6368.4269 |  | 45.6 |  | 85.8674
CFB4 | 19461 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 13328.8389 | 3815 | 4595.882 | 17533.2898 |  | 45.6 | 528 | 85.2937
CFB5 | 43618 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 29873.9682 | 8310 | 4715.9822 | 39189.8121 |  | 45.6 | 720 | 83.1216
CFB6 | 45242 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 30533.8258 | 8364 | 4709.7818 | 39392.615 |  | 45.6 | 720 | 83.231
SRB3 | 48220 | 64 | 460 | 793.1 | 130 |  | 663.1 | 31974.682 | 16110 | 3000 | 48330 |  |  | 622.08
TOTAL | 162200 |  |  | 790.1333 | 123.3333 | 146765 | 678.5364 | 109369.8584 |  |  | 144445.7169 | 75.7169 |  | 0.19574 | 84.3784
[10 empty] | 4646.7067 |  |  |  |  | 67.8621

## Oct 04
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Net Output Energy | Fuel Cons. | Calorific value | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy |  | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | C | M | M,C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  |  | Monthly |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | I=A*F | G | H | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | Mkcal | MT | Kcal/kg | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES |  | UTR004 | CLR012 |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | ENCON | UTY S/I | C.LAB | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 3304 | 42 | 405 | 766.5 | 120 |  | 646.5 | 2136.036 |  |  | 0 |  | 45.9 | 301
CFB2 | 1629 | 42 | 405 | 766.5 | 120 |  | 646.5 | 1053.1485 |  |  | 0 |  | 45.9 | 163
CFB3 | 596 | 11 | 300 | 727.3 | 120 |  | 607.3 | 361.9508 |  |  | 0 |  | 45.9 | 122
CFB1,2&3 | 5529 | [6 empty] | 3551.1353 | 1322 | 4751.381 | 6281.3257 |  | 45.9 |  | 83.0451
CFB4 | 23208 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 15895.1592 | 4387 | 4813.381 | 21116.3024 |  | 45.9 | 678 | 81.9754
CFB5 | 43114 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 29528.7786 | 8032 | 4902.1806 | 39374.3146 |  | 45.9 | 711 | 80.4905
CFB6 | 40805 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 27539.2945 | 7356 | 4991.0804 | 36714.3874 |  | 45.9 | 642 | 79.0568
SRB3 | 55051 | 64 | 460 | 793.1 | 130 |  | 663.1 | 36504.3181 | 18833.51 | 3000 | 56500.53 |  |  | 740.33
TOTAL | 167707 |  |  | 781.1571 | 122.8571 | 159279 | 664.4741 | 113018.6857 |  |  | 153705.5344 | 73.5294 |  | 0.22051 | 81.142
[10 empty] | 4864.5058 |  |  |  |  | 63.2492

## Nov 04
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Net Output Energy | Fuel Cons. | Calorific value | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy |  | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | C | M | M,C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  |  | Monthly |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | I=A*F | G | H | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | Mkcal | MT | Kcal/kg | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES |  | UTR004 | CLR012 |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | ENCON | UTY S/I | C.LAB | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 258 | 42 | 405 | 766.5 | 120 |  | 646.5 | 166.797 |  |  | 0 |  | 54.1 | 33
CFB2 | 759 | 42 | 405 | 766.5 | 120 |  | 646.5 | 490.6935 |  |  | 0 |  | 54.1 | 56
CFB3
CFB1,2&3 | 1017 | [6 empty] | 657.4905 | 271 | 4820.5794 | 1306.377 |  | 54.1 |  | 96.476
CFB4 | 27878 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 19093.6422 | 5245 | 4857.0804 | 25475.3867 |  | 54.1 | 720 | 95.751
CFB5 | 43024 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 29467.1376 | 8040 | 4841.1806 | 38923.092 |  | 54.1 | 720 | 96.0654
CFB6 | 49415 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 33350.1835 | 8988 | 4953.2808 | 44520.0878 |  | 54.1 | 684 | 93.8913
SRB3 | 51896 | 64 | 460 | 793.1 | 130 |  | 663.1 | 34412.2376 | 17917.94 | 3000 | 53753.82 |  |  | 696.42
TOTAL | 173230 |  |  | 790.1333 | 123.3333 | 159623 | 676.4877 | 116980.6914 |  |  | 162672.3866 | 71.9118 |  | 0.23937 | 95.5459
[10 empty] | 4868.0303 |  |  |  |  | 72.6754

## Dec 04
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Net Output Energy | Fuel Cons. | Calorific value | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy |  | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | C | M | M,C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  |  | Monthly |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | I=A*F | G | H | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | Mkcal | MT | Kcal/kg | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES |  | UTR004 | CLR012 |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | ENCON | UTY S/I | C.LAB | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 3097 | 42 | 405 | 766.5 | 120 |  | 646.5 | 2002.2105 |  |  | 0 |  | 47.5 | 258
CFB2 | 2972 | 42 | 405 | 766.5 | 120 |  | 646.5 | 1921.398 |  |  | 0 |  | 47.5 | 258
CFB3 | 1340 | 11 | 300 | 727.3 | 120 |  | 607.3 | 813.782 |  |  | 0 |  | 47.5 | 58
CFB1,2&3 | 7409 | [6 empty] | 4737.3905 | 1483 | 4656.0804 | 6904.9672 |  | 47.5 |  | 87.6989
CFB4 | 24852 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 17021.1348 | 4799 | 4619.88 | 22170.8041 |  | 47.5 | 651 | 88.3861
CFB5 | 49725 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 34056.6525 | 9470 | 4725.88 | 44754.0836 |  | 47.5 | 744 | 86.4037
CFB6 | 42621 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 28764.9129 | 7858 | 4794.9802 | 37678.9544 |  | 47.5 | 590 | 85.1585
SRB3 | 56291 | 64 | 460 | 793.1 | 130 |  | 663.1 | 37326.5621 | 19312.67 | 3000 | 57938.01 |  |  | 743.25
TOTAL | 180898 |  |  | 781.1571 | 122.8571 | 171317 | 664.807 | 121906.6528 |  |  | 162541.8521 | 75.0002 |  | 0.22507 | 86.9118
[10 empty] | 4699.2051 |  |  |  |  | 67.3502

## Jan 05
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 402 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 259.893 | 0 |  | 54.2 | 47
CFB2 | 5073 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 3279.6945 | 0 |  | 54.2 | 369
CFB3
CFB1,2&3 | 5475 | [6 empty] | 1330 | 5175.9782 | 3539.5875 | 6884.051 | 51.4172 | 54.2 |  | 90.0177
CFB4 | 14097 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 2754 | 4803.0804 | 9655.0353 | 13227.6834 | 72.9911 | 54.2 | 346 | 97.0065
CFB5 | 51061 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 9347 | 4958.4812 | 34971.6789 | 46346.9238 | 75.4563 | 54.2 | 744 | 93.9662
CFB6 | 56781 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 10014 | 5019.0804 | 38321.4969 | 50261.0711 | 76.2449 | 54.2 | 744 | 92.8317
SRB3 | 55051 | 64 | 460 | 793.1 | 130 |  | 663.1 | 18534.17 | 3000 | 36504.3181 | 55602.51 | 65.6523 |  | 731
TOTAL | 182465 |  |  | 790.1333 | 123.3333 | 172201 | 673.7377 |  |  | 122992.1167 | 165438.1883 | 74.3432 |  | 0.24522 | 93.4555
[9 empty] | 4989.1551 | [5 empty] | 70.5384

## Feb 05
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 2640 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1706.76 | 0 |  | 56.1 | 200
CFB2 | 6340 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 4098.81 | 0 |  | 56.1 | 461
CFB3
CFB1,2&3 | 8980 | [6 empty] | 1936 | 5095.381 | 5805.57 | 9864.6576 | 58.8522 | 56.1 |  | 94.6471
CFB4 | 20915 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 4207 | 4540.7818 | 14324.6835 | 19103.069 | 74.9863 | 56.1 | 492 | 106.2071
CFB5 | 47005 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8787 | 4785.4812 | 32193.7245 | 42050.0233 | 76.5605 | 56.1 | 672 | 100.7763
CFB6 | 43826 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 7977 | 4887.882 | 29578.1674 | 38990.6347 | 75.8597 | 56.1 | 583 | 98.6651
SRB3 | 45271 | 64 | 460 | 793.1 | 130 |  | 663.1 | 15233.77 | 3000 | 30019.2001 | 45701.31 | 65.6856 |  | 597.5
TOTAL | 165997 |  |  | 790.1333 | 123.3333 | 157523 | 673.0961 |  |  | 111921.3455 | 145845.0371 | 76.7399 |  | 0.1988 | 100.0739
[9 empty] | 4827.3815 | [5 empty] | 80.179

## Mar 05
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 2627 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1698.3555 | 0 |  | 50.6 | 187
CFB2 | 1802 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1164.993 | 0 |  | 50.6 | 168
CFB3
CFB1,2&3 | 4429 | [6 empty] | 1244 | 5312.9822 | 2863.3485 | 6609.3499 | 43.3227 | 50.6 |  | 81.8716
CFB4 | 27809 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5269 | 4818.7818 | 19046.3841 | 25390.1613 | 75.0148 | 50.6 | 741 | 90.2681
CFB5 | 47053 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8168 | 5168.5814 | 32226.5997 | 42216.9729 | 76.3356 | 50.6 | 731 | 84.159
CFB6 | 36817 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 6303 | 5204.4832 | 24847.7933 | 32803.8576 | 75.7466 | 50.6 | 556 | 83.5784
SRB3 | 57592 | 64 | 460 | 793.1 | 130 |  | 663.1 | 19858.37 | 3000 | 38189.2552 | 59575.11 | 64.1027 |  | 738.75
TOTAL | 173700 |  |  | 790.1333 | 123.3333 | 161602 | 675.39 |  |  | 117173.3808 | 159986.1018 | 73.2397 |  | 0.23665 | 84.9693
[9 empty] | 5126.2072 | [5 empty] | 64.8616

## Apr 05
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1
CFB2
CFB3
CFB1,2&3
CFB4 | 26143 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5299 | 4492.2808 | 17905.3407 | 23804.596 | 75.218 | 50.1 | 720 | 95.8721
CFB5 | 45641 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8249 | 4986.381 | 31259.5209 | 41132.6569 | 75.9968 | 50.1 | 720 | 86.3721
CFB6 | 48295 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 8493 | 5040.2808 | 32594.2955 | 42807.1048 | 76.1423 | 50.1 | 716 | 85.4485
SRB3 | 56289 | 64 | 460 | 793.1 | 130 |  | 663.1 | 20470.71 | 3000 | 37325.2359 | 61412.13 | 60.7783 |  | 715.5
TOTAL | 176368 |  |  | 801.95 | 125 | 160449 | 688.2325 |  |  | 119084.393 | 169156.4877 | 70.399 |  | 0.24917 | 89.2309
[9 empty] | 4839.6475 | [5 empty] | 66.997

## May 05
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1
CFB2
CFB3
CFB1,2&3
CFB4 | 28232 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5393 | 4781.882 | 19336.0968 | 25788.6896 | 74.979 | 50.1 | 744 | 90.0658
CFB5 | 50352 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8794 | 5151.2808 | 34486.0848 | 45300.3634 | 76.1276 | 50.1 | 744 | 83.6072
CFB6 | 52597 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 9150 | 5113.6816 | 35497.7153 | 46790.1866 | 75.8657 | 50.1 | 744 | 84.2219
SRB3 | 53052 | 64 | 460 | 793.1 | 130 |  | 663.1 | 20412.55 | 3000 | 35178.7812 | 61237.65 | 57.4463 |  | 721.83
TOTAL | 184233 |  |  | 801.95 | 125 | 158641 | 694.3139 |  |  | 124498.6781 | 179116.8896 | 69.5069 |  | 0.24437 | 85.965
[9 empty] | 5015.6148 | [5 empty] | 64.9577

## Jun 05
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 13 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 8.4045 |  |  | 49.2 | 24
CFB2 | 252 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 162.918 |  |  | 49.2 | 35
CFB3 | [12 empty] | 49.2
CFB1,2&3 | 265 | [6 empty] | 192 | 4886.0824 | 171.3225 | 938.1278 | 18.2622 | 49.2 |  | 86.5617
CFB4 | 27679 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5218 | 4886.0824 | 18957.3471 | 25495.578 | 74.3554 | 49.2 | 720 | 86.5617
CFB5 | 46295 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8490 | 4966.6816 | 31707.4455 | 42167.1268 | 75.1947 | 49.2 | 720 | 85.1569
CFB6 | 47733 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 8570 | 5009.9822 | 32215.0017 | 42935.5475 | 75.0311 | 49.2 | 720 | 84.4209
SRB3 | 52910 | 64 | 460 | 793.1 | 130 |  | 663.1 | 20013.64 | 3000 | 35084.621 | 60040.92 | 58.4345 |  | 716
TOTAL | 174882 |  |  | 790.1333 | 123.3333 | 156831 | 679.5302 |  |  | 118135.7378 | 170639.1722 | 69.2313 |  | 0.24395 | 85.6753
[9 empty] | 4937.2072 | [5 empty] | 64.7746

## July 05
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1
CFB2 | 488 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 315.492 | 0 |  | 50.3 | 47 | 0
CFB3
CFB1,2&3 | 488 | [6 empty] | 90 | 4956.0784 | 315.492 | 446.0471 |  | 50.3 |  | 87.2471
CFB4 | 28239 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5295 | 4956.0784 | 19340.8911 | 26242.4351 |  | 50.3 | 739 | 87.2471
CFB5 | 48833 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8850 | 5070.379 | 33445.7217 | 44872.8541 |  | 50.3 | 744 | 85.2803
CFB6 | 50347 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 9116 | 4986.2788 | 33979.1903 | 45454.9175 |  | 50.3 | 744 | 86.7187
SRB3 | 51115 | 64 | 460 | 793.1 | 130 |  | 663.1 | 18871.6 | 3000 | 33894.3565 | 56614.8 |  |  | 725.33
TOTAL | 179022 |  |  | 794.86 | 124 | 148923 | 691.7081 |  |  | 120975.6516 | 173185.0068 | 69.8534 |  | 0.24183 | 86.6233
[9 empty] | 4992.2037 | [5 empty] | 65.6751

## Aug 05
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 2017 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1303.9905 | 0 |  | 46.9 | 182 | 0
CFB2 | 2617 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1691.8905 | 0 |  | 46.9 | 219 | 0
CFB3 | 312 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 189.4776 | 0 |  | 46.9 | 66 | 0
CFB1,2&3 | 4946 | [6 empty] | 1134 | 5116.9802 | 3185.3586 | 5802.6555 | 54.8948 | 46.9 |  | 78.7917
CFB4 | 29390 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5488 | 4982.1786 | 20129.211 | 27342.1962 | 73.6196 | 46.9 | 744 | 80.9235
CFB5 | 39965 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 7329 | 5029.379 | 27372.0285 | 36860.3187 | 74.2588 | 46.9 | 621 | 80.1641
CFB6 | 49931 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 9087 | 5018.7798 | 33698.4319 | 45605.652 | 73.8909 | 46.9 | 699 | 80.3334
SRB3 | 51420 | 64 | 460 | 793.1 | 130 |  | 663.1 | 18858 | 3000 | 34096.602 | 56574 | 60.269 |  | 725.5
TOTAL | 175652 |  |  | 781.1571 | 122.8571 | 145230 | 679.5782 |  |  | 118481.632 | 166382.1669 | 71.2105 |  | 0.22279 | 80.0532
[9 empty] | 5036.8294 | [5 empty] | 62.2185

## Sep 05
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 1517 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 980.7405 | 0 |  | 49.9 | 187 | 0
CFB2 | 1988 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1285.242 | 0 |  | 49.9 | 186 | 0
CFB3 | 298 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 180.9754 | 0 |  | 49.9 | 64 | 0
CFB1,2&3 | 3803 | [6 empty] | 987 | 4751.4792 | 2446.9579 | 4689.71 | 52.1772 | 49.9 |  | 90.2803
CFB4 | 22331 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 4385 | 4832.6796 | 15294.5019 | 21191.3 | 72.1735 | 49.9 | 577 | 88.7634
CFB5 | 46166 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 9150 | 4704.381 | 31619.0934 | 43045.0862 | 73.4558 | 49.9 | 720 | 91.1841
CFB6 | 46739 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 8871 | 4794.88 | 31544.1511 | 42535.3805 | 74.1598 | 49.9 | 669 | 89.4631
SRB3 | 50114 | 64 | 460 | 793.1 | 130 |  | 663.1 | 19675.85 | 3000 | 33230.5934 | 59027.55 | 56.2968 |  | 719
TOTAL | 169153 |  |  | 781.1571 | 122.8571 | 145484 | 675.491 |  |  | 114135.2977 | 165799.3167 | 68.8394 |  | 0.2303 | 89.9227
[9 empty] | 4770.8549 | [5 empty] | 69.2134

## Oct 05
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 2526 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1633.059 | 0 |  | 51.1 | 256 | 0
CFB2 | 3075 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1987.9875 | 0 |  | 51.1 | 256 | 0
CFB3 | 3415 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 2073.9295 | 0 |  | 51.1 | 245 | 0
CFB1,2&3 | 9016 | [6 empty] | 2270 | 4805.1786 | 5694.976 | 10907.7554 |  | 51.1 |  | 91.4182
CFB4 | 29169 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 6215 | 4757.6796 | 19977.8481 | 29568.9787 |  | 51.1 | 739 | 92.3309
CFB5 | 48979 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 10071 | 4854.9802 | 33545.7171 | 48894.5056 |  | 51.1 | 743 | 90.4804
CFB6 | 33655 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 6850 | 4762.7798 | 22713.7595 | 32625.0416 |  | 51.1 | 538 | 92.232
SRB3 | 47998 | 64 | 460 | 793.1 | 130 |  | 663.1 | 17626.57 | 2838.35 | 31827.4738 | 50030.375 |  |  | 659.75
TOTAL | 168817 |  |  | 781.1571 | 122.8571 | 157610 | 666.4559 |  |  | 113759.7745 | 161118.9009 | 70.6061 |  | 0.19197 | 91.6154
[9 empty] | 4795.1546 | [5 empty] | 74.028

## Nov 05
Emission factor determination
| To derive steam enthalpy at the boiler end |  |  |  | To derive feed water enthalpy fed to the boiler |  | To derive the efficiency of the boiler | [5 empty] | To derive emission factor of the Fuel mix
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 1949 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1260.0285 | 0 |  | 53.2 | 143 | 0
CFB2 | 2462 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1591.683 | 0 |  | 53.2 | 143 | 0
CFB3 | 2546 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 1546.1858 | 0 |  | 53.2 | 143 | 0
CFB1,2&3 | 6957 | [6 empty] | 1618 | 5119.1786 | 4397.8973 | 8282.831 | 53.0965 | 53.2 |  | 89.3372
CFB4 | 28260 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5137 | 5154.2808 | 19355.274 | 26477.5405 | 73.1007 | 53.2 | 718 | 88.7288
CFB5 | 47279 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8377 | 5254.9802 | 32381.3871 | 44020.9691 | 73.559 | 53.2 | 718 | 87.0286
CFB6 | 38941 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 6769 | 5313.1806 | 26281.2809 | 35964.9195 | 73.0748 | 53.2 | 583 | 86.0752
SRB3 | 48739 | 64 | 460 | 793.1 | 130 |  | 663.1 | 17681.21 | 3000 | 32318.8309 | 53043.63 | 60.9288 |  | 709
TOTAL | 170176 |  |  | 781.1571 | 122.8571 | 170883 | 657.7896 |  |  | 114734.6702 | 159507.0591 | 71.9308 |  | 0.22458 | 87.7925
[9 empty] | 5210.4051 | [5 empty] | 68.076

## Dec 05
Emission factor determination
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1
CFB2
CFB3
CFB1,2&3
CFB4 | 27557 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 4787 | 5364.9802 | 18873.7893 | 25682.1602 |  | 55.1 | 738 | 88.2886
CFB5 | 47215 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8072 | 5436.1806 | 32337.5535 | 43880.8498 |  | 55.1 | 744 | 87.1323
CFB6 | 49976 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 8454 | 5452.88 | 33728.8024 | 46098.6475 |  | 55.1 | 738 | 86.8654
SRB3 | 54721 | 64 | 460 | 793.1 | 130 |  | 663.1 | 20733.86 | 2970 | 36285.4951 | 61579.5642 |  |  | 743.08
TOTAL | 179469 |  |  | 801.95 | 125 | 180101 | 676.5098 |  |  | 121225.6403 | 177241.2217 | 68.3959 |  | 0.25078 | 87.4288
[9 empty] | 5418.0136 | [5 empty] | 65.5034

## Jan 06
Emission factor determination
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 2514 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1625.301 | 0 |  | 55.2 | 157 | 0
CFB2 | 2437 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1575.5205 | 0 |  | 55.2 | 157 | 0
CFB3 | 1169 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 709.9337 | 0 |  | 55.2 | 90 | 0
CFB1,2&3 | 6120 | [6 empty] | 1401 | 5156.9802 | 3910.7552 | 7224.9293 | 54.1286 | 55.2 |  | 92.0163
CFB4 | 30834 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5484 | 5265.9802 | 21118.2066 | 28878.6354 | 73.1274 | 55.2 | 744 | 90.1117
CFB5 | 45192 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 7853 | 5339.9802 | 30952.0008 | 41934.8645 | 73.8097 | 55.2 | 684 | 88.8629
CFB6 | 46893 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 8128 | 5296.7798 | 31648.0857 | 43052.2262 | 73.5109 | 55.2 | 668 | 89.5877
SRB3 | 49592 | 64 | 460 | 793.1 | 130 |  | 663.1 | 19979.68 | 3000 | 32884.4552 | 59939.04 | 54.8632 |  | 741.67
TOTAL | 178631 |  |  | 781.1571 | 122.8571 | 158274 | 672.3009 |  |  | 120513.5035 | 173804.7661 | 69.3384 |  | 0.22879 | 90.1447
[9 empty] | 5264.9301 | [5 empty] | 69.5202

## Feb 06
Emission factor determination
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1
CFB2 | 3591 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 2321.5815 | 0 |  | 55.2 | 219
CFB3
CFB1,2&3 | 3591 | [6 empty] | 890 | 5236.5814 | 2321.5815 | 4660.5574 | 49.8134 | 55.2 |  | 90.6176
CFB4 | 15850 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 2785 | 5340.1806 | 10855.665 | 14872.403 | 72.992 | 55.2 | 449 | 88.8596
CFB5 | 43432 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 7571 | 5300.5814 | 29746.5768 | 40130.7018 | 74.1242 | 55.2 | 671 | 89.5234
CFB6 | 46110 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 7966 | 5312.381 | 31119.639 | 42318.427 | 73.5369 | 55.2 | 672 | 89.3246
SRB3 | 50176 | 64 | 460 | 793.1 | 130 |  | 663.1 | 19012.24 | 2970 | 33271.7056 | 56466.3528 | 58.9231 |  | 670.92
TOTAL | 159159 |  |  | 794.86 | 124 | 145999 | 681.1129 |  |  | 107315.1679 | 153787.8846 | 69.7813 |  | 0.25016 | 89.5813
[9 empty] | 5297.4311 | [5 empty] | 67.1713

## Mar 06
Emission factor determination
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Net Output Energy | Fuel Cons. | Calorific value | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy |  | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | C | M | M,C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  |  | Monthly |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | I=A*F | G | H | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | Mkcal | MT | Kcal/kg | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES |  | UTR004 | CLR012 |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | ENCON | UTY S/I | C.LAB | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1
CFB2
CFB3
CFB1,2&3
CFB4 | 28832 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 19747.0368 | 5189 | 5188.9822 | 26925.6286 |  | 57.9 | 744 | 95.9219
CFB5 | 49224 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 33713.5176 | 8696 | 5234.383 | 45518.1946 |  | 57.9 | 744 | 95.0899
CFB6 | 53768 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 36288.0232 | 9254 | 5238.6816 | 48478.7595 |  | 57.9 | 744 | 95.0119
SRB3 | 56009 | 64 | 460 | 793.1 | 130 |  | 663.1 | 37139.5679 | 18527 | 3000 | 55581 |  |  | 738.5
TOTAL | 187833 |  |  | 801.95 | 125 | 170198 | 688.6858 | 126888.1455 |  | 129357.9244 | 176503.5827 | 71.8898 |  | 0.24861 | 95.3412
[10 empty] | 5220.6823 |  |  |  |  | 71.6383

## Apr 06
Emission factor determination
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 2500 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1616.25 | 0 |  | 55.4 | 175 | 0
CFB2 | 1061 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 685.9365 | 0 |  | 55.4 | 175 | 0
CFB3 | 502 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 304.8646 | 0 |  | 55.4 | 51 | 0
CFB1,2&3 | 4063 | [6 empty] | 936 | 5182.7818 | 2607.0511 | 4851.0838 | 53.7416 | 55.4 |  | 91.89
CFB4 | 26078 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 4691 | 5202.4812 | 17860.8222 | 24404.8393 | 73.1856 | 55.4 | 699 | 91.542
CFB5 | 47191 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8392 | 5228.6816 | 32321.1159 | 43879.096 | 73.6595 | 55.4 | 720 | 91.0833
CFB6 | 51009 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 8688 | 5242.882 | 34425.9741 | 45550.1588 | 75.5782 | 55.4 | 720 | 90.8366
SRB3 | 45368 | 64 | 460 | 793.1 | 130 |  | 663.1 | 16656 | 3000 | 30083.5208 | 49968 | 60.2056 |  | 630.17
TOTAL | 173709 |  |  | 781.1571 | 122.8571 | 161608 | 666.8585 |  |  | 117298.4841 | 163802.0941 | 71.6099 |  | 0.19878 | 91.338
[9 empty] | 5214.2067 | [5 empty] | 73.1817

## May 06
Emission factor determination
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1
CFB2
CFB3
CFB1,2&3
CFB4 | 28806 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5186 | 5189.381 | 19729.2294 | 26912.1299 |  | 53.4 | 740 | 88.46
CFB5 | 50766 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 9025 | 5210.5814 | 34769.6334 | 47025.4971 |  | 53.4 | 743 | 88.1001
CFB6 | 53510 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 9172 | 5198.9802 | 36113.899 | 47685.0464 |  | 53.4 | 736 | 88.2967
SRB3 | 54740 | 64 | 460 | 793.1 | 130 |  | 663.1 | 20394.34 | 3000 | 36298.094 | 61183.02 |  |  | 739
TOTAL | 187822 |  |  | 801.95 | 125 | 180520 | 681.8097 |  |  | 126910.8558 | 182805.6934 | 69.4239 |  | 0.24983 | 88.2856
[9 empty] | 5199.6475 | [5 empty] | 66.2291

## Jun 06
Emission factor determination
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 1394 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 901.221 | 0 |  | 51.2 | 74
CFB2 | 3613 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 2335.8045 | 0 |  | 51.2 | 215
CFB3 | 304 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 184.6192 | 0 |  | 51.2 | 34
CFB1,2&3 | 5311 | [6 empty] | 1111 | 5134.6776 | 3421.6447 | 5704.6268 |  | 51.2 |  | 85.7192
CFB4 | 23041 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 4152 | 5236.9802 | 15780.7809 | 21743.9418 |  | 51.2 | 584 | 84.0447
CFB5 | 49221 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8916 | 5191.0804 | 33711.4629 | 46283.6728 |  | 51.2 | 720 | 84.7878
CFB6 | 44099 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 7684 | 5200.88 | 29762.4151 | 39963.5619 |  | 51.2 | 655 | 84.6281
SRB3 | 56776 | 64 | 460 | 793.1 | 130 |  | 663.1 | 20815.54 | 3000 | 37648.1656 | 62446.62 |  |  | 707
TOTAL | 178448 |  |  | 781.1571 | 122.8571 | 169783 | 664.2656 |  |  | 120324.4692 | 170437.7966 | 70.5973 |  | 0.23653 | 84.7949
[9 empty] | 5190.9046 | [5 empty] | 64.7381

## July 06
Emission factor determination
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Net Output Energy | Fuel Cons. | Calorific value | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy |  | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | C | M | M,C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  |  | Monthly |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | I=A*F | G | H | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | Mkcal | MT | Kcal/kg | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES |  | UTR004 | CLR012 |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | ENCON | UTY S/I | C.LAB | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1
CFB2 | 5946 | 42 | 405 | 766.5 | 120 |  | 646.5 | 3844.089 |  |  | 0 |  | 53 | 334
CFB3
CFB1,2&3 | 5946 | [6 empty] | 3844.089 | 1197 | 5297.1806 | 6340.7252 | 60.6254 | 53 |  | 86.0107
CFB4 | 17193 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 11775.4857 | 3163 | 5182.6796 | 16392.8156 | 71.8332 | 53 | 436 | 87.9109
CFB5 | 53706 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 36783.2394 | 9938 | 5160.7798 | 51287.8297 | 71.7192 | 53 | 743 | 88.284
CFB6 | 53768 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 36288.0232 | 9580 | 5153.6796 | 49372.2506 | 73.4988 | 53 | 742 | 88.4056
SRB3 | 56681 | 64 | 460 | 793.1 | 130 |  | 663.1 | 37585.1711 | 20275.87 | 3000 | 60827.61 | 61.7897 |  | 732.67
TOTAL | 187294 |  |  | 794.86 | 124 | 174390 | 679.4032 | 126276.0084 |  | 127248.1488 | 177880.5058 | 70.9892 |  | 0.24523 | 87.6528
[10 empty] | 5198.5799 |  |  |  |  | 66.1576

## Aug 06
Emission factor determination
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 113 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 73.0545 | 0 |  | 51.5 | 15
CFB2 | 156 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 100.854 | 0 |  | 51.5 | 16
CFB3 | [13 empty] | 0
CFB1,2&3 | 269 | [6 empty] | 220 | 5123.1806 | 173.9085 | 1127.0997 |  | 51.5 |  | 86.4149
CFB4 | 28799 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5547 | 5123.1806 | 19724.4351 | 28418.2828 |  | 51.5 | 703 | 86.4149
CFB5 | 48518 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 9342 | 5076.4792 | 33229.9782 | 47424.4687 |  | 51.5 | 743 | 87.2099
CFB6 | 47730 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 8838 | 5077.2788 | 32212.977 | 44872.99 |  | 51.5 | 714 | 87.1962
SRB3 | 53044 | 64 | 460 | 793.1 | 130 |  | 663.1 | 18925.06 | 3000 | 35173.4764 | 56775.18 |  |  | 701
TOTAL | 178360 |  |  | 790.1333 | 123.3333 | 171001 | 671.8886 |  |  | 120514.7752 | 177490.9215 | 67.8991 |  | 0.24239 | 86.809
[9 empty] | 5100.0298 | [5 empty] | 65.7671

## Sep 06
Emission factor determination
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1
CFB2 | 1341 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 866.9565 | 0 |  | 49.8 | 212
CFB3
CFB1,2&3 | 1341 | [6 empty] | 449 | 5042.9802 | 866.9565 | 2264.2981 | 38.2881 | 49.8 |  | 84.8913
CFB4 | 28655 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 5474 | 5059.0804 | 19625.8095 | 27693.4061 | 70.8682 | 49.8 | 720 | 84.6212
CFB5 | 47909 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 9181 | 5002.0804 | 32812.8741 | 45924.1002 | 71.4502 | 49.8 | 720 | 85.5854
CFB6 | 49669 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 9161 | 5003.381 | 33521.6081 | 45835.9733 | 73.1338 | 49.8 | 720 | 85.5632
SRB3 | 53268 | 64 | 460 | 793.1 | 130 |  | 663.1 | 20128 | 3000 | 35322.0108 | 60384 | 58.4956 |  | 708.67
TOTAL | 180842 |  |  | 794.86 | 124 | 168036 | 679.6408 |  |  | 122149.259 | 179837.4796 | 67.922 |  | 0.23004 | 85.1653
[9 empty] | 5026.8805 | [5 empty] | 65.5741

## Oct 06
Emission factor determination
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Fuel Cons. | Calorific value | Net Output Energy | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | M | M,C | C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  | Monthly |  |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | G | H | I=A*F | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | MT | Kcal/kg | Mkcal | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES | UTR004 | CLR012 |  |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | UTY S/I | C.LAB | ENCON | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 3840 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 2482.56 | 0 |  | 52.8 | 250
CFB2 | 2770 | 42 | 405 | 766.5 | 120 |  | 646.5 |  |  | 1790.805 | 0 |  | 52.8 | 155
CFB3 | 257 | 11 | 300 | 727.3 | 120 |  | 607.3 |  |  | 156.0761 | 0 |  | 52.8 | 35
CFB1,2&3 | 6867 | [6 empty] | 1701 | 4948.1248 | 4429.4411 | 8416.7603 | 52.6264 | 52.8 |  | 91.7307
CFB4 | 26212 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 4945 | 5071.0804 | 17952.5988 | 25076.4926 | 71.5913 | 52.8 | 646 | 89.5065
CFB5 | 46834 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 8838 | 5038.0824 | 32076.6066 | 44526.5723 | 72.0392 | 52.8 | 668 | 90.0928
CFB6 | 49358 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 8937 | 5056.0804 | 33311.7142 | 45186.1905 | 73.721 | 52.8 | 686 | 89.7721
SRB3 | 57647 | 64 | 460 | 793.1 | 130 |  | 663.1 | 21586.46 | 3000 | 38225.7257 | 64759.38 | 59.0273 |  | 734.83
TOTAL | 186918 |  |  | 781.1571 | 122.8571 | 179565 | 663.133 |  |  | 125996.0864 | 179548.6354 | 70.1738 |  | 0.23145 | 90.2755
[9 empty] | 5028.342 | [5 empty] | 69.3808

## Nov 06
Emission factor determination
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Net Output Energy | Fuel Cons. | Calorific value | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy |  | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | C | M | M,C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  |  | Monthly |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | I=A*F | G | H | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | Mkcal | MT | Kcal/kg | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES |  | UTR004 | CLR012 |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | ENCON | UTY S/I | C.LAB | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1 | 7779 | 42 | 405 | 766.5 | 120 |  | 646.5 | 5029.1235 |  |  | 0 |  | 50.5 | 477
CFB2 | 3407 | 42 | 405 | 766.5 | 120 |  | 646.5 | 2202.6255 |  |  | 0 |  | 50.5 | 295
CFB3 | 2269 | 11 | 300 | 727.3 | 120 |  | 607.3 | 1377.9637 |  |  | 0 |  | 50.5 | 125
CFB1,2&3 | 13455 | [6 empty] | 8609.7127 | 3038 | 5120.7818 | 15556.9351 | 55.3432 | 50.5 |  | 84.7767
CFB4 | 17572 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 12035.0628 | 3325 | 5025.1806 | 16708.7255 | 72.0286 | 50.5 | 473 | 86.3895
CFB5 | 51433 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 35226.4617 | 9429 | 5149.0804 | 48550.6791 | 72.5561 | 50.5 | 720 | 84.3107
CFB6 | 46165 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 31156.7585 | 8157 | 5135.1806 | 41887.6682 | 74.3817 | 50.5 | 603 | 84.539
SRB3 | 49662 | 64 | 460 | 793.1 | 130 |  | 663.1 | 32930.8722 | 17866.37 | 3000 | 53599.11 | 61.4392 |  | 615
TOTAL | 178287 |  |  | 781.1571 | 122.8571 | 167702 | 665.5941 | 119958.8679 |  |  | 160746.1827 | 74.6263 |  | 0.18591 | 85.004
[10 empty] | 5107.5558 |  |  |  |  | 69.2006

## Dec 06
Emission factor determination
Parameter | Steam Gen. | Steam Pressure | Steam Temperature | Steam Enthalpy | Feed Water Enthalpy |  | Net Enthalpy | Net Output Energy | Fuel Cons. | Calorific value | Input Energy | Efficiency | Carbon Contain of Coal | Boiler Hours of Operation | Emission Factor for Steam
Description | Total steam generated by the boiler | Steam Pressure at boiler outlet | Steam Temperature at boiler outlet | Determined by steam stable using the value of B,C | Feed Water Temp at boiler inlet |  | Steam Enthalpy - Feed Water Enthalpy |  | Total fuel consumed by type in the month | NCV of fuel in the month NCV = GCV-10*M |  | Determined by Direct Method
Measured - M/ Calculated - C/ Estimated - E | M | M | M | C | M |  | C | C | C | M,C | C | C | M | M | C
Monitoring Freq | Monthly | Monthly | Monthly |  | Monthly |  |  |  |  | Monthly |  |  | Monthly | Monthly
Formula | A | B | C | D | E |  | F=D-E | I=A*F | G | H | J=G*H | K=I/J | N | O | Q=(N*G*0.98*44/12)/I
Units | MT | kg/cm2 | oC | Kcal/kg | Kcal/kg |  | Kcal/kg | Mkcal | MT | Kcal/kg | Mkcal | % | % | Hours | tCO2/TJ
Reference/ Records | UTR004 | PIC6467 | TIC45 | STEAM TABLES | STEAM TABLES |  | STEAM TABLES |  | UTR004 | CLR012 |  |  |  | UTR004
Responsibility | UTY S/I | UTY S/I | UTY S/I | ENCON | ENCON |  | ENCON | ENCON | UTY S/I | C.LAB | ENCON | ENCON | C.LAB | UTY S/I | ENCON
Boilers
CFB1
CFB2
CFB3
CFB1,2&3
CFB4 | 29970 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 20526.453 | 6214 | 4565.2808 | 28368.6549 |  | 51 | 744 | 96.0338
CFB5 | 47301 | 62.5 | 480 | 804.9 | 120 |  | 684.9 | 32396.4549 | 9051 | 4908.4812 | 44426.6633 |  | 51 | 736 | 89.3191
CFB6 | 55471 | 62.5 | 480 | 804.9 | 130 |  | 674.9 | 37437.3779 | 9814 | 5084.1806 | 49896.1484 |  | 51 | 744 | 86.2324
SRB3 | 56886 | 64 | 460 | 793.1 | 130 |  | 663.1 | 37721.1066 | 20966.25 | 3000 | 62898.75 |  |  | 742
TOTAL | 189628 |  |  | 801.95 | 125 | 181465 | 682.3309 | 128081.3924 |  |  | 185590.2166 | 69.013 |  | 0.25017 | 90.5284
[10 empty] | 4852.6475 |  |  |  |  | 67.881