## Sheet1
Tonnes of Sugar Cane crushed as per the R.T. 8(C) reports
| Sr.No. | Period | Gross Season Days | Tonnes of Sugar cane crushed Per day (TCD)
| 1 | 29 Jul 04 - 31 Mar 05 | 246 | 1068.8
| 2 | 27 Jul 05 - 04 May 06 | 282 | 2137
| 3 | 27 Jul 06 - 26 Jun 07 | 335 | 3647
|  |  | Average TCD (2004 - 2007) | 2284.2667
1 |  | Reference plant efficiency = | MWh_el / MWh_biomass |  | Reference Plant Efficiency calculated at 3500 TCD
[5 empty] | Cane Crushed | 3500 |  | Bagasse generation | 4384800
A |  | MWh_el = | Steam to fuel ratio / Specific steam consupmtion |  | Total bagasse | 4384800 | Tonne | Steam/ bagasse | 2.079 | ISGEC John Thompson
[5 empty] | Calorific value | 2272 | kCal/kg | Steam generation | 9115999.2 | Tonne
| (a) | Steam to fuel ratio = | kg of steam / kg of biomass |  | Total kcal | 9962265600000 | kCal | Number of hours | 4320
[5 empty] | 1 kwh | 860 | kCal | Steam generation per hour | 2110.185 | ton
| (b) | Specific steam consupmtion = | kg of steam / kWh of electricity |  | Total kwh | 11584029767.4419 | kWh | Specific steam consumption | 6.9 | ISGEC John Thompson
[5 empty] | MWh bagasse | 11584029.7674 | MWh | Power generation | 305.8239 | MW
A = (a) / (b) = |  | MWh_el = | kWh of electricity / kg of biomass
[8 empty] | MWh electrical | 1321159.3043 | MWh
A |  | MWh_el = | MWh_el / Tonne of biomass |  | E (Mwhe/MWhb) | 11.41%
B |  | MWh_bagasse = | kCal / kg of biomass
|  | MWh_bagasse = | kWh_biomass * (kCal / 860) / kg of biomass
B |  | MWh_bagasse = | MWh_biomass / Tonne of biomass
1 = A / B = |  | Reference plant efficiency = | (MWh_el / MWh_biomass )
Note on I18: YourNameHere: For 180 days of operation at 24 hours. (Bagasse/Sugarcane) = 29%
Note on L18: YourNameHere: Refer to the letter from ISGEC John Thompson
Note on L22: YourNameHere: Refer to the letter from ISGEC John Thompson
Note on L30: YourNameHere: Refer to the letter from ISGEC John Thompson
Note on L34: YourNameHere: Refer to the letter from ISGEC John Thompson