## F-08-alt1 (2) (hidden)
FORMATO 8
ANALISIS DE SOSTENIBILIDAD DEL PROYECTO
1 | Entidad que se hará cargo de la operación y mantenimiento
2 | Capacidad técnica y logistica
3 | Participación de la población beneficiaria
4 | Flujos de costo de operación
ALTERNATIVA I: INTERCONEXIÓN MAJES CAMANÁ EN 138 KV
| COSTOS Y FUENTES | Años
|  | 1 | 5 | 10 | 11 | 15 | 20
| Compra de Energía (mil US$) | 2676.6147 | 4119.4183 | 4643.9915 | 4760.1101 | 5266.8684 | 6006.7226
| Costos de Oper. y Mant. mil US$ | 235.3303 | 235.3303 | 235.3303 | 235.3303 | 235.3303 | 235.3303
| Tarifas o Cuotas -(Venta de energía) | 3124.7068 | 3671.6996 | 4163.8802 | 4272.889 | 4748.4364 | 5442.7057
| Cobertura % | 107.3% | 84.31% | 85.34% | 85.54% | 86.3% | 87.19%

## GRUPOS TÉRMICOS (2) (hidden)
ANEXO Nº 3.4
INVERSIONES DESAGREGADAS DE LA SITUACIÓN SIN PROYECTO “GENERACIÓN TÉRMICA AISLADA”
1 |  | DESCRIPCIÓN | 2005 | 2009 | 2014 | 2019 | 2024
|  |  | 1 | 5 | 10 | 15 | 20
1 | 1 | TOTAL DE COSTOS DE INVERSIÓN - Mil US-$ | 0 | 0 | 350 | 175 | 350
1 |  | TOTAL DE COSTOS DE INVERSIÓN - Mil S/. | 0 | 0 | 1214.5 | 607.25 | 1214.5
1 | 2 | TOTAL COSTOS DE OPERACIÓN Y MANTENIMIENTO - Mil US-$ | 2472.4986 | 2576.3046 | 2921.6507 | 3471.8135 | 3888.9583
1 |  | TOTAL COSTOS DE OPERACIÓN Y MANTENIMIENTO - Mil S/. | 8579.5702 | 8939.7769 | 10138.1279 | 12047.1929 | 13494.6852
1 |  | COSTO TOTAL | 2472.4986 | 2576.3046 | 3271.6507 | 3646.8135 | 4238.9583 | #REF!
1 |  | COSTO TOTAL SIN PROYECTO -MIL S/. | 8579.5702 | 8939.7769 | 11352.6279 | 12654.4429 | 14709.1852
1 |  | Variables importantes
1 | 1 | Costo de los grupos térmicos instalados | 350
1 | 2 | Costo en lubricantes y mantenimiento | 7.5
1 | 3 | Costo en Over haul para los grupos nuevos se realizará cada 5 años y representa el | 40%
1 |  | Eficienci de los grupos | 12.34
1 | 4 | Precio de compra de combustible D2 | 5.65
1 |  |  | 1.6282
1 | 5 | Según Superintendencia de Banca y seguros; al 30 de Junio del 2004; tipo de Cambio : | 3.47

## F-04 (2) (hidden)
FORMATO 4
BALANCE OFERTA - DEMANDA EN EL MERCADO DEL PRODUCTO O SERVICIO
AÑO |  | ALT I: INTERCONEXIÓN MAJES CAMANÁ EN 138 KV |  |  |  |  | ALT II: INTERCONEXIÓN MAJES CAMANÁ EN 60 KV
|  | Demanda -kW |  |  | Oferta-kW | Superhabit | Demanda -kW |  |  | Oferta-kW | Superhabit
|  | Camaná | Pérdidas de LT | Total | S.E. Camaná | o Deficit (kW) | Camaná | Pérdidas de LT | Total | S.E. Camaná | o Deficit (kW)
1 | 2005 | 3248.6028 | 32.486 | 3281.0889 | 16000 | 12718.9111 | 3248.6028 | 162.4301 | 3411.033 | 13000 | 9588.967
5 | 2009 | 5002.8157 | 50.0282 | 5052.8439 | 16000 | 10947.1561 | 5002.8157 | 250.1408 | 5252.9565 | 13000 | 7747.0435
10 | 2014 | 5640.6108 | 56.4061 | 5697.0169 | 16000 | 10302.9831 | 5640.6108 | 282.0305 | 5922.6413 | 13000 | 7077.3587
15 | 2019 | 6397.9272 | 63.9793 | 6461.9065 | 16000 | 9538.0935 | 6397.9272 | 319.8964 | 6717.8235 | 13000 | 6282.1765
20 | 2024 | 7297.4687 | 72.9747 | 7370.4434 | 16000 | 8629.5566 | 7297.4687 | 364.8734 | 7662.3422 | 13000 | 5337.6578
Nota:
La fuentes actuales para el suministro de energía eléctrica para el proyecto son:
- SINAC, a través de las líneas de Transmisión 138 kV Socabaya-Cerro Verde-Reparición-Majes, las cuales
transportan energía y potencia proveniente de la Barra infinita Socabaya
- El suministro de energía será permanemte y confiable, sin restricciones de orden técnico y a costo razonable,
de tal manera que cubra la demanda de cada localidad y carga minera existente y futura
- Se considera que la construcción del proyecto se iniciará en el 2005 y será puesta en servicio en el año 2006
- Para la evaluación se utiliza la demanda de Camana, sin embargo las instalaciones han sido diseñadas,
considerando las demandas de los PSEs Ocoña, Atico y Caraveli

## F-03 (2) (hidden)
FORMATO 3
ANÁLISIS GENERAL DE LA OFERTA DEL PRODUCTO O SERVICIO
a) Describir procedimiento de cálculo, variables importantes y supuestos utilizados para la estimación de la oferta
La fuentes actuales para el suministro de energía eléctrica para el proyecto son:
- SINAC, a través de las líneas de Transmisión 138 kV Socabaya-Cerro Verde-Reparición-Majes, las cuales transportan energía y potencia proveniente de la Barra infinita Socabaya
- El suministro de energía será permanemte y confiable, sin restricciones de orden técnico y a costo razonable, de tal manera que cubra la demanda de cada localidad y carga minera existente y futura
- Se considera que la construcción del proyecto se iniciará en el 2005 y será puesta en servicio en el año 2006
- En el año 2 (2005) se prevé la entrada del proyecto
Época del | DESCRIPCIÓN | 2005 | 2009 | 2014 | 2019 | 2024
Año |  | 1 | 5 | 10 | 15 | 20
Todo el año | Oferta SINAC (1) en MW-Alternativa I-138 Kv | 16 | 16 | 16 | 16 | 16
Todo el año | Oferta SINAC (1) en MW Alternativa II-60 kV | 13 | 13 | 13 | 13 | 13

## res-demand (hidden)
FORMATO 2
ANÁLISIS GENERAL DE LA DEMANDA DEL PRODUCTO O SERVICIO
| A | PROCEDIMIENTO DE CÁLCULO, VARIABLES IMPORTANTES Y SUPUESTOS UTLIZADOS PARA LA ESTIMACION DE LA DEMANDA
Para el Estudio de la demanda se han asumido las siguientes premisas
- El suministro de energía será permanemte y confiable, sin restricciones de orden técnico y a costo razonable, de tal manera que cubra la demanda de Camaná y de las cargas productivas existentes.
- Se considera que la construcción del proyecto se iniciará en el 2005 y será puesta en servicio en el año 2006
| B | VARIABLES IMPORTANTES
|  | Variables importantes |  |  | Fuentes de Información
|  | Crecimiento anual de la población |  | : | Registro de INEI.
|  | Crecimiento anual de la población electrificada comercial e industrial |  | : | Registro de INEI. Registro de empresas distribuidoras en áreas rurales.
|  | Número de habitantes por abonado |  | : | Registro de INEI.
|  | Porcentaje de abonados domésticos |  | : | Registro de la unidad de negocios de SEAL en Camaná
|  | Porcentaje de abonados comerciales |  | : | Registro de la unidad de negocios de SEAL en Camaná
|  | Porcentaje de abonados pequeños industriales |  | : | Registro de la unidad de negocios de SEAL en Camaná (2004)
|  | Cargas en media tension (molinos) |  | : | Registro de la unidad de negocios de SEAL en Camaná
|  | Crecim. consumo abon. domésticos con proyecto año2 y consumo anual |  | :
|  | Crecimiento consumo abonados comerciales con proyecto año 2 |  | :
|  | Crecimiento consumo abonados P. industriales con proyecto año 2 |  | :
Tasa de crecimiento de las cargas después del 2do año
|  | Consumo de alumbrado público (porcentaje del consumo total) |  | : | Registro de la unidad de negocios de SEAL en Camaná
|  | Porcentaje de pérdidas de energía a partir de la barra de 10 kV |  | :
|  | Factor de carga |  | : | Registro de la unidad de negocios de SEAL en Camaná
|  | Potencia efectiva actual de centrales térmicas |  | :
-CT La pampa
-CT Cercado
Indicador:
El coeficiente de electrificación se incrementa hasta el año 4 luego del cual el crecimiento es con la tasa poblacional
| C.- | PROYECCIÓN
1 | ITEM |  | Descripción /Años | 2005 | 2009 | 2014 | 2019 | 2024
2 |  |  |  | 1 | 5 | 10 | 15 | 20
3 | 1 | NUMERO DE HABITANTES
4 |  | Habitantes electrificados con proyecto |  | 46400 | 58593.5572 | 69590.7655 | 82651.9991 | 98164.6475
5 |  | Habitantes electrificados sin proyecto |  | 46419 | 53266.8702 | 63264.3322 | 75138.181 | 89240.5887
6 | 1.1 | Sin Proyecto
7 |  | Número de lotes electrificados domésticos |  | 9886.32 | 11344.7796 | 13474.0394 | 16002.932 | 19006.4632
8 |  | Número de abonados comerciales |  | 360.4388 | 413.6118 | 491.241 | 583.4402 | 692.944
9 |  | Número de abonados peq. Industrial |  | 51.4913 | 59.0874 | 70.1773 | 83.3486 | 98.992
10 |  | Número de cargas en media tensión (molinos) |  | 17 | 17 | 17 | 17 | 17
11 |  | Total de clientes |  | 10315.25 | 11834.4787 | 14052.4577 | 16686.7209 | 19815.3992
12 | 1.2 | Con Proyecto
13 |  | Número de lotes electrificados domésticos |  | 9882.3456 | 13021 | 15465 | 18367 | 21814
14 |  | Número de abonados comerciales |  | 360.2939 | 474.724 | 563.8281 | 669.6302 | 795.3021
15 |  | Número de abonados peq. Industrial |  | 51.4706 | 67.8177 | 80.5469 | 95.6615 | 113.6146
16 |  | Número de cargas en media tensión (molinos) |  | 17 | 25 | 25 | 25 | 25
17 |  | Total de clientes |  | 10311.11 | 13588.5417 | 16134.375 | 19157.2917 | 22747.9167
36 | 3 | ENERGÍA Y POTENCIA DE INGRESO AL SISTEMA
37 | 3.1 | Sin Proyecto
38 |  | Energía al ingreso del sistema (MWh), con proyecto |  | 15722.6625 | 18474.9797 | 20951.4967 | 23892.822 | 27386.1938
39 |  | Potencia al ingreso del sistema (KW) con proyecto |  | 3249.5582 | 3818.4068 | 4330.2531 | 4938.1659 | 5660.1756
40 | 3.2 | Con Proyecto
41 |  | Energía al ingreso del sistema (MWh), sin proyecto |  | 15718.0399 | 24205.6237 | 27291.5313 | 30955.7309 | 35308.0728
42 |  | Potencia al ingreso del sistema (KW) sin proyecto |  | 3248.6028 | 5002.8157 | 5640.6108 | 6397.9272 | 7297.4687
Pérdidas de potencia en MW
[9 empty] | Pérdidas en el tramo de línea Sandia-Ananea | [6 empty] | 0.159 |  |  |  |  | 0.095 | [9 empty] | 0.067
[9 empty] | Resto del Sistema | [6 empty] | 0.219 |  |  |  |  | 0.498 | [9 empty] | 0.553
Pérdidas de energía en MWh-año
[9 empty] | Pérdidas en el tramo de línea Sandia-Ananea |  | 0 | 0 | 0 | 0 | 0 | 601.7069 | 0 | 0 | 0 | 0 | 359.5104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.5494
[9 empty] | Resto del Sistema |  | 0 | 0 | 0 | 0 | 0 | 828.7661 | 0 | 0 | 0 | 0 | 1884.5914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2092.729
[9 empty] | TOTAL |  | 0 | 0 | 0 | 0 | 0 | 1430.473 | 0 | 0 | 0 | 0 | 2244.1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2346.2784
[11 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[10 empty] | Factor de carga-Sandia-Azángaro | 0.6 |  | Factor de pérdidas-Sandia-Azángaro | [5 empty] | 0.432
[10 empty] | Factor de carga-resto del sistema | 0.35 |  | Factor de pérdidas-resto del sistema | [5 empty] | 0.19075

## Hoja1 (hidden)
METAS | AÑOS
| Unidad de medida | 1 | 2 | 3 | 4 | 5 | 6 | ...
Venta de energía | MWh | 0 | 2076.8868 | 2158.0267 | 2242.0061 | 2328.9168 | 2418.8533
clientes conectados | usuarios | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[9 empty] | COSTOS |  | AÑOS (Nuevos Soles)
[11 empty] | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
[9 empty] | SIN PROYECTO | OPERACIÓN | 15223935.8724 | 1952163.7311 | 2055494.1023 | 2133043.3988 | 2316399.5635 | 2245502.7574 | 2446412.1641 | 2421870.1092 | 2720810.6545 | 2611591.9059
[10 empty] | mantenimiento | 3805983.9681 | 17569473.5799 | 18499446.9204 | 19197390.5895 | 20847596.0713 | 20209524.8162 | 22017709.4765 | 21796830.9825 | 24487295.8909 | 23504327.153
[9 empty] | CON PROYECTO | OPERACIÓN | 8833861.9608 | 9838624.0992 | 10890333.2304 | 11556778.8637 | 12219651.0991 | 12573695.4306 | 12935648.323 | 13384395.6587 | 13762938.7503 | 14150179.7891
[10 empty] | mantenimiento | 981540.2179 | 1093180.4555 | 1210037.0256 | 1284086.5404 | 1357739.011 | 1397077.2701 | 1437294.2581 | 1487155.0732 | 1529215.4167 | 1572242.1988
20
[9 empty] | Tarifas de Venta en Barra | PPB | AÑOS (Nuevos Soles) 1: PEBP; AÑOS (Nuevos Soles) 2: PEBF
[9 empty] | 10 kV | S/kw-mes | AÑOS (Nuevos Soles) 1: cS/kw-h; AÑOS (Nuevos Soles) 2: cS/kw-h
[9 empty] | Tarifa en Barra para sistemas aislados Térmicos tipo A (Sin Proyecto) | 26.03 | AÑOS (Nuevos Soles) 1: 35.9; AÑOS (Nuevos Soles) 2: 35.9
[9 empty] | Tarifa en Barra Cálculada para Camaná –SINAC (Alt -I-138 kV) | 31.952 | AÑOS (Nuevos Soles) 1: 13.3361; AÑOS (Nuevos Soles) 2: 11.2025
[9 empty] | Tarifa en Barra Cálculada para Camaná –SINAC (Alt -II-60 kV) | 32.8515 | AÑOS (Nuevos Soles) 1: 12.9979; AÑOS (Nuevos Soles) 2: 10.8163

## CTermica
ANNEX Nº 2.1
1 |  | DISAGGREGATED INVESTMENT OF THE SITUATION WITHOUT PROJECT “ISOLATED THERMIC GENERATION”
1
1 |  | DESCRIPTION |  | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
1 |  |  |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21
1 | 1 | Isolated System Puerto Maldonado
1 | A | Investments in New Groups due to the increasing demand
1 | 1 | Installed Power Puerto Maldonado T.C. kW |  | 4900 | 5800 | 5800 | 6700 | 6700 | 6700 | 6700 | 7600 | 7600 | 7600 | 7600 | 8500 | 8500 | 8500 | 8500 | 8500 | 9400 | 9400 | 9400 | 10300 | 10300 | 10300
1 | 2 | Demand of Puerto Maldonado kW |  | 5512.187 | 5677.2733 | 5964.1625 | 6179.9852 | 6388.6409 | 6579.5989 | 6776.1936 | 6978.5887 | 7186.9523 | 7401.4575 | 7622.2824 | 7849.6098 | 8083.6283 | 8324.5313 | 8572.5182 | 8827.7938 | 9090.5689 | 9361.0601 | 9639.4905 | 9926.0893 | 10221.0923 | 10524.7421
1 | 3 | Demand of Power of the new groups |  | 612.187 | 0 | 164.1625 | 0 | 0 | 0 | 76.1936 | 0 | 0 | 0 | 22.2824 | 0 | 0 | 0 |  | 327.7938 | 0 | 0 | 239.4905 |  | 0 | 224.7421
1 | 3.1 | Thermic Group to implement KW |  | 900 | 0 | 900 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 900 | 0 | 0 | 0 | 0 | 900 | 0 | 0 | 900 | 0 | 0 | 900
1 | 3.2 | Name of group |  | GRUPO-1 | 0 | GRUPO-2 | 0 | 0 | 0 | GRUPO-3 | 0 | 0 | 0 | GRUPO-4 | 0 | 0 | 0 | 0 | GRUPO-5 | 0 | 0 | GRUPO-6 | 0 | 0 | GRUPO-7
1 | 4 | Cost of the New Group Thousands-US $ |  | 316.8 | 0 | 316.8 | 0 | 0 | 0 | 316.8 | 0 | 0 | 0 | 316.8 | 0 | 0 | 0 | 0 | 316.8 | 0 | 0 | 316.8 | 0 | 0 | 316.8
1 | B | Investments in New Groups due to the replacement of existings |  | 0 | 0 | 0 | 264 | 0 | 363 | 0 | 264 | 0 | 297 | 297 | 0 | 297 | 0 | 594 | 363 | 0 | 0 | 594 | 0 | 429 | 297
1 | 1 | GROUP -8 - Replacement of CUMMINS 01 (1100 kW) |  | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | GROUP-9 - Replacement of CAT 02 (800 kW) |  | 0 | 0 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | GROUP-10 - Replacement del CAT 03 (800 kW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 4 | GROUP-11 - Replacement del CUMMINS 02 (900 kW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 5 | GROUP-12 - Replacement del CUMMINS 03 (900 kW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 6 | GROUP-13 - Replacement del CAT 04 (400 kW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 0
1 | 7 | GROUP-14 - Replacement del GROUP-1 (900 kW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 8 | GROUP-15 - Replacement del GROUP-2 (900 kW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 9 | GROUP-16 - Replacement del GROUP-3 (900 kW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0
| 10 | GRUPO-17 - Reemplazo del GROUP-4 (900 kW)
1 | 11 | GROUP-18 - Replacement of GROUP-8 (1100 kW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 363 | 0 | 0 | 0 | 0 | 0 | 0
1 | 12 | GROUP-19 - Replacement of GROUP-9 (900 kW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 13 | GROUP-20 - Replacement del GROUP-10 (900 kW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0 | 0 | 0
1 | 14 | GROUP-21 - Replacement of GROUP-11 (900 kW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297 | 0
1 | 15 | GROUP-22 - Replacement of GROUP-12 (900 kW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297
1 | C | Operation and Maintenance Costs
1 | 1 | Energy MWh-year
1 |  | Total Energy in Puerto Maldonado City |  | 20943.0547 | 21757.2355 | 22602.122 | 23478.8126 | 24388.4434 | 25332.1893 | 26311.2653 | 27326.9276 | 28380.4754 | 29473.2522 | 30606.6468 | 31782.0954 | 33001.0828 | 34265.1441 | 35575.8662 | 36934.89 | 38343.9113 | 39804.6835 | 41319.019 | 42888.7909 | 44515.9357 | 46202.4546
0 |  | Total hours required |  | 29010.994 | 30138.8235 | 31906.5338 | 33331.6063 | 34744.5141 | 36090.4673 | 37486.7582 | 38935.1741 | 40437.5628 | 41995.8351 | 43611.9662 | 45287.9986 | 47026.0437 | 48828.2843 | 50696.977 | 52634.4545 | 54643.128 | 56725.49 | 58884.1166 | 61121.6709 | 63440.9049 | 65844.6631
1 | 2 | Operation Costs |  | 3379.7825 | 3511.1747 | 3647.5221 | 3789.0022 | 3935.798 | 4088.0994 | 4246.1023 | 4410.0095 | 4580.0307 | 4756.3826 | 4939.2894 | 5128.9829 | 5325.7026 | 5529.6964 | 5741.2202 | 5960.539 | 6187.9263 | 6423.6652 | 6668.0481 | 6921.3773 | 7183.9653 | 7456.1351
1 | 2.1 | Fuel Costs
1 |  | Nº of gallons of oil (Thousands of gallons) |  | 1545.6129 | 1605.7 | 1668.0533 | 1732.7537 | 1799.8851 | 1869.5343 | 1941.7908 | 2016.7474 | 2094.5 | 2175.1478 | 2258.7931 | 2345.5421 | 2435.5043 | 2528.7929 | 2625.5252 | 2725.8221 | 2829.809 | 2937.615 | 3049.3741 | 3165.2244 | 3285.3089 | 3409.7752
1 |  | Fuel Cost (Thousands US $) |  | 3379.7825 | 3511.1747 | 3647.5221 | 3789.0022 | 3935.798 | 4088.0994 | 4246.1023 | 4410.0095 | 4580.0307 | 4756.3826 | 4939.2894 | 5128.9829 | 5325.7026 | 5529.6964 | 5741.2202 | 5960.539 | 6187.9263 | 6423.6652 | 6668.0481 | 6921.3773 | 7183.9653 | 7456.1351
1 | 3 | Maintenance Costs |  | 985.3852 | 1173.6467 | 1039.327 | 1018.9513 | 1126.6462 | 1165.3398 | 1458.9219 | 1120.404 | 1445.1995 | 1208.4033 | 1761.7525 | 1303.0659 | 1690.9644 | 1658.3109 | 1712.0505 | 1641.0505 | 1698.8204 | 2293.752 | 1820.7998 | 1885.1604 | 1825.1534 | 2809.5006
1 | 3.1 | Lubricant, Operation and Maintenance Costs |  | 858.6652 | 892.0467 | 926.687 | 962.6313 | 999.9262 | 1038.6198 | 1078.7619 | 1120.404 | 1163.5995 | 1208.4033 | 1254.8725 | 1303.0659 | 1353.0444 | 1404.8709 | 1458.6105 | 1514.3305 | 1572.1004 | 1631.992 | 1694.0798 | 1758.4404 | 1825.1534 | 1894.3006
1 | 3.2 | Over haul |  | 126.72 | 281.6 | 112.64 | 56.32 | 126.72 | 126.72 | 380.16 | 0 | 281.6 | 0 | 506.88 | 0 | 337.92 | 253.44 | 253.44 | 126.72 | 126.72 | 661.76 | 126.72 | 126.72 | 0 | 915.2
1 | 3,2,1 | Over haul Costs in existing groups |  | 126.72 | 281.6 | 112.64 | 56.32 | 0 | 126.72 | 126.72 | 0 | 0 | 0 | 0 | 0 | 56.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | CUMMINS 01 (1100 kW) | 1100
1 |  | Nominal Operation Hours | 14000 | 2005 0: 14000
0 |  | Total Energy MWH | 15400
1 |  | Annual Hours of Use |  | 4061.5392 | 4219.4353 | 3893.5073 | 4193.6825 | 4371.4503 | 4383.2271 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours of use | 23007 | 27068.5392 | 31287.9745 | 35181.4817 | 39375.1642 | 43746.6145 | 48129.8416 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours for Over hault Use |  | 13068.5392 | 17287.9745 | 3893.5073 | 8087.1898 | 12458.6401 | 16841.8672 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Over hault/op | 2 | op | ovh | op | op | op | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
0 |  | Amount Over hault |  | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 154.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | CAT 02 (800 kW) | 800
1 |  | Nominal Operation Hours | 25000 | 2005 0: 25000
0 |  | Total Energy MWH | 20000
1 |  | Annual Hours of Use |  | 5274.7262 | 5479.7861 | 5056.503 | 5282.3465 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours of use | 54452 | 59726.7262 | 65206.5123 | 70263.0153 | 75545.3617 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours for Over hault Use |  | 9726.7262 | 15206.5123 | 20263.0153 | 25545.3617 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Over hault/op | 2 | op | op | op | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
0 |  | Over hault/op |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | CAT 03 (800 kW) | 800
1 |  | Nominal Operation Hours | 22000 | 2005 0: 22000
0 |  | Total Energy MWH | 17600
1 |  | Annual Hours of Use |  | 4641.759 | 4822.2118 | 4449.7226 | 4792.78 | 4995.9432 | 5009.4024 | 5203.2093 | 4792.0214 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours of use | 33662 | 38303.759 | 43125.9708 | 47575.6934 | 52368.4734 | 57364.4166 | 62373.819 | 67577.0284 | 72369.0498 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours for Over hault Use |  | 16303.759 | 21125.9708 | 25575.6934 | 4792.78 | 9788.7232 | 14798.1256 | 20001.3349 | 24793.3564 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Over hault/op | 2 | op | op | ovh | op | op | op | op | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
0 |  | Over hault/op |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 112.64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | CUMMINS 02 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 4272.5282 | 4438.6267 | 4095.7674 | 4411.5361 | 4598.5386 | 4610.9272 | 4789.3177 | 4454.4479 | 4626.3313 | 4804.6082 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours of use | 14147 | 18419.5282 | 22858.1549 | 26953.9224 | 31365.4585 | 35963.9971 | 40574.9243 | 45364.242 | 49818.6899 | 54445.0212 | 59249.6295 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours for Over hault Use |  | 18419.5282 | 4438.6267 | 8534.3941 | 12945.9303 | 17544.4689 | 22155.3961 | 4789.3177 | 9243.7656 | 13870.0969 | 18674.7052 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Over hault/op | 2 | ovh | op | op | op | op | ovh | op | op | op | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
0 |  | Over hault/op |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 126.72 | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | CUMMINS 03 (900 kW) | 900
1 |  | Nominal Operation Hours | 14000 | 2005 0: 14000
0 |  | Total Energy MWH | 12600
1 |  | Annual Hours of Use |  | 3323.0775 | 3452.2652 | 3185.5969 | 3431.1948 | 3576.6412 | 3586.2767 | 3725.0249 | 3464.5706 | 3598.2577 | 3736.9175 | 3482.3243 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours of use | 9281 | 12604.0775 | 16056.3427 | 19241.9396 | 22673.1344 | 26249.7755 | 29836.0523 | 33561.0771 | 37025.6477 | 40623.9054 | 44360.8229 | 47843.1472 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours for Over hault Use |  | 12604.0775 | 16056.3427 | 3185.5969 | 6616.7916 | 10193.4328 | 13779.7095 | 17504.7344 | 3464.5706 | 7062.8283 | 10799.7458 | 14282.0701 | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Over hault/op | 2 | op | ovh | op | op | op | op | ovh | op | op | op | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
0 |  | Over hault/op |  | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 126.72 | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | CAT 04 (400 kW) | 400
1 |  | Nominal Operation Hours | 30000 | 2005 0: 30000
0 |  | Total Energy MWH | 12000
1 |  | Annual Hours of Use |  | 3164.8357 | 3287.8717 | 3033.9018 | 3267.8045 | 3406.3249 | 3415.5016 | 3547.6427 | 3299.591 | 3426.9121 | 3558.9691 | 3242.5254 | 3367.1374 | 3496.3601 | 3630.3557 | 3769.292 | 3556.3821 | 3692.1032 | 3832.8034 | 3646.0753 | 3784.6236 | 4027.994 | inop
1 |  | Accumulated hours of use | 18812 | 21976.8357 | 25264.7074 | 28298.6092 | 31566.4137 | 34972.7386 | 38388.2402 | 41935.883 | 45235.474 | 48662.3861 | 52221.3552 | 55463.8805 | 58831.018 | 62327.3781 | 65957.7338 | 69727.0258 | 73283.4079 | 76975.5111 | 80808.3145 | 84454.3898 | 88239.0134 | 92267.0073 | inop
1 |  | Accumulated hours for Over hault Use |  | 21976.8357 | 25264.7074 | 28298.6092 | 31566.4137 | 3406.3249 | 6821.8265 | 10369.4693 | 13669.0603 | 17095.9724 | 20654.9415 | 23897.4668 | 27264.6043 | 30760.9644 | 3630.3557 | 7399.6477 | 10956.0297 | 14648.133 | 18480.9364 | 22127.0117 | 25911.6353 | 29939.6292 | inop
1 |  | Over hault/op | 2 | op | op | op | ovh | op | op | op | op | op | op | op | op | ovh | op | op | op | op | op | op | op | inop | inop
0 |  | Over hault/op |  | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 56.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 56.32 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over haul Costs in New Groups |  | 0 | 0 | 0 | 0 | 126.72 | 0 | 253.44 | 0 | 281.6 | 0 | 506.88 | 0 | 281.6 | 253.44 | 253.44 | 126.72 | 126.72 | 661.76 | 126.72 | 126.72 | 0 | 915.2
1 |  | GROUP-1 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 4272.5282 | 4438.6267 | 4095.7674 | 4411.5361 | 4598.5386 | 4610.9272 | 4789.3177 | 4454.4479 | 4626.3313 | 4804.6082 | 4377.4092 | 4545.6355 | 4720.0862 | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours of use | 0 | 4272.5282 | 8711.1549 | 12806.9224 | 17218.4585 | 21816.9971 | 26427.9243 | 31217.242 | 35671.6899 | 40298.0212 | 45102.6295 | 49480.0387 | 54025.6743 | 58745.7604 | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours for Over hault Use |  | 4272.5282 | 8711.1549 | 12806.9224 | 17218.4585 | 21816.9971 | 4610.9272 | 9400.2449 | 13854.6928 | 18481.0241 | 4804.6082 | 9182.0175 | 13727.653 | 18447.7392 | inop | inop | inop | inop | inop | inop | inop | inop | inop
1 |  | Over hault | 2 | op | op | op | op | ovh | op | op | op | ovh | op | op | op | inop | inop | inop | inop | inop | inop | inop | inop | inop | inop
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | GROUP-2 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  |  |  | 4095.7674 | 4411.5361 | 4598.5386 | 4610.9272 | 4789.3177 | 4454.4479 | 4626.3313 | 4804.6082 | 4377.4092 | 4545.6355 | 4720.0862 | 4900.9802 | 5088.5442 | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours of use | 0 |  |  | 4095.7674 | 8507.3035 | 13105.8422 | 17716.7694 | 22506.0871 | 26960.5349 | 31586.8663 | 36391.4745 | 40768.8838 | 45314.5193 | 50034.6055 | 54935.5857 | 60024.1299 | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours for Over hault Use |  |  |  | 4095.7674 | 8507.3035 | 13105.8422 | 17716.7694 | 22506.0871 | 4454.4479 | 9080.7792 | 13885.3875 | 18262.7967 | 4545.6355 | 9265.7217 | 14166.7019 | 19255.2461 | inop | inop | inop | inop | inop | inop | inop
1 |  | Over hault | 2 |  |  | op | op | op | op | ovh | op | op | op | ovh | op | op | op | inop | inop | inop | inop | inop | inop | inop | inop
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | GROUP-3 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use | [8 empty] | 4454.4479 | 4626.3313 | 4804.6082 | 4377.4092 | 4545.6355 | 4720.0862 | 4900.9802 | 5088.5442 | 4801.1158 | 4984.3394 | 5174.2846 | 4922.2017 | inop | inop | inop
1 |  | Accumulated hours of use | 0 | [7 empty] | 4454.4479 | 9080.7792 | 13885.3875 | 18262.7967 | 22808.4323 | 27528.5184 | 32429.4986 | 37518.0428 | 42319.1586 | 47303.498 | 52477.7825 | 57399.9842 | inop | inop | inop
1 |  | Accumulated hours for Over hault Use | [8 empty] | 4454.4479 | 9080.7792 | 13885.3875 | 18262.7967 | 4545.6355 | 9265.7217 | 14166.7019 | 19255.2461 | 4801.1158 | 9785.4552 | 14959.7397 | 19881.9414 | inop | inop | inop
1 |  | Over hault | 2 | [7 empty] | op | op | op | ovh | op | op | op | ovh | op | op | op | inop | inop | inop | inop
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | GROUP-4 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 2015 10: 4377.4092; 2016 11: 4545.6355; 2017 12: 4720.0862; 2018 13: 4900.9802; 2019 14: 5088.5442; 2020 15: 4801.1158; 2021 16: 4984.3394; 2022 17: 5174.2846; 2023 18: 4922.2017; 2024 19: 5109.2418; 2025 20: 5437.7918; 2026 21: 5926.0197
1 |  | Accumulated hours of use | 0 | 2015 10: 4377.4092; 2016 11: 8923.0448; 2017 12: 13643.131; 2018 13: 18544.1112; 2019 14: 23632.6553; 2020 15: 28433.7711; 2021 16: 33418.1105; 2022 17: 38592.3951; 2023 18: 43514.5968; 2024 19: 48623.8386; 2025 20: 54061.6304; 2026 21: 59987.6501
1 |  | Accumulated hours for Over hault Use |  | 2015 10: 4377.4092; 2016 11: 8923.0448; 2017 12: 13643.131; 2018 13: 18544.1112; 2019 14: 5088.5442; 2020 15: 9889.6599; 2021 16: 14873.9993; 2022 17: 20048.2839; 2023 18: 4922.2017; 2024 19: 10031.4435; 2025 20: 15469.2354; 2026 21: 21395.2551
1 |  | Over hault | 3 | 2015 10: op; 2016 11: op; 2017 12: op; 2018 13: ovh; 2019 14: op; 2020 15: op; 2021 16: op; 2022 17: ovh; 2023 18: op; 2024 19: op; 2025 20: op; 2026 21: ovh
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 126.72
1 |  | GROUP-5 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 2020 15: 4801.1158; 2021 16: 4984.3394; 2022 17: 5174.2846; 2023 18: 4922.2017; 2024 19: 5109.2418; 2025 20: 5437.7918; 2026 21: 5926.0197
1 |  | Accumulated hours of use | 0 | 2020 15: 4801.1158; 2021 16: 9785.4552; 2022 17: 14959.7397; 2023 18: 19881.9414; 2024 19: 24991.1833; 2025 20: 30428.9751; 2026 21: 36354.9948
1 |  | Accumulated hours for Over hault Use |  | 2020 15: 4801.1158; 2021 16: 9785.4552; 2022 17: 14959.7397; 2023 18: 19881.9414; 2024 19: 5109.2418; 2025 20: 10547.0337; 2026 21: 16473.0534
1 |  | Over hault | 1 | 2020 15: op; 2021 16: op; 2022 17: op; 2023 18: ovh; 2024 19: op; 2025 20: op; 2026 21: op
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0
1 |  | GROUP-6 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 2023 18: 4922.2017; 2024 19: 5109.2418; 2025 20: 5437.7918; 2026 21: 5926.0197
1 |  | Accumulated hours of use | 0 | 2023 18: 4922.2017; 2024 19: 10031.4435; 2025 20: 15469.2354; 2026 21: 21395.2551
1 |  | Accumulated hours for Over hault Use |  | 2023 18: 4922.2017; 2024 19: 10031.4435; 2025 20: 15469.2354; 2026 21: 21395.2551
1 |  | Over hault | 1 | 2023 18: op; 2024 19: op; 2025 20: op; 2026 21: ovh
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.72
|  | GRUPO-7 (900 kW) | 900
|  | Horas de Operación Nominales | 18000 | 2005 0: 18000
|  | Total Energy MWH | 16200
|  | Annual Hours of Use |  | 2026 21: 5926.0197
|  | Accumulated hours of use | 0 | 2026 21: 5926.0197
|  | Accumulated hours for Over hault Use |  | 2026 21: 5926.0197
|  | Over hault | 0 | bar: 2026 21
|  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | GROUP-8 (1100 kW) | 1100
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 19800
1 |  | Annual Hours of Use | [6 empty] | 5635.5777 | 5853.6105 | 5444.3252 | 5654.405 | 5872.299 | 5350.1669 | 5555.7768 | 5768.9942 | 5990.0869 | 6219.3318 | 5868.0304 | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours of use | 0 | [5 empty] | 5635.5777 | 11489.1882 | 16933.5134 | 22587.9184 | 28460.2173 | 33810.3842 | 39366.161 | 45135.1552 | 51125.2421 | 57344.5739 | 63212.6043 | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours for Over hault Use | [6 empty] | 5635.5777 | 11489.1882 | 16933.5134 | 22587.9184 | 5872.299 | 11222.4658 | 16778.2426 | 22547.2368 | 5990.0869 | 12209.4187 | 18077.4491 | inop | inop | inop | inop | inop | inop
1 |  | Over hault | 2 | [5 empty] | op | op | op | ovh | op | op | op | ovh | op | op | inop | inop | inop | inop | inop | inop | inop
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154.88 | 0 | 0 | 0 | 154.88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | GROUP-9 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  |  |  |  | 4411.5361 | 4598.5386 | 4776.6795 | 4961.4827 | 4550.8645 | 4726.4684 | 4908.6041 | 4377.4092 | 4545.6355 | 4720.0862 | 4900.9802 | 5088.5442 | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours of use | 0 |  |  |  | 4411.5361 | 9010.0748 | 13786.7542 | 18748.237 | 23299.1015 | 28025.5698 | 32934.1739 | 37311.5832 | 41857.2187 | 46577.3049 | 51478.2851 | 56566.8293 | inop | inop | inop | inop | inop | inop | inop
1 |  | Accumulated hours for Over hault Use |  |  |  |  | 4411.5361 | 9010.0748 | 13786.7542 | 18748.237 | 4550.8645 | 9277.3329 | 14185.937 | 18563.3462 | 4545.6355 | 9265.7217 | 14166.7019 | 19255.2461 | inop | inop | inop | inop | inop | inop | inop
1 |  | Over hault | 2 |  |  |  | op | op | op | ovh | op | op | op | ovh | op | op | op | inop | inop | inop | inop | inop | inop | inop | inop
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | GROUP-10 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use | [8 empty] | 4454.4479 | 4626.3313 | 4804.6082 | 4377.4092 | 4545.6355 | 4720.0862 | 4900.9802 | 5088.5442 | 4801.1158 | 4984.3394 | 5174.2846 | 5371.1863 | inop | inop | inop
1 |  | Accumulated hours of use | 0 | [7 empty] | 4454.4479 | 9080.7792 | 13885.3875 | 18262.7967 | 22808.4323 | 27528.5184 | 32429.4986 | 37518.0428 | 42319.1586 | 47303.498 | 52477.7825 | 57848.9688 | inop | inop | inop
1 |  | Accumulated hours for Over hault Use | [8 empty] | 4454.4479 | 9080.7792 | 13885.3875 | 18262.7967 | 4545.6355 | 9265.7217 | 14166.7019 | 19255.2461 | 4801.1158 | 9785.4552 | 14959.7397 | 20330.926 | inop | inop | inop
1 |  | Over hault | 2 | [7 empty] | op | op | op | ovh | op | op | op | ovh | op | op | op | inop | inop | inop | inop
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | GROUP-11 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 2014 9: 4804.6082; 2015 10: 4377.4092; 2016 11: 4545.6355; 2017 12: 4720.0862; 2018 13: 4900.9802; 2019 14: 5088.5442; 2020 15: 4801.1158; 2021 16: 4984.3394; 2022 17: 5174.2846; 2023 18: 4922.2017; 2024 19: 5109.2418; 2025 20: 5437.7918; 2026 21: inop
1 |  | Accumulated hours of use | 0 | 2014 9: 4804.6082; 2015 10: 9182.0175; 2016 11: 13727.653; 2017 12: 18447.7392; 2018 13: 23348.7194; 2019 14: 28437.2636; 2020 15: 33238.3794; 2021 16: 38222.7187; 2022 17: 43397.0033; 2023 18: 48319.205; 2024 19: 53428.4468; 2025 20: 58866.2387; 2026 21: inop
1 |  | Accumulated hours for Over hault Use |  | 2014 9: 4804.6082; 2015 10: 9182.0175; 2016 11: 13727.653; 2017 12: 18447.7392; 2018 13: 4900.9802; 2019 14: 9989.5244; 2020 15: 14790.6402; 2021 16: 19774.9795; 2022 17: 5174.2846; 2023 18: 10096.4863; 2024 19: 15205.7281; 2025 20: 20643.5199; 2026 21: inop
1 |  | Over hault | 2 | 2014 9: op; 2015 10: op; 2016 11: op; 2017 12: ovh; 2018 13: op; 2019 14: op; 2020 15: op; 2021 16: ovh; 2022 17: op; 2023 18: op; 2024 19: op; 2025 20: inop; 2026 21: inop
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 0 | 0
1 |  | GROUP-12 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 2015 10: 4377.4092; 2016 11: 4545.6355; 2017 12: 4720.0862; 2018 13: 4900.9802; 2019 14: 5088.5442; 2020 15: 4801.1158; 2021 16: 4984.3394; 2022 17: 5174.2846; 2023 18: 4922.2017; 2024 19: 5109.2418; 2025 20: 5437.7918; 2026 21: 5926.0197
1 |  | Accumulated hours of use | 0 | 2015 10: 4377.4092; 2016 11: 8923.0448; 2017 12: 13643.131; 2018 13: 18544.1112; 2019 14: 23632.6553; 2020 15: 28433.7711; 2021 16: 33418.1105; 2022 17: 38592.3951; 2023 18: 43514.5968; 2024 19: 48623.8386; 2025 20: 54061.6304; 2026 21: 59987.6501
1 |  | Accumulated hours for Over hault Use |  | 2015 10: 4377.4092; 2016 11: 8923.0448; 2017 12: 13643.131; 2018 13: 18544.1112; 2019 14: 5088.5442; 2020 15: 9889.6599; 2021 16: 14873.9993; 2022 17: 20048.2839; 2023 18: 4922.2017; 2024 19: 10031.4435; 2025 20: 15469.2354; 2026 21: 21395.2551
1 |  | Over hault | 2 | 2015 10: op; 2016 11: op; 2017 12: op; 2018 13: ovh; 2019 14: op; 2020 15: op; 2021 16: op; 2022 17: ovh; 2023 18: op; 2024 19: op; 2025 20: op; 2026 21: inop
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 0
1 |  | GROUP-13 (400 kW) | 400
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 7200
1 |  | Annual Hours of Use |  | 2025 20: 2416.7964; 2026 21: 2633.7865
1 |  | Accumulated hours of use | 0 | 2025 20: 2416.7964; 2026 21: 5050.5829
1 |  | Accumulated hours for Over hault Use |  | 2025 20: 2416.7964; 2026 21: 5050.5829
1 |  | Over hault | 0 | bar: 2025 20 to 2026 21
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | GROUP-14 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 2017 12: 4720.0862; 2018 13: 4900.9802; 2019 14: 5088.5442; 2020 15: 4801.1158; 2021 16: 4984.3394; 2022 17: 5174.2846; 2023 18: 4922.2017; 2024 19: 5109.2418; 2025 20: 5437.7918; 2026 21: 5926.0197
1 |  | Accumulated hours of use | 0 | 2017 12: 4720.0862; 2018 13: 9621.0664; 2019 14: 14709.6105; 2020 15: 19510.7263; 2021 16: 24495.0657; 2022 17: 29669.3503; 2023 18: 34591.552; 2024 19: 39700.7938; 2025 20: 45138.5856; 2026 21: 51064.6053
1 |  | Accumulated hours for Over hault Use |  | 2017 12: 4720.0862; 2018 13: 9621.0664; 2019 14: 14709.6105; 2020 15: 19510.7263; 2021 16: 4984.3394; 2022 17: 10158.6239; 2023 18: 15080.8256; 2024 19: 20190.0675; 2025 20: 5437.7918; 2026 21: 11363.8115
1 |  | Over hault | 2 | 2017 12: op; 2018 13: op; 2019 14: op; 2020 15: ovh; 2021 16: op; 2022 17: op; 2023 18: op; 2024 19: ovh; 2025 20: op; 2026 21: op
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 126.72 | 0 | 0
1 |  | GROUP-15 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 2019 14: 5088.5442; 2020 15: 4801.1158; 2021 16: 4984.3394; 2022 17: 5174.2846; 2023 18: 4922.2017; 2024 19: 5109.2418; 2025 20: 5437.7918; 2026 21: 5926.0197
1 |  | Accumulated hours of use | 0 | 2019 14: 5088.5442; 2020 15: 9889.6599; 2021 16: 14873.9993; 2022 17: 20048.2839; 2023 18: 24970.4856; 2024 19: 30079.7274; 2025 20: 35517.5193; 2026 21: 41443.5389
1 |  | Accumulated hours for Over hault Use |  | 2019 14: 5088.5442; 2020 15: 9889.6599; 2021 16: 14873.9993; 2022 17: 20048.2839; 2023 18: 4922.2017; 2024 19: 10031.4435; 2025 20: 15469.2354; 2026 21: 21395.2551
1 |  | Over hault | 2 | 2019 14: op; 2020 15: op; 2021 16: op; 2022 17: ovh; 2023 18: op; 2024 19: op; 2025 20: op; 2026 21: ovh
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 126.72
1 |  | GROUP-16 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 2023 18: 4922.2017; 2024 19: 5109.2418; 2025 20: 5437.7918; 2026 21: 5926.0197
1 |  | Accumulated hours of use | 0 | 2023 18: 4922.2017; 2024 19: 10031.4435; 2025 20: 15469.2354; 2026 21: 21395.2551
1 |  | Accumulated hours for Over hault Use |  | 2023 18: 4922.2017; 2024 19: 10031.4435; 2025 20: 15469.2354; 2026 21: 21395.2551
1 |  | Over hault | 1 | 2023 18: op; 2024 19: op; 2025 20: op; 2026 21: ovh
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.72
1 |  | GROUP-17 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 2026 21: 5926.0197
1 |  | Accumulated hours of use | 0 | 2026 21: 5926.0197
1 |  | Accumulated hours for Over hault Use |  | 2026 21: 5926.0197
1 |  | Over hault | 0 | bar: 2026 21
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | GROUP-18 (1100 kW) | 1100
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 19800
1 |  | Annual Hours of Use |  | 2020 15: 5868.0304; 2021 16: 6091.9704; 2022 17: 6324.1256; 2023 18: 6016.0243; 2024 19: 6244.6289; 2025 20: 6646.19; 2026 21: 7242.9129
1 |  | Accumulated hours of use | 0 | 2020 15: 5868.0304; 2021 16: 11960.0008; 2022 17: 18284.1263; 2023 18: 24300.1506; 2024 19: 30544.7795; 2025 20: 37190.9696; 2026 21: 44433.8825
1 |  | Accumulated hours for Over hault Use |  | 2020 15: 5868.0304; 2021 16: 11960.0008; 2022 17: 18284.1263; 2023 18: 6016.0243; 2024 19: 6244.6289; 2025 20: 12890.8189; 2026 21: 20133.7319
1 |  | Over hault | 2 | 2020 15: op; 2021 16: op; 2022 17: ovh; 2023 18: op; 2024 19: op; 2025 20: op; 2026 21: ovh
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154.88 | 0 | 0 | 0 | 154.88
1 |  | GROUP-19 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 2019 14: 5088.5442; 2020 15: 4801.1158; 2021 16: 4984.3394; 2022 17: 5174.2846; 2023 18: 4922.2017; 2024 19: 5109.2418; 2025 20: 5437.7918; 2026 21: 5926.0197
1 |  | Accumulated hours of use | 0 | 2019 14: 5088.5442; 2020 15: 9889.6599; 2021 16: 14873.9993; 2022 17: 20048.2839; 2023 18: 24970.4856; 2024 19: 30079.7274; 2025 20: 35517.5193; 2026 21: 41443.5389
1 |  | Accumulated hours for Over hault Use |  | 2019 14: 5088.5442; 2020 15: 9889.6599; 2021 16: 14873.9993; 2022 17: 20048.2839; 2023 18: 4922.2017; 2024 19: 10031.4435; 2025 20: 15469.2354; 2026 21: 21395.2551
1 |  | Over hault | 2 | 2019 14: op; 2020 15: op; 2021 16: op; 2022 17: ovh; 2023 18: op; 2024 19: op; 2025 20: op; 2026 21: ovh
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.72 | 0 | 0 | 0 | 126.72
1 |  | GROUP-20 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 2023 18: 4922.2017; 2024 19: 5109.2418; 2025 20: 5437.7918; 2026 21: 5926.0197
1 |  | Accumulated hours of use | 0 | 2023 18: 4922.2017; 2024 19: 10031.4435; 2025 20: 15469.2354; 2026 21: 21395.2551
1 |  | Accumulated hours for Over hault Use |  | 2023 18: 4922.2017; 2024 19: 10031.4435; 2025 20: 15469.2354; 2026 21: 21395.2551
1 |  | Over hault | 1 | 2023 18: op; 2024 19: op; 2025 20: op; 2026 21: ovh
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 126.72
1 |  | GROUP-21 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 2025 20: 5437.7918; 2026 21: 5926.0197
1 |  | Accumulated hours of use | 0 | 2025 20: 5437.7918; 2026 21: 11363.8115
1 |  | Accumulated hours for Over hault Use |  | 2025 20: 5437.7918; 2026 21: 11363.8115
1 |  | Over hault | 0 | bar: 2025 20 to 2026 21
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | GROUP-21 (900 kW) | 900
1 |  | Nominal Operation Hours | 18000 | 2005 0: 18000
0 |  | Total Energy MWH | 16200
1 |  | Annual Hours of Use |  | 2026 21: 5926.0197
1 |  | Accumulated hours of use | 0 | 2026 21: 5926.0197
1 |  | Accumulated hours for Over hault Use |  | 2026 21: 5926.0197
1 |  | Over hault | 0 | bar: 2026 21
0 |  | Over hault |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Over Hault Cost |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 |  | Total-Operation and Maintenance Costs |  | 4365.1677 | 4684.8213 | 4686.8491 | 4807.9535 | 5062.4442 | 5253.4392 | 5705.0242 | 5530.4136 | 6025.2302 | 5964.7859 | 6701.0419 | 6432.0488 | 7016.667 | 7188.0073 | 7453.2707 | 7601.5895 | 7886.7467 | 8717.4172 | 8488.8479 | 8806.5377 | 9009.1187 | 10265.6358
1 |  | SUMMARY
1 |  | TOTAL INVESTMENT COSTS - Thousands US-$ |  | 316.8 | 0 | 316.8 | 264 | 0 | 363 | 316.8 | 264 | 0 | 297 | 613.8 | 0 | 297 | 0 | 594 | 679.8 | 0 | 0 | 910.8 | 0 | 429 | 613.8
1 |  | TOTAL INVESTMENT COSTS - Thousands S/. |  | 1080.9216 | 0 | 1080.9216 | 900.768 | 0 | 1238.556 | 1080.9216 | 900.768 | 0 | 1013.364 | 2094.2856 | 0 | 1013.364 | 0 | 2026.728 | 2319.4776 | 0 | 0 | 3107.6496 | 0 | 1463.748 | 2094.2856
1 |  | TOTAL OPERATION AND MAINTENANCE COSTS- Thousands US-$ |  | 4365.1677 | 4684.8213 | 4686.8491 | 4807.9535 | 5062.4442 | 5253.4392 | 5705.0242 | 5530.4136 | 6025.2302 | 5964.7859 | 6701.0419 | 6432.0488 | 7016.667 | 7188.0073 | 7453.2707 | 7601.5895 | 7886.7467 | 8717.4172 | 8488.8479 | 8806.5377 | 9009.1187 | 10265.6358
1 |  | TOTAL OPERATION AND MAINTENANCE COSTS - Thousands S/. |  | 14893.9523 | 15984.6104 | 15991.5293 | 16404.7372 | 17273.0597 | 17924.7344 | 19465.5426 | 18869.7711 | 20558.0854 | 20351.8497 | 22863.9551 | 21946.1505 | 23940.8678 | 24525.4808 | 25430.5597 | 25936.6232 | 26909.5797 | 29743.8276 | 28963.9489 | 30047.9068 | 30739.113 | 35026.3493
1 |  | TOTAL COST |  | 4681.9677 | 4684.8213 | 5003.6491 | 5071.9535 | 5062.4442 | 5616.4392 | 6021.8242 | 5794.4136 | 6025.2302 | 6261.7859 | 7314.8419 | 6432.0488 | 7313.667 | 7188.0073 | 8047.2707 | 8281.3895 | 7886.7467 | 8717.4172 | 9399.6479 | 8806.5377 | 9438.1187 | 10879.4358
1 |  | TOTAL COST WITHOUT PROJECT -Thousand S/. |  | 15974.8739 | 15984.6104 | 17072.4509 | 17305.5052 | 17273.0597 | 19163.2904 | 20546.4642 | 19770.5391 | 20558.0854 | 21365.2137 | 24958.2407 | 21946.1505 | 24954.2318 | 24525.4808 | 27457.2877 | 28256.1008 | 26909.5797 | 29743.8276 | 32071.5985 | 30047.9068 | 32202.861 | 37120.6349
1 | 1 | a) Cost of installed new thermic groups |  | 2005 0: 352; 2006 1: $/kw
1 |  | b) Cost of Replacement of thermic groups |  | 2005 0: 330; 2006 1: $/kw
1 | 2 | Lubricants and Maintenance Costs |  | 2005 0: 41; 2006 1: $/MWh
1 | 3 | Cost in Over haul for new groups will be conducted with |  | 2005 0: 40%; 2006 1: of the investments of each group
1 |  | Groups Efficiency |  | 2005 0: 13.55; 2006 1: kwh/gal
1 | 4 | Purchase price of fuel Diesel |  | 2005 0: 7.461; 2006 1: S/. / gal.oil; 2007 2: (according to Osinerg publications for isolated systems type F: Pto. Maldonado)
1 |  |  |  | 2005 0: 2.1867; 2006 1: $ / gal.oil
1 | 5 | According to Superintendencia de Banca y seguros; in November 30th 2004; exchange rate : |  | 2005 0: 3.412; 2006 1: S/. / US$
|  | Total cost without project - thousand S/. "PERFIL" (initial evaluation, before pre feasibility and feasibility study) |  | 15305.3945 | 12527.7188 | 11948.0322 | 15207.4293 | 15820.8855 | 16830.8426 | 19196.0958 | 15011.5091 | 15624.5062 | 24307.2196 | 20685.9767 | 17460.7099 | 18073.707 | 23813.1203 | 23003.6774 | 23747.1907 | 21051.204 | 23119.7211 | 24393.3343 |  | 29075.1714 | 29075.1714
|  | NPV |  | 2005 0: 126970.9203; 2006 1: 126970.9203
|  |  |  | 152014.6763 | 134255.9959
100%
Additional Notes December 2008 (ELSE - DEUMAN)
GRUPO is GROUP (present in some equations)
Lines and columns in this color are the ones that where just reduced in the original document and now are open in order to have a fully readable document, many of them have no information | bar: 2013 8
Note on T217: pc04: grup 17

## F-01
FORM 1
ALTERNATIVES TO REACH THE CENTRAL OBJETIVE
ITEM | COMPONENTS | DESCRIPTION
Unique Alternative
Line - 138 kV San Gabán-Mazuko-67,6 km-200 mm² AAAC
TL-66kV Mazuko-Pto Mald-sector I- 26,8 km 200 mm² AAAC (Towers)
1 | Transmission Lines | TL-66kV Mazuko-Pto Mald-sector II- 125,9 km 200 mm² AAAC (Concrete Poles-rural area)
TL-66kV Mazuko-Pto Mald-sector III- 5,3 km 200 mm² AAAC (Concrete Poles -Urban area)
Expansion of the San Gabán 138 kV Substation
2 | Substations | Mazuko 138/66/33 kV 20-26/12,3-16/8-10,5 MVA Substation (ONAN/ONAF)
Puerto Maldonado 66/33/10 kV 12,3-16/3,9-5/12,3-16 MVA Substation (ONAN/ONAF)
3 | Comunications | Control and communications System

## F-02
FORM 2
GENERAL ANALYSIS OF THE PRODUCT OR SERVICE DEMAND
| A | CALCULATION PROCEDURE, IMPORTANT VARIABLES AND ASSUMPTIONS USED TO ESTIMATE THE DEMAND
For the demand study the next assumptions have been considered
- The energy supply will be permanent and reliable, without technical restrictions and at a reasonable cost, in order to cover the demand of the city and the productive loads
- It is considered that the construction starts its construction in 2006 and start operation in 207
| B | IMPORTANT VARIABLES
|  | Especial loads of medium voltage: |  |  | 23 Trade Management of ElectroSur Este
|  | Percentage of energy loses from the 10 kV bar |  |  | 8% Trade Management of ElectroSur Este
|  | Load Factor (low voltage) : |  |  | 43% Trade Management of ElectroSur Este
Effective power of the thermal power plants
|  | -CT Puerto Maldonado |  |  | 4200 | kW Trade Management of ElectroSur Este
|  | -CT Huepetuhe y Mazuko |  |  | 682 | kW Municipality
|  | Demand of the 23 especial loads connected to the project at the start: |  |  | 799.436 | kW Trade Management of ElectroSur Este
Efficiency of each plant kWH /gl
|  |  | Power Plant | kWh/gl
|  |  | Thermal | kWh/gal
|  |  | Puerto Maldonado | 13.64
|  |  | Huepetuhe | 10.61
|  |  | Mazuko pueblo | 8.08
| C.- | PROJECTION
1 | ITEM |  | Description /years | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
2 |  |  |  | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
3 | 1 | NUMBER OF BENEFIT PEOPLE
4 | 1.1 | Without project
5 | 1.1.1 | Puerto Maldonado
6 | a | City Puerto Maldonado
7 |  | -Domestic, commercial, general use |  | 29656 | 30427.056 | 31218.1595 | 32029.8316 | 32862.6072 | 33717.035 | 34593.6779 | 35493.1135 | 36415.9345 | 37362.7488 | 38334.1803 | 39330.869 | 40353.4715 | 41402.6618 | 42479.131 | 43583.5884 | 44716.7617 | 45879.3975 | 47072.2619 | 48296.1407 | 49551.8403 | 50840.1882
8 |  | -Especial loads |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
9 | b | Laberinto Circuit
10 |  | -Domestic, commercial, general use |  | 2435 | 2488.57 | 2543.3185 | 2599.2715 | 2656.4555 | 2714.8975 | 2774.6253 | 2835.667 | 2898.0517 | 2961.8089 | 3026.9687 | 3093.562 | 3161.6203 | 3231.176 | 3302.2618 | 3374.9116 | 3449.1597 | 3525.0412 | 3602.5921 | 3681.8491 | 3762.8498 | 3845.6325
11 |  | -Especial loads |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
12 | c | Planchón Circuit |  | 2153 | 2196.06 | 2239.9812 | 2284.7808 | 2330.4764 | 2377.086 | 2424.6277 | 2473.1202 | 2522.5826 | 2573.0343 | 2624.495 | 2676.9849 | 2730.5246 | 2785.1351 | 2840.8378 | 2897.6545 | 2955.6076 | 3014.7198 | 3075.0142 | 3136.5145 | 3199.2447 | 3263.2296
13 | d | Human location (poor areas) Home Associations
14 |  | -I Stage |  |  |  | 2116.0816 | 2164.7515 | 2214.5408 | 2265.4752 | 2317.5812 | 2370.8855 | 2425.4159 | 2481.2005 | 2538.2681 | 2596.6482 | 2656.3712 | 2717.4677 | 2779.9694 | 2843.9087 | 2909.3186 | 2976.233 | 3044.6863 | 3114.7141 | 3186.3525 | 3259.6387
15 |  | -II Stage |  |  |  |  | 1144.4705 | 1170.7933 | 1197.7216 | 1225.2692 | 1253.4504 | 1282.2797 | 1311.7722 | 1341.9429 | 1372.8076 | 1404.3822 | 1436.683 | 1469.7267 | 1503.5304 | 1538.1116 | 1573.4882 | 1609.6784 | 1646.701 | 1684.5751 | 1723.3203
16 |  | -III Stage | [5 empty] | 647.2768 | 662.1641 | 677.3939 | 692.974 | 708.9124 | 725.2173 | 741.8973 | 758.961 | 776.4171 | 794.2747 | 812.543 | 831.2315 | 850.3498 | 869.9079 | 889.9157 | 910.3838 | 931.3226 | 952.743
17 | 1.1.2 | Mazuko and Huapetuhe
18 | a | Mazuko Town |  | 2334 | 2385.348 | 2437.8257 | 2491.4578 | 2546.2699 | 2602.2878 | 2659.5382 | 2718.048 | 2777.8451 | 2838.9576 | 2901.4147 | 2965.2458 | 3030.4812 | 3097.1518 | 3165.2892 | 3234.9255 | 3306.0939 | 3378.828 | 3453.1622 | 3529.1318 | 3606.7726 | 3686.1216
19 | b | Huapetuhe |  | 3927 | 4013.394 | 4101.6887 | 4191.9258 | 4284.1482 | 4378.3994 | 4474.7242 | 4573.1682 | 4673.7779 | 4776.601 | 4881.6862 | 4989.0833 | 5098.8431 | 5211.0177 | 5325.6601 | 5442.8246 | 5562.5667 | 5684.9432 | 5810.012 | 5937.8322 | 6068.4645 | 6201.9707
20 | 1.2 | With project
21 | 1.2.1 | Puerto Maldonado
22 | a | City Puerto Maldonado
23 |  | -Domestic, commercial, general use |  | 29656 | 30427.056 | 31218.1595 | 32029.8316 | 32862.6072 | 33717.035 | 34593.6779 | 35493.1135 | 36415.9345 | 37362.7488 | 38334.1803 | 39330.869 | 40353.4715 | 41402.6618 | 42479.131 | 43583.5884 | 44716.7617 | 45879.3975 | 47072.2619 | 48296.1407 | 49551.8403 | 50840.1882
24 |  | -Especial loads |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
25 | b | Laberinto Circuit
26 |  | -Domestic, commercial, general use |  | 2435 | 2488.57 | 2543.3185 | 2599.2715 | 2656.4555 | 2714.8975 | 2774.6253 | 2835.667 | 2898.0517 | 2961.8089 | 3026.9687 | 3093.562 | 3161.6203 | 3231.176 | 3302.2618 | 3374.9116 | 3449.1597 | 3525.0412 | 3602.5921 | 3681.8491 | 3762.8498 | 3845.6325
27 |  | -Especial loads |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
28 | c | Planchón Circuit |  | 2153 | 2488.57 | 2543.3185 | 2599.2715 | 2656.4555 | 2714.8975 | 2774.6253 | 2835.667 | 2898.0517 | 2961.8089 | 3026.9687 | 3093.562 | 3161.6203 | 3231.176 | 3302.2618 | 3374.9116 | 3449.1597 | 3525.0412 | 3602.5921 | 3681.8491 | 3762.8498 | 3845.6325
29 | d | Human location (poor areas) Home Associations
30 |  | -I Stage |  | 2022 | 2069 | 2117 | 2165 | 2216 | 2266 | 2317 | 2371 | 2425 | 2481 | 2538 | 2597 | 2657 | 2718 | 2780 | 2845 | 2909 | 2975 | 3044 | 3114 | 3187 | 3259
31 |  | -II Stage |  | 1069 | 1092 | 1119 | 1145 | 1170 | 1197 | 1225 | 1254 | 1283 | 1312 | 1342 | 1374 | 1405 | 1437 | 1469 | 1504 | 1538 | 1574 | 1610 | 1647 | 1684 | 1724
32 |  | -III Stage |  | 591 | 604 | 619 | 632 | 648 | 663 | 677 | 692 | 710 | 726 | 743 | 759 | 777 | 795 | 811 | 832 | 850 | 871 | 891 | 910 | 931 | 952
33 | 1.2.2 | Mazuko and Huapetuhe
34 |  | Mazuko Town |  | 2334 | 2385.348 | 2437.8257 | 2491.4578 | 2546.2699 | 2602.2878 | 2659.5382 | 2718.048 | 2777.8451 | 2838.9576 | 2901.4147 | 2965.2458 | 3030.4812 | 3097.1518 | 3165.2892 | 3234.9255 | 3306.0939 | 3378.828 | 3453.1622 | 3529.1318 | 3606.7726 | 3686.1216
35 |  | Huapetuhe |  | 3927 | 4013.394 | 4101.6887 | 4191.9258 | 4284.1482 | 4378.3994 | 4474.7242 | 4573.1682 | 4673.7779 | 4776.601 | 4881.6862 | 4989.0833 | 5098.8431 | 5211.0177 | 5325.6601 | 5442.8246 | 5562.5667 | 5684.9432 | 5810.012 | 5937.8322 | 6068.4645 | 6201.9707
36 |  | Mine Loads from Huapetuhe |  | 0 | 0 | 41.95 | 61.95 | 82.95 | 93.95 | 104.95 | 107.9 | 110.85 | 115.8 | 118.75 | 121.7 | 126.65 | 129.6 | 132.55 | 137.5 | 140.45 | 143.4 | 148.35 | 151.3 | 154.25 | 159.2 | 74536.7455
37
38 | 2 | NUMBER OF SUBSCRIBERS
39 | 2.1 | Without project
40 | 2.1.1 | Puerto Maldonado
41 | a | City Puerto Maldonado
42 |  | -Domestic, commercial, general use |  | 9623 | 9925.4263 | 10237.0736 | 10558.217 | 10889.1395 | 11230.1327 | 11581.4965 | 11943.5396 | 12316.5799 | 12700.9444 | 13096.9699 | 13505.0029 | 13925.4 | 14358.5284 | 14804.7659 | 15264.5014 | 15738.1351 | 16226.079 | 16728.757 | 17246.6054 | 17780.0732 | 18329.6227
43 |  | -Especial loads |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
44 | b | Laberinto Circuit
45 |  | -Domestic, commercial, general use |  | 303 | 313.8854 | 325.1031 | 336.6625 | 348.5731 | 360.8448 | 373.4878 | 386.5125 | 399.9294 | 413.7497 | 427.9844 | 442.6452 | 457.744 | 473.2929 | 489.3043 | 505.7912 | 522.7667 | 540.2444 | 558.238 | 576.7618 | 595.8305 | 615.4591
46 |  | -Especial loads |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
47 | c | Planchón Circuit |  | 549 | 567.5863 | 586.6964 | 606.3439 | 626.5427 | 647.3068 | 668.6509 | 690.5898 | 713.1389 | 736.3136 | 760.1301 | 784.6047 | 809.7543 | 835.596 | 862.1474 | 889.4267 | 917.4523 | 946.2431 | 975.8186 | 1006.1987 | 1037.4036 | 1069.4542
48 | d | Human location (poor areas) Home Associations
49 |  | -I Stage |  |  |  | 416.8176 | 428.9126 | 441.3436 | 454.1194 | 467.2495 | 480.7434 | 494.6107 | 508.8617 | 523.5066 | 538.5559 | 554.0206 | 569.9118 | 586.2408 | 603.0196 | 620.26 | 637.9745 | 656.1757 | 674.8767 | 694.0909 | 713.8318
50 |  | -II Stage |  |  |  |  | 185.6878 | 191.0695 | 196.6005 | 202.2849 | 208.1267 | 214.1303 | 220.2999 | 226.64 | 233.1553 | 239.8504 | 246.7301 | 253.7994 | 261.0633 | 268.5272 | 276.1963 | 284.0761 | 292.1722 | 300.4906 | 309.037
51 |  | -III Stage | [5 empty] | 118.4092 | 121.8369 | 125.3596 | 128.9799 | 132.7004 | 136.5239 | 140.453 | 144.4906 | 148.6397 | 152.9032 | 157.2841 | 161.7857 | 166.4112 | 171.1639 | 176.0471 | 181.0645 | 186.2195 | 191.5159
52 | 2.1.2 | Mazuko and Huapetuhe
53 | a | Mazuko Town |  | 389 | 399.9135 | 411.1188 | 422.6237 | 434.4358 | 446.5631 | 459.0137 | 471.796 | 484.9186 | 498.3902 | 512.2198 | 526.4167 | 540.9904 | 555.9506 | 571.3071 | 587.0703 | 603.2505 | 619.8585 | 636.9053 | 654.4021 | 672.3606 | 690.7925
54 | b | Huapetuhe |  | 726 | 746.4104 | 767.3675 | 788.8854 | 810.9787 | 833.6623 | 856.9514 | 880.8618 | 905.4095 | 930.6109 | 956.483 | 983.0431 | 1010.3088 | 1038.2984 | 1067.0306 | 1096.5245 | 1126.7997 | 1157.8762 | 1189.7748 | 1222.5165 | 1256.1229 | 1290.6164
55 | 2.2 | With project
56 | 2.2.1 | Puerto Maldonado
57 | a | City Puerto Maldonado
58 |  | -Domestic, commercial, general use |  | 9623 | 9925.4263 | 10237.0736 | 10558.217 | 10889.1395 | 11230.1327 | 11581.4965 | 11943.5396 | 12316.5799 | 12700.9444 | 13096.9699 | 13505.0029 | 13925.4 | 14358.5284 | 14804.7659 | 15264.5014 | 15738.1351 | 16226.079 | 16728.757 | 17246.6054 | 17780.0732 | 18329.6227
59 |  | -Especial loads |  | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20 | 20
60 | b | Laberinto Circuit
61 |  | -Domestic, commercial, general use |  | 303 | 313.8854 | 325.1031 | 336.6625 | 348.5731 | 360.8448 | 373.4878 | 386.5125 | 399.9294 | 413.7497 | 427.9844 | 442.6452 | 457.744 | 473.2929 | 489.3043 | 505.7912 | 522.7667 | 540.2444 | 558.238 | 576.7618 | 595.8305 | 615.4591
62 |  | -Especial loads |  | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
63 | c | Planchón Circuit |  | 549 | 567.5863 | 586.6964 | 606.3439 | 626.5427 | 647.3068 | 668.6509 | 690.5898 | 713.1389 | 736.3136 | 760.1301 | 784.6047 | 809.7543 | 835.596 | 862.1474 | 889.4267 | 917.4523 | 946.2431 | 975.8186 | 1006.1987 | 1037.4036 | 1069.4542
64 | d | Human location (poor areas) Home Associations
65 |  | -I Stage |  |  |  | 416.8176 | 428.9126 | 441.3436 | 454.1194 | 467.2495 | 480.7434 | 494.6107 | 508.8617 | 523.5066 | 538.5559 | 554.0206 | 569.9118 | 586.2408 | 603.0196 | 620.26 | 637.9745 | 656.1757 | 674.8767 | 694.0909 | 713.8318
66 |  | -II Stage |  |  |  |  | 185.6878 | 191.0695 | 196.6005 | 202.2849 | 208.1267 | 214.1303 | 220.2999 | 226.64 | 233.1553 | 239.8504 | 246.7301 | 253.7994 | 261.0633 | 268.5272 | 276.1963 | 284.0761 | 292.1722 | 300.4906 | 309.037
67 |  | -III Stage | [5 empty] | 118.4092 | 121.8369 | 125.3596 | 128.9799 | 132.7004 | 136.5239 | 140.453 | 144.4906 | 148.6397 | 152.9032 | 157.2841 | 161.7857 | 166.4112 | 171.1639 | 176.0471 | 181.0645 | 186.2195 | 191.5159
68 | 2.2.2 | Mazuko and Huapetuhe
69 |  | Mazuko Town |  | 389 | 399.9135 | 411.1188 | 422.6237 | 434.4358 | 446.5631 | 459.0137 | 471.796 | 484.9186 | 498.3902 | 512.2198 | 526.4167 | 540.9904 | 555.9506 | 571.3071 | 587.0703 | 603.2505 | 619.8585 | 636.9053 | 654.4021 | 672.3606 | 690.7925
70 |  | Huapetuhe |  | 726 | 746.4104 | 767.3675 | 788.8854 | 810.9787 | 833.6623 | 856.9514 | 880.8618 | 905.4095 | 930.6109 | 956.483 | 983.0431 | 1010.3088 | 1038.2984 | 1067.0306 | 1096.5245 | 1126.7997 | 1157.8762 | 1189.7748 | 1222.5165 | 1256.1229 | 1290.6164
71 |  | Mine Loads from Huapetuhe |  | 0 | 0 | 41.95 | 61.95 | 82.95 | 93.95 | 104.95 | 107.9 | 110.85 | 115.8 | 118.75 | 121.7 | 126.65 | 129.6 | 132.55 | 137.5 | 140.45 | 143.4 | 148.35 | 151.3 | 154.25 | 159.2 | 23392.5295
72 | 3 | ENERGY DEMAND MWH-YEAR
73 | 3.1 | Without project
74 | 3.1.2 | Puerto Maldonado
75 | a | City Puerto Maldonado
76 |  | -Domestic, commercial, general use |  | 15043.7614 | 15689.9598 | 16361.4633 | 17059.1997 | 17784.1292 | 18537.2453 | 19319.5763 | 20132.1862 | 20976.176 | 21852.6849 | 22762.8916 | 23708.0158 | 24689.3191 | 25708.1068 | 26765.7294 | 27863.5839 | 29003.1152 | 30185.8182 | 31413.2391 | 32686.977 | 34008.686 | 35380.0769
77 |  | -Especial loads |  | 3676.2337 | 3744.5005 | 3814.2822 | 3885.6157 | 3958.5385 | 4033.0892 | 4109.3072 | 4187.2332 | 4266.9086 | 4348.3761 | 4431.6793 | 4516.8629 | 4603.9729 | 4693.0562 | 4784.1612 | 4877.3374 | 4972.6353 | 5070.107 | 5169.8059 | 5271.7865 | 5376.1049 | 5482.8185
78 | b | Laberinto Circuit
79 |  | -Domestic, commercial, general use |  | 1280.5043 | 1341.129 | 1404.2031 | 1469.814 | 1538.0517 | 1609.0094 | 1682.7831 | 1759.472 | 1839.1786 | 1922.0085 | 2008.071 | 2097.4786 | 2190.3477 | 2286.7983 | 2386.9542 | 2490.9433 | 2598.8975 | 2710.9529 | 2827.2499 | 2947.9336 | 3073.1533 | 3203.0634
80 |  | -Especial loads |  | 169.6826 | 173.7595 | 177.9391 | 182.224 | 186.6168 | 191.1204 | 195.7377 | 200.4714 | 205.3247 | 210.3006 | 215.4022 | 220.6328 | 225.9957 | 231.4943 | 237.1321 | 242.9127 | 248.8397 | 254.9169 | 261.1482 | 267.5376 | 274.0891 | 280.8068
81 | c | Planchón Circuit |  | 772.8727 | 807.8868 | 844.2343 | 881.9593 | 921.1072 | 961.725 | 1003.861 | 1047.5647 | 1092.8875 | 1139.8821 | 1188.6027 | 1239.1053 | 1291.4474 | 1345.6884 | 1401.8892 | 1460.1127 | 1520.4236 | 1582.8885 | 1647.5758 | 1714.5563 | 1783.9024 | 1855.689
82 | d | Human location (poor areas) Home Associations
83 |  | -I Stage |  | 0 | 0 | 431.2247 | 448.6758 | 466.7605 | 485.5003 | 504.917 | 525.0333 | 545.8726 | 567.4589 | 589.8172 | 612.973 | 636.9529 | 661.784 | 687.4946 | 714.1137 | 741.6712 | 770.198 | 799.7259 | 830.2877 | 861.9173 | 894.6497
84 |  | -II Stage |  | 0 | 0 | 0 | 134.619 | 140.0753 | 145.7298 | 151.5893 | 157.6605 | 163.9506 | 170.467 | 177.217 | 184.2086 | 191.4498 | 198.9487 | 206.7141 | 214.7546 | 223.0794 | 231.6978 | 240.6195 | 249.8545 | 259.4129 | 269.3056
85 |  | -III Stage |  | 0 | 0 | 0 | 0 | 86.8072 | 90.3114 | 93.9426 | 97.7051 | 101.6032 | 105.6415 | 109.8246 | 114.1575 | 118.6449 | 123.2922 | 128.1045 | 133.0874 | 138.2464 | 143.5874 | 149.1163 | 154.8394 | 160.7629 | 166.8936
86 | 3.1.2 | Mazuko and Huapetuhe
87 | a | Mazuko Town |  | 725.9247 | 754.3958 | 783.8658 | 814.367 | 845.9329 | 878.5976 | 912.3966 | 947.3664 | 983.5443 | 1020.9693 | 1059.681 | 1099.7205 | 1141.1303 | 1183.9537 | 1228.2358 | 1274.0227 | 1321.3622 | 1370.3031 | 1420.8962 | 1473.1934 | 1527.2483 | 1583.1161
88 | b | Huapetuhe |  | 1022.0502 | 1062.4202 | 1104.2132 | 1147.4755 | 1192.2545 | 1238.5995 | 1286.5609 | 1336.1908 | 1387.5429 | 1440.6724 | 1495.6365 | 1552.4937 | 1611.3045 | 1672.1313 | 1735.0382 | 1800.0914 | 1867.359 | 1936.9112 | 2008.8202 | 2083.1605 | 2160.0087 | 2239.4439
89 | 2.2 | With project
90 | 2.2.1 | Puerto Maldonado
91 | a | City Puerto Maldonado
92 |  | -Domestic, commercial, general use |  | 0 | 0 | 17997.6096 | 18765.1197 | 19562.5421 | 20390.9698 | 21251.5339 | 22145.4048 | 23073.7936 | 24037.9534 | 25039.1808 | 26078.8174 | 27158.251 | 28278.9175 | 29442.3024 | 30649.9423 | 31903.4267 | 33204.4 | 34554.563 | 35955.6747 | 37409.5546 | 38918.0846
93 |  | -Especial loads |  | 0 | 0 | 3976.2144 | 4135.263 | 4300.6735 | 4472.7004 | 4588.9906 | 4708.3044 | 4830.7203 | 4956.319 | 5085.1833 | 5217.3981 | 5353.0504 | 5492.2298 | 5635.0277 | 5781.5385 | 5931.8585 | 6086.0868 | 6244.325 | 6406.6775 | 6573.2511 | 6744.1556
94 | b | Laberinto Circuit
95 |  | -Domestic, commercial, general use |  | 0 | 0 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548 | 1408.5548
96 |  | -Especial loads |  | 0 | 0 | 183.5287 | 190.8698 | 198.5046 | 206.4448 | 211.8124 | 217.3195 | 222.9698 | 228.767 | 234.715 | 240.8176 | 247.0788 | 253.5029 | 260.094 | 266.8564 | 273.7947 | 280.9133 | 288.2171 | 295.7107 | 303.3992 | 311.2876
97 | c | Planchón Circuit |  | 0 | 0 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599 | 850.1599
98 | d | Human location (poor areas) Home Associations
99 |  | -I Stage |  | 0 | 0 | 474.3472 | 493.5433 | 513.4366 | 534.0504 | 555.4087 | 577.5367 | 600.4599 | 624.2048 | 648.7989 | 674.2703 | 700.6481 | 727.9624 | 756.2441 | 785.5251 | 815.8383 | 847.2178 | 879.6985 | 913.3165 | 948.1091 | 984.1147
100 |  | -II Stage |  | 0 | 0 | 0 | 148.0809 | 154.0828 | 160.3028 | 166.7482 | 173.4265 | 180.3457 | 187.5137 | 194.9387 | 202.6295 | 210.5947 | 218.8436 | 227.3855 | 236.2301 | 245.3873 | 254.8676 | 264.6814 | 274.8399 | 285.3542 | 296.2361
101 |  | -III Stage |  | 0 | 0 | 0 | 0 | 95.4879 | 99.3426 | 103.3369 | 107.4756 | 111.7635 | 116.2056 | 120.8071 | 125.5732 | 130.5094 | 135.6214 | 140.915 | 146.3961 | 152.071 | 157.9461 | 164.0279 | 170.3233 | 176.8392 | 183.5829
102 | 2.2.2 | Mazuko and Huapetuhe
103 |  | Mazuko Town |  | 0 | 0 | 862.2523 | 895.8037 | 930.5261 | 966.4574 | 1003.6363 | 1042.103 | 1081.8988 | 1123.0662 | 1165.6491 | 1209.6926 | 1255.2433 | 1302.3491 | 1351.0594 | 1401.425 | 1453.4984 | 1507.3334 | 1562.9858 | 1620.5127 | 1679.9731 | 1741.4277
104 |  | Huapetuhe |  | 0 | 0 | 1214.6345 | 1262.223 | 1311.48 | 1362.4595 | 1415.217 | 1469.8099 | 1526.2972 | 1584.7397 | 1645.2001 | 1707.743 | 1772.4349 | 1839.3444 | 1908.542 | 1980.1006 | 2054.0949 | 2130.6023 | 2209.7022 | 2291.4765 | 2376.0096 | 2463.3882
105 |  | Mine Loads from Huapetuhe |  | 0 | 0 | 11355.026 | 16768.626 | 22452.906 | 25430.386 | 28407.866 | 29206.372 | 30004.878 | 31344.744 | 32143.25 | 32941.756 | 34281.622 | 35080.128 | 35878.634 | 37218.5 | 38017.006 | 38815.512 | 40155.378 | 40953.884 | 41752.39 | 43092.256
106 | 4 | ENERGY AND POWER INTO THE SYSTEM
107 | 4.1 | Sin Proyecto
108 | 4.1.1 | Puerto Maldonado
109 | a. | Domestic, commercial, general use
110 |  | Energy into the system (MWh) |  | 17097.1384 | 17838.9755 | 18609.9007 | 19410.9729 | 20243.2881 | 21107.9797 | 22006.2203 | 22939.2229 | 23908.2421 | 24914.5755 | 25959.5653 | 27044.5997 | 28171.1142 | 29340.5935 | 30554.5729 | 31814.6399 | 33122.4363 | 34479.6596 | 35888.0648 | 37349.4668 | 38865.7417 | 40438.8293
111 |  | Power into the system (KW) |  | 4712.7511 | 4863.2071 | 5018.2308 | 5177.9567 | 5342.5233 | 5512.073 | 5686.7526 | 5866.7127 | 6052.1087 | 6243.1 | 6439.8512 | 6642.531 | 6851.3134 | 7066.3772 | 7287.9066 | 7516.0907 | 7751.1244 | 7993.208 | 8242.5478 | 8499.3556 | 8763.8497 | 9036.2546
112 |  | Load Factor |  | 0.41414 | 0.41874 | 0.42334 | 0.42794 | 0.43254 | 0.43715 | 0.44175 | 0.44635 | 0.45096 | 0.45556 | 0.46017 | 0.46478 | 0.46938 | 0.47399 | 0.4786 | 0.4832 | 0.48781 | 0.49242 | 0.49703 | 0.50164 | 0.50625 | 0.51086
113 | b. | Especial loads
114 |  | Energy into the system (MWh) |  | 3845.9163 | 3918.26 | 3992.2213 | 4067.8397 | 4145.1553 | 4224.2096 | 4305.0449 | 4387.7046 | 4472.2334 | 4558.6767 | 4647.0815 | 4737.4957 | 4829.9686 | 4924.5506 | 5021.2934 | 5120.2501 | 5221.475 | 5325.024 | 5430.9541 | 5539.3241 | 5650.1939 | 5763.6254
115 |  | Power into the system (KW) |  | 799.436 | 814.0662 | 829.0199 | 844.3048 | 859.9289 | 875.9004 | 892.2279 | 908.9199 | 925.9852 | 943.433 | 961.2726 | 979.5134 | 998.1654 | 1017.2385 | 1036.7429 | 1056.6894 | 1077.0885 | 1097.9516 | 1119.2898 | 1141.1149 | 1163.4388 | 1186.2737
116 |  | Load Factor |  | 0.54918 | 0.54945 | 0.54973 | 0.55 | 0.55027 | 0.55054 | 0.5508 | 0.55107 | 0.55134 | 0.5516 | 0.55186 | 0.55212 | 0.55238 | 0.55264 | 0.55289 | 0.55315 | 0.5534 | 0.55365 | 0.5539 | 0.55414 | 0.55439 | 0.55463
117 | c. | Total
118 |  | Energy into the system (MWh) |  | 20943.0547 | 21757.2355 | 22602.122 | 23478.8126 | 24388.4434 | 25332.1893 | 26311.2653 | 27326.9276 | 28380.4754 | 29473.2522 | 30606.6468 | 31782.0954 | 33001.0828 | 34265.1441 | 35575.8662 | 36934.89 | 38343.9113 | 39804.6835 | 41319.019 | 42888.7909 | 44515.9357 | 46202.4546
119 |  | Power into the system (KW) |  | 5512.187 | 5677.2733 | 5964.1625 | 6179.9852 | 6388.6409 | 6579.5989 | 6776.1936 | 6978.5887 | 7186.9523 | 7401.4575 | 7622.2824 | 7849.6098 | 8083.6283 | 8324.5313 | 8572.5182 | 8827.7938 | 9090.5689 | 9361.0601 | 9639.4905 | 9926.0893 | 10221.0923 | 10524.7421
120 |  | Load Factor |  | 0.43372 | 0.43748 | 0.43261 | 0.4337 | 0.43578 | 0.43951 | 0.44325 | 0.44701 | 0.45079 | 0.45458 | 0.45838 | 0.4622 | 0.46603 | 0.46988 | 0.47374 | 0.47762 | 0.48151 | 0.48541 | 0.48932 | 0.49324 | 0.49718 | 0.50113
121 | 4.2 | Con Proyecto
122 | 4.2.1 | Puerto Maldonado
123 | a. | Domestic, commercial, general use
124 |  | Energy into the system (MWh) |  | 0 | 0 | 20945.2379 | 21845.6136 | 22781.0535 | 23752.828 | 24762.2511 | 25810.6819 | 26899.5262 | 28030.2379 | 29204.3208 | 30423.33 | 31688.8738 | 33002.6153 | 34366.2742 | 35781.629 | 37250.5183 | 38774.8433 | 40356.5698 | 41997.73 | 43700.425 | 45466.8268
125 |  | Power into the system (KW) |  | 0 | 0 | 5648.6569 | 5828.1117 | 6012.9959 | 6203.4689 | 6399.6948 | 6601.8427 | 6810.0861 | 7024.604 | 7245.5801 | 7473.2038 | 7707.6696 | 7949.1777 | 8197.9342 | 8454.151 | 8718.0461 | 8989.8437 | 9269.7746 | 9558.076 | 9854.9922 | 10160.7742
126 |  | Load Factor |  |  |  | 0.42329 | 0.42789 | 0.43249 | 0.4371 | 0.4417 | 0.4463 | 0.45091 | 0.45551 | 0.46012 | 0.46472 | 0.46933 | 0.47394 | 0.47855 | 0.48315 | 0.48776 | 0.49237 | 0.49698 | 0.50159 | 0.5062 | 0.51082
127 | b. | Especial loads
128 |  | Energy into the system (MWh) |  | 0 | 0 | 4159.7431 | 4326.1328 | 4499.1781 | 4679.1453 | 4800.803 | 4925.6239 | 5053.6901 | 5185.0861 | 5319.8983 | 5458.2157 | 5600.1293 | 5745.7326 | 5895.1217 | 6048.3948 | 6205.6531 | 6367.0001 | 6532.5421 | 6702.3882 | 6876.6503 | 7055.4432
129 |  | Power into the system (KW) |  | 0 | 0 | 864.6699 | 899.2567 | 935.227 | 972.6361 | 997.9246 | 1023.8706 | 1050.4913 | 1077.8041 | 1105.827 | 1134.5785 | 1164.0775 | 1194.3435 | 1225.3964 | 1257.2568 | 1289.9454 | 1323.484 | 1357.8946 | 1393.1999 | 1429.4231 | 1466.5881
130 |  | Load Factor |  |  |  | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918 | 0.54918
131 | c. | Total Puerto Maldonado
132 |  | Energy into the system (MWh) |  | 0 | 0 | 25104.981 | 26171.7464 | 27280.2316 | 28431.9733 | 29563.0541 | 30736.3058 | 31953.2163 | 33215.324 | 34524.2191 | 35881.5457 | 37289.003 | 38748.3479 | 40261.3959 | 41830.0238 | 43456.1714 | 45141.8434 | 46889.1119 | 48700.1182 | 50577.0753 | 52522.27
133 |  | Power into the system (KW) |  | 0 | 0 | 6513.3268 | 6727.3685 | 6948.2229 | 7176.1049 | 7397.6194 | 7625.7133 | 7860.5774 | 8102.408 | 8351.4071 | 8607.7823 | 8871.7471 | 9143.5212 | 9423.3307 | 9711.4078 | 10007.9915 | 10313.3277 | 10627.6692 | 10951.2759 | 11284.4153 | 11627.3623
134 |  | Load Factor |  |  |  | 0.44 | 0.4441 | 0.4482 | 0.45229 | 0.4562 | 0.46012 | 0.46404 | 0.46797 | 0.47191 | 0.47586 | 0.47981 | 0.48377 | 0.48773 | 0.4917 | 0.49568 | 0.49966 | 0.50365 | 0.50765 | 0.51165 | 0.51565
135 | 4.2.2 | Mazuko
136 | a. | Domestic, commercial, general use
137 |  | Energy into the system (MWh) |  | 0 | 0 | 2076.8868 | 2158.0267 | 2242.0061 | 2328.9168 | 2418.8533 | 2511.9129 | 2608.1959 | 2707.8059 | 2810.8492 | 2917.4356 | 3027.6782 | 3141.6935 | 3259.6014 | 3381.5256 | 3507.5933 | 3637.9358 | 3772.688 | 3911.9892 | 4055.9827 | 4204.816
138 |  | Power into the system (KW) |  | 0 | 0 | 1991.079 | 2048.6366 | 2107.7498 | 2168.4591 | 2230.8063 | 2294.8342 | 2360.5866 | 2428.1085 | 2497.446 | 2568.6464 | 2641.7581 | 2716.8309 | 2793.9156 | 2873.0646 | 2954.3315 | 3037.7711 | 3123.4398 | 3211.3952 | 3301.6967 | 3394.4049
139 |  | Load Factor |  |  |  | 0.11907 | 0.12025 | 0.12143 | 0.1226 | 0.12378 | 0.12495 | 0.12613 | 0.1273 | 0.12848 | 0.12966 | 0.13083 | 0.13201 | 0.13318 | 0.13436 | 0.13553 | 0.13671 | 0.13788 | 0.13906 | 0.14023 | 0.14141
140 | b. | Mine Loads Huapetuhe
141 |  | Energy into the system (MWh) |  | 0 | 0 | 11355.026 | 16768.626 | 22452.906 | 25430.386 | 28407.866 | 29206.372 | 30004.878 | 31344.744 | 32143.25 | 32941.756 | 34281.622 | 35080.128 | 35878.634 | 37218.5 | 38017.006 | 38815.512 | 40155.378 | 40953.884 | 41752.39 | 43092.256
142 |  | Power into the system (KW) |  | 0 | 0 | 1375.0996 | 2030.6894 | 2719.0587 | 3079.6331 | 3440.2075 | 3536.907 | 3633.6064 | 3795.8649 | 3892.5644 | 3989.2639 | 4151.5224 | 4248.2219 | 4344.9214 | 4507.1799 | 4603.8793 | 4700.5788 | 4862.8373 | 4959.5368 | 5056.2363 | 5218.4948
143 |  | Load Factor |  |  |  | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265 | 0.94265
144 | c. | Total Mazuko
145 |  | Energy into the system (MWh) |  | 0 | 0 | 13431.9128 | 18926.6527 | 24694.9121 | 27759.3028 | 30826.7193 | 31718.2849 | 32613.0739 | 34052.5499 | 34954.0992 | 35859.1916 | 37309.3002 | 38221.8215 | 39138.2354 | 40600.0256 | 41524.5993 | 42453.4478 | 43928.066 | 44865.8732 | 45808.3727 | 47297.072
146 |  | Power into the system (KW) |  | 0 | 0 | 3366.1786 | 4079.326 | 4826.8084 | 5248.0922 | 5671.0138 | 5831.7412 | 5994.1931 | 6223.9735 | 6390.0104 | 6557.9103 | 6793.2805 | 6965.0527 | 7138.837 | 7380.2445 | 7558.2108 | 7738.3499 | 7986.2771 | 8170.932 | 8357.933 | 8612.8997
147 |  | Load Factor |  |  |  | 0.45551 | 0.52964 | 0.58404 | 0.60381 | 0.62053 | 0.62088 | 0.62109 | 0.62457 | 0.62444 | 0.62421 | 0.62695 | 0.62644 | 0.62585 | 0.62799 | 0.62717 | 0.62627 | 0.6279 | 0.62682 | 0.62567 | 0.62687
148 | 4.2.3 | Total
149 |  | Energy into the system (MWh) |  | 0 | 0 | 38536.8938 | 45098.3991 | 51975.1438 | 56191.2761 | 60389.7734 | 62454.5907 | 64566.2902 | 67267.8738 | 69478.3183 | 71740.7373 | 74598.3033 | 76970.1694 | 79399.6313 | 82430.0494 | 84980.7707 | 87595.2912 | 90817.1779 | 93565.9914 | 96385.4479 | 99819.342
150 |  | Power into the system (KW) |  | 0 | 0 | 9879.5054 | 10806.6945 | 11775.0313 | 12424.1971 | 13068.6332 | 13457.4545 | 13854.7705 | 14326.3815 | 14741.4176 | 15165.6926 | 15665.0276 | 16108.574 | 16562.1677 | 17091.6523 | 17566.2024 | 18051.6777 | 18613.9463 | 19122.208 | 19642.3483 | 20240.2619
151 |  | Load Factor |  |  |  | 0.44528 | 0.47639 | 0.50388 | 0.51629 | 0.52751 | 0.52978 | 0.53199 | 0.536 | 0.53803 | 0.54001 | 0.54362 | 0.54546 | 0.54726 | 0.55055 | 0.55225 | 0.55394 | 0.55696 | 0.55857 | 0.56016 | 0.56298
152
153 |  | Variable for the sensitivity analysis of electricity demand - Puerto Maldonado |  | 2007 1: 100%
154 | bar: 2005 -1 to 2007 1
155 |  | Variable for the sensitivity analysis of electricity demand - Mazuco |  | 2007 1: 100%
156
157 |  | PSE Puerto (small electric system) |  | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
158 |  | Energy into the system (MWh) |  | 0 | 0 | 0 | 0 | 0 | 2619.3266 | 2838.9253 | 3017.6076 | 3204.4363 | 3401.476 | 3607.7931 | 3824.4557 | 4050.5339 | 4288.0994 | 4539.2262 | 4800.9901 | 5149.4691 | 5517.743 | 5905.894 | 6313.0065 | 6743.1671 | 6995.4647
159 |  | Power into the system (KW) |  | 0 | 0 | 0 | 0 | 0 | 590.4935 | 614.3205 | 636.3707 | 658.854 | 682.0804 | 705.9604 | 730.6045 | 755.8233 | 782.0281 | 808.83 | 830.1405 | 859.4715 | 889.9349 | 921.143 | 953.2084 | 992.944 | 1023.1627
160 |  | Load Factor | [6 empty] | 0.50637 | 0.52754 | 0.54131 | 0.55521 | 0.56928 | 0.58339 | 0.59756 | 0.61177 | 0.62595 | 0.64065 | 0.6602 | 0.68395 | 0.70778 | 0.7319 | 0.75604 | 0.77524 | 0.78049
161 |  | PSE Iberia
162 |  | Energy into the system (MWh) |  | 0 | 0 | 0 | 0 | 2306.4205 | 2470.2752 | 2646.3122 | 2791.6581 | 2946.2651 | 3107.2037 | 3275.5465 | 3454.3683 | 3639.746 | 3835.7589 | 4039.4883 | 4255.0181 | 4529.4347 | 4818.8269 | 5125.2861 | 5446.9062 | 5787.7842 | 6010.0195
163 |  | Power into the system (KW) |  | 0 | 0 | 0 | 0 | 661.1148 | 683.4673 | 706.8081 | 728.5288 | 750.9362 | 773.9427 | 797.5606 | 821.903 | 847.0828 | 872.9137 | 899.6093 | 923.2839 | 952.7518 | 983.328 | 1014.6276 | 1047.0663 | 1080.9599 | 1112.0248
164 |  | Load Factor | [5 empty] | 0.39825 | 0.41259 | 0.4274 | 0.43743 | 0.44788 | 0.45831 | 0.46883 | 0.47978 | 0.4905 | 0.50162 | 0.51259 | 0.52609 | 0.5427 | 0.55942 | 0.57664 | 0.59384 | 0.61122 | 0.61696
165 |  | PSE Mazuko
166 |  | Energy into the system (MWh) |  | 0 | 0 | 0 | 0 | 0 | 0 | 1698.8614 | 1777.7709 | 1859.1808 | 1946.1336 | 2034.6725 | 2127.8422 | 2224.6883 | 2326.2578 | 2430.5987 | 2540.7605 | 2673.7938 | 2814.7506 | 2960.6842 | 3113.6492 | 3273.7018 | 3386.8996
167 |  | Power into the system (KW) |  | 0 | 0 | 0 | 0 | 0 | 0 | 493.4879 | 506.8589 | 520.7113 | 534.7513 | 549.1852 | 564.0194 | 579.2607 | 594.7157 | 610.7914 | 625.2948 | 642.2331 | 659.6136 | 677.4438 | 695.7315 | 716.7844 | 735.0106
168 |  | Load Factor | [7 empty] | 0.39299 | 0.40039 | 0.40759 | 0.41545 | 0.42293 | 0.43067 | 0.43842 | 0.44652 | 0.45427 | 0.46385 | 0.47526 | 0.48713 | 0.4989 | 0.51089 | 0.52137 | 0.52602
|  | TOTAL ENERGY |  | 0 | 0 | 0 | 0 | 2306.4205 | 5089.6018 | 7184.0988 | 7587.0365 | 8009.8822 | 8454.8133 | 8918.0121 | 9406.6662 | 9914.9682 | 10450.1161 | 11009.3132 | 11596.7688 | 12352.6976 | 13151.3205 | 13991.8643 | 14873.562 | 15804.6531 | 16392.3838
|  | TOTAL POWER |  | 0 | 0 | 0 | 0 | 661.1148 | 1273.9608 | 1814.6165 | 1871.7584 | 1930.5015 | 1990.7744 | 2052.7062 | 2116.5269 | 2182.1669 | 2249.6575 | 2319.2307 | 2378.7192 | 2454.4564 | 2532.8765 | 2613.2145 | 2696.0062 | 2790.6883 | 2870.1982
DO NOT DELETE
|  | SENSITIVITY 01 |  | 2005: 100%
SENSITIVITY 02 | bar: 2005
Pérdidas de potencia en MW
[27 empty] | Pérdidas en el tramo de línea Sandia-Ananea | [6 empty] | 0.159 |  |  |  |  | 0.095 | [9 empty] | 0.067
[27 empty] | Resto del Sistema | [6 empty] | 0.219 |  |  |  |  | 0.498 | [9 empty] | 0.553
Pérdidas de energía en MWh-año
[27 empty] | Pérdidas en el tramo de línea Sandia-Ananea |  | 0 | 0 | 0 | 0 | 0 | 601.7069 | 0 | 0 | 0 | 0 | 359.5104 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 253.5494
[27 empty] | Resto del Sistema |  | 0 | 0 | 0 | 0 | 0 | 828.7661 | 0 | 0 | 0 | 0 | 1884.5914 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2092.729
[27 empty] | TOTAL |  | 0 | 0 | 0 | 0 | 0 | 1430.473 | 0 | 0 | 0 | 0 | 2244.1018 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2346.2784
[29 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
[28 empty] | Factor de carga-Sandia-Azángaro | 0.6 |  | Factor de pérdidas-Sandia-Azángaro | [5 empty] | 0.432
[28 empty] | Factor de carga-resto del sistema | 0.35 |  | Factor de pérdidas-resto del sistema | [5 empty] | 0.19075

## F-03
FORM 3
ANALYSIS OF THE SUPPLY OF PRODUCTS OR SERVICES
a) Describe the calculation procedure, important variables and assumptions used to estimate the supply
Current sources for the supply of electricity for the project are:
- National Interconnected System-SINAC (SEIN), in the Infinite Busbar Infinite Machupiccho 138-kV with energy from the HPP San gabán and the System
- The supply of energy will be permanent and reliable, without technical restrictions and reasonable cost, covering the demand of each locality and the current and future mining load
- It is considered that the construction of the project will begin in 2006 and will be put into service in 2007
Time of | DESCRIPTION | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
Year |  | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
All the year | Mazuko S.S. Supply (1) |  |  | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29 | 10.29
All the year | Puerto Maldonado S.S. Supply (2) |  |  | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68 | 15.68
Notes:
(1) The supply is limited by the power of Mazuko 138/66/33kV - 20-26/12,3-16/8-10,5 MVA (ONAN/ONAF)transfor. , which in its reeling at 33 kV can provide up to 9.45 MW
(2) The supply is limites by the power of Puerto 66/33/10 kV - 16-12,3/3,9-5/12,3-16 MVA (ONAN/ONAF) transformator, equivalent to 15,2 MW, which is the transmission capacity of 66 kV Mazuko - Puerto Maldonado line
(3) The lines as the substations are designed to provide power to SESs of Puerto Maldonado, Iberia and Mazuko, for vegetative growth of cities with electric service
(Puerto Maldonado, Iberia Iñapari, Mazuko and Huapetuhe), and the mining charges in Mazuko
(4) The supply in Mazuko S.S. can be increased from 23.4 MW Total (reeled in 138 kV) to 30.1 MW, which is the transmission capacity of the 138 kV San Gabán - Mazuko line

## F-04
FORM 4
SUPPLY - DEMAND BALANCE IN MARKET OF THE PRODUCT OR SERVICE
YEAR |  | Demands Considered for the Evaluation (1) | [9 empty] | Total Demands considered for the design of TT.LL. and SS.SS. (2)
|  | Demand -kW |  |  |  | Supply-kW |  |  | Superhabit or Deficit (kW) |  |  | Demand -kW |  |  |  | Supply-kW |  |  | Superhabit or Deficit (kW)
|  | S.S. Mazuko | S.S. Puerto | Loses of TL and Transf. | Total | S.S. Mazuko | S.S. Puerto | Total | S.S. Mazuko | S.S. Puerto | Total | S.S. Mazuko | S.S. Puerto | Loses of TL and Transf. | Total | S.S. Mazuko | S.S. Puerto | Total | S.S. Mazuko | S.S. Puerto | Total
|  | (1) | (1) | (3) | (4) | (5) | (6) | (7) | (8) | (8) | (8) | (2) | (2) | (3) | (4) | (5) | (6) | (7) | (8) | (8) | (8)
0 | 2006
1 | 2007 | 3366.1786 | 6513.3268 | 65.1333 | 9944.6386 | 10290 | 15680 | 25970 | 6858.6882 | 9166.6732 | 16025.3614 | 3366.1786 | 6513.3268 | 65.1333 | 9944.6386 | 10290 | 15680 | 25970 | 6858.6882 | 9166.6732 | 16025.3614
2 | 2008 | 4079.326 | 6727.3685 | 67.2737 | 10873.9681 | 10290 | 15680 | 25970 | 6143.4003 | 8952.6315 | 15096.0319 | 4079.326 | 6727.3685 | 67.2737 | 10873.9681 | 10290 | 15680 | 25970 | 6143.4003 | 8952.6315 | 15096.0319
3 | 2009 | 4826.8084 | 6948.2229 | 69.4822 | 11844.5135 | 10290 | 15680 | 25970 | 5393.7093 | 8731.7771 | 14125.4865 | 4826.8084 | 7609.3377 | 76.0934 | 12512.2395 | 10290 | 15680 | 25970 | 5387.0982 | 8070.6623 | 13457.7605
4 | 2010 | 5248.0922 | 7176.1049 | 71.761 | 12495.9581 | 10290 | 15680 | 25970 | 4970.1468 | 8503.8951 | 13474.0419 | 5248.0922 | 8450.0657 | 84.5007 | 13782.6585 | 10290 | 15680 | 25970 | 4957.4072 | 7229.9343 | 12187.3415
5 | 2011 | 5671.0138 | 7397.6194 | 73.9762 | 13142.6094 | 10290 | 15680 | 25970 | 4545.01 | 8282.3806 | 12827.3906 | 6164.5016 | 8718.7481 | 87.1875 | 14970.4372 | 10290 | 15680 | 25970 | 4038.3109 | 6961.2519 | 10999.5628
6 | 2012 | 5831.7412 | 7625.7133 | 76.2571 | 13533.7116 | 10290 | 15680 | 25970 | 4382.0017 | 8054.2867 | 12436.2884 | 6338.6001 | 8990.6128 | 89.9061 | 15419.119 | 10290 | 15680 | 25970 | 3861.4938 | 6689.3872 | 10550.881
7 | 2013 | 5994.1931 | 7860.5774 | 78.6058 | 13933.3763 | 10290 | 15680 | 25970 | 4217.2011 | 7819.4226 | 12036.6237 | 6514.9044 | 9270.3676 | 92.7037 | 15877.9757 | 10290 | 15680 | 25970 | 3682.3919 | 6409.6324 | 10092.0243
8 | 2014 | 6223.9735 | 8102.408 | 81.0241 | 14407.4056 | 10290 | 15680 | 25970 | 3985.0025 | 7577.592 | 11562.5944 | 6758.7247 | 9558.4311 | 95.5843 | 16412.7402 | 10290 | 15680 | 25970 | 3435.691 | 6121.5689 | 9557.2598
9 | 2015 | 6390.0104 | 8351.4071 | 83.5141 | 14824.9316 | 10290 | 15680 | 25970 | 3816.4755 | 7328.5929 | 11145.0684 | 6939.1956 | 9854.9282 | 98.5493 | 16892.6731 | 10290 | 15680 | 25970 | 3252.2551 | 5825.0718 | 9077.3269
10 | 2016 | 6557.9103 | 8607.7823 | 86.0778 | 15251.7704 | 10290 | 15680 | 25970 | 3646.0119 | 7072.2177 | 10718.2296 | 7121.9297 | 10160.2897 | 101.6029 | 17383.8223 | 10290 | 15680 | 25970 | 3066.4674 | 5519.7103 | 8586.1777
11 | 2017 | 6793.2805 | 8871.7471 | 88.7175 | 15753.745 | 10290 | 15680 | 25970 | 3408.002 | 6808.2529 | 10216.255 | 7372.5412 | 10474.6533 | 104.7465 | 17951.941 | 10290 | 15680 | 25970 | 2812.7123 | 5205.3467 | 8018.059
12 | 2018 | 6965.0527 | 9143.5212 | 91.4352 | 16200.0092 | 10290 | 15680 | 25970 | 3233.512 | 6536.4788 | 9769.9908 | 7559.7685 | 10798.463 | 107.9846 | 18466.2161 | 10290 | 15680 | 25970 | 2622.2469 | 4881.537 | 7503.7839
13 | 2019 | 7138.837 | 9423.3307 | 94.2333 | 16656.401 | 10290 | 15680 | 25970 | 3056.9297 | 6256.6693 | 9313.599 | 7749.6284 | 11131.77 | 111.3177 | 18992.7161 | 10290 | 15680 | 25970 | 2429.0539 | 4548.23 | 6977.2839
14 | 2020 | 7380.2445 | 9711.4078 | 97.1141 | 17188.7664 | 10290 | 15680 | 25970 | 2812.6414 | 5968.5922 | 8781.2336 | 8005.5393 | 11464.8322 | 114.6483 | 19585.0198 | 10290 | 15680 | 25970 | 2169.8124 | 4215.1678 | 6384.9802
15 | 2021 | 7558.2108 | 10007.9915 | 100.0799 | 17666.2823 | 10290 | 15680 | 25970 | 2631.7093 | 5672.0085 | 8303.7177 | 8200.4439 | 11820.2148 | 118.2021 | 20138.8609 | 10290 | 15680 | 25970 | 1971.354 | 3859.7852 | 5831.1391
16 | 2022 | 7738.3499 | 10313.3277 | 103.1333 | 18154.811 | 10290 | 15680 | 25970 | 2448.5168 | 5366.6723 | 7815.189 | 8397.9635 | 12186.5906 | 121.8659 | 20706.42 | 10290 | 15680 | 25970 | 1770.1706 | 3493.4094 | 5263.58
17 | 2023 | 7986.2771 | 10627.6692 | 106.2767 | 18720.223 | 10290 | 15680 | 25970 | 2197.4462 | 5052.3308 | 7249.777 | 8663.7209 | 12563.4399 | 125.6344 | 21352.7952 | 10290 | 15680 | 25970 | 1500.6447 | 3116.5601 | 4617.2048
18 | 2024 | 8170.932 | 10951.2759 | 109.5128 | 19231.7207 | 10290 | 15680 | 25970 | 2009.5552 | 4728.7241 | 6738.2793 | 8866.6636 | 12951.5506 | 129.5155 | 21947.7297 | 10290 | 15680 | 25970 | 1293.8209 | 2728.4494 | 4022.2703
19 | 2025 | 8357.933 | 11284.4153 | 112.8442 | 19755.1924 | 10290 | 15680 | 25970 | 1819.2228 | 4395.5847 | 6214.8076 | 9074.7175 | 13358.3191 | 133.5832 | 22566.6198 | 10290 | 15680 | 25970 | 1081.6993 | 2321.6809 | 3403.3802
20 | 2026 | 8612.8997 | 11627.3623 | 116.2736 | 20356.5356 | 10290 | 15680 | 25970 | 1560.8267 | 4052.6377 | 5613.4644 | 9347.9103 | 13762.5498 | 137.6255 | 23248.0856 | 10290 | 15680 | 25970 | 804.4642 | 1917.4502 | 2721.9144
Notes:
(1) Demands considered for the economic assessments are: | [11 empty] | (2) Total Demands considered for the design of TT.LL. and SS.SS. are:
| S.S. Puerto Maldonado | [5 empty] | S.S. Mazuko | [5 empty] | S.S. Puerto Maldonado | [5 empty] | S.E. Mazuko
| Puerto Maldonado City | [5 empty] | Mazuko Town | [5 empty] | Puerto Maldonado City | [5 empty] | Mazuko Town
| Laberinto Circuit and Planchón | [5 empty] | Huapetuhe | [5 empty] | Laberinto Circuit and Planchón | [5 empty] | Huapetuhe
| Human settlements, UPIS , Association of Homes of Pto. Maldonado, | [5 empty] | Mining Charges sector Huapetuhe and its developing | [5 empty] | AA.HH, UPIS , Asociación de Viviendas de Pto, Maldonado | [5 empty] | Mining Charges sector Huapetuhe
| which will enter by stages in 2007,2008 and 2009 | [11 empty] | PSEs Puerto Maldonado e Iberia | [5 empty] | PSE Mazuko
(3) Loses in 66 kV Mazuko-Pto. Maldonado Line and Mazuko and Pto. Maldonado Transform. | [11 empty] | (4) Total Demand; summation of demand plus loses
(5) Supply is limited by the power of Mazuko 138/66/33 kV - 20-26/12,3-16/8-10,5 transfor. MVA | [11 empty] | (6) The supply is limited by the power of Pto. Maldonado transform.
(ONAN/ONAF) | [11 empty] | 66/33/10 kV 16-12,3/3,9-5/12,3-16 MVA (ONAN/ONAF)
(7) Total Supply ; summation of Mazuko and Puerto Maldonado transformers' power | [11 empty] | (8) Supply-Demand Balance
which covers the demand of each town and the existing and future mining charge
(9) The supply of energy will be permanemte and reliable, without technical restrictions and at a reasonable cost,
(10) The lines as the substations are designed to provide power to SESs of Puerto Maldonado, Iberia and Mazuko, to vegetative growing of cities with electricity
service (Puerto Maldonado, Iberia Iñapari, Mazuko and Huapetuhe) and mining charges in Mazuko sector

## F-05-Cost-Priv
FORM 5
INCREMENTAL COSTS
| At Private Prices | [22 empty] | COMPRA DE ENERGÍA |  |  | TC= | #REF!
Premises
1. Costs of O&M with project, determined according to the OSINERG-GART forms and validated bye Electro Sur Este -ELSE
| 2. Facilities lifetime |  | 30 | years cording to the Electric Concesión Law
3. Cost of the purchasing of energy and power
| Item | Sale fare | PPB | PEBP | PEBF
|  | 10 kV | S/kw-mes | cS/kw-h | cS/kw-h
| 1 | Tarifa en la S.E. San Gabán 138 kV (Barra base de Machupicchu) sin IGV | 29.47 | 9.96 | 8.33
|  | Tarifa en la S.E. San Gabán 138 kV (Barra base de Machupicchu) con IGV | 35.0693 | 11.8524 | 9.9127
| 2 | Tarifa en Barra Cálculada para Mazuko 33 kV sin IGV | 31.0448 | 11.5118 | 9.8113
|  | Tarifa en Barra Cálculada para Mazuko 33 kV con IGV | 36.9434 | 13.6991 | 11.6754
| 3 | Tarifa en Barra Cálculada para Pto. Maldonado 10 kV sin IGV | 36.836 | 17.1549 | 15.0468
|  | Tarifa en Barra Cálculada para Pto. Maldonado 10 kV con IGV | 43.8349 | 20.4144 | 17.9056
| HEADING |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | PPB | PEBP | PEBF
|  |  | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | S/kw-mes | cS/kw-h | cS/kw-h
2 | A | Investment costs - mil S/. | [21 empty] | 26.23 | 10.63 | 7.79 | 22.9kV | SUMINISTRO AZANGARO
3 | A.1 | Costs with Project | 45707.7861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -14602.2044
| A.1.1 | Investments | 43.8349 0 2006: 45707.7861
| 1 | INTANGIBLES | 43.8349 0 2006: 363.04
| 1.1 | Updating of the Final Engineering Study | 43.8349 0 2006: 272.96
| 1.2 | Oversight of the Studies and Administrative costs (8% of A) | 43.8349 0 2006: 21.8368
| 1.3 | File Management and Technical Easement | 43.8349 0 2006: 68.24
| 2 | INVESTMENTS IN ASSETS | 43.8349 0 2006: 36812.28
| 2.1 | San Gabán-Mazuko 138kV line-67,6 km-200 mm² AAAC | 43.8349 0 2006: 11546.0784
| 2,1,1 | Direct Costs | 43.8349 0 2006: 9838.8943
|  | Equipment and Material Supplying | 43.8349 0 2006: 4954.5009
|  | Electromechanical assembly and Civil Works | 43.8349 0 2006: 4488.0333
|  | Equipment and material transportation | 43.8349 0 2006: 396.3601
| 2,1,2 | Indirect Costs | 43.8349 0 2006: 1707.1841
|  | Easement (cost of land) | 43.8349 0 2006: 34.5721
|  | General Expenses | 43.8349 0 2006: 983.8894
|  | Utilities | 43.8349 0 2006: 688.7226
| 2.2 | LT-66kV Mazk-Pto Mald-section I- 26,8 km 200 mm² AAAC | 43.8349 0 2006: 3660.1372
| 2,2,1 | Direct Costs | 43.8349 0 2006: 3117.3807
|  | Equipment and Material Supplying | 43.8349 0 2006: 1517.1937
|  | Electromechanical assembly and Civil Works | 43.8349 0 2006: 1478.8115
|  | Equipment and material transportation | 43.8349 0 2006: 121.3755
| 2,2,2 | Indirect Costs | 43.8349 0 2006: 542.7565
|  | Easement (cost of land) | 43.8349 0 2006: 12.8018
|  | General Expenses | 43.8349 0 2006: 311.7381
|  | Utilities | 43.8349 0 2006: 218.2166
| 2.3 | LT-66kV Mazk-Pto Mald-section II- 125,9 km 200 mm² AAAC | 43.8349 0 2006: 11684.8211
| 2,3,1 | Direct Costs | 43.8349 0 2006: 9935.6249
|  | Equipment and Material Supplying | 43.8349 0 2006: 5337.1088
|  | Electromechanical assembly and Civil Works | 43.8349 0 2006: 4249.4481
|  | Equipment and material transportation | 43.8349 0 2006: 349.0681
| 2,3,2 | Indirect Costs | 43.8349 0 2006: 1749.1961
|  | Easement (cost of land) | 43.8349 0 2006: 60.1399
|  | General Expenses | 43.8349 0 2006: 993.5625
|  | Utilities | 43.8349 0 2006: 695.4937
| 2.4 | LT-66kV Mazk-Pto Mald-section III- 5,3 km 200 mm² AAAC | 43.8349 0 2006: 772.2384
| 2,4,1 | Direct Costs | 43.8349 0 2006: 650.7592
|  | Equipment and Material Supplying | 43.8349 0 2006: 370.4443
|  | Electromechanical assembly and Civil Works | 43.8349 0 2006: 250.6793
|  | Equipment and material transportation | 43.8349 0 2006: 29.6355
| 2,4,2 | Indirect Costs | 43.8349 0 2006: 121.4792
|  | Easement (cost of land) | 43.8349 0 2006: 10.8502
|  | General Expenses | 43.8349 0 2006: 65.0759
|  | Utilities | 43.8349 0 2006: 45.5531
| 2.5 | Expansion of the San Gabán 138 kV Substation | 43.8349 0 2006: 782.99
| 2,5,1 | Direct Costs | 43.8349 0 2006: 625.48
|  | Equipment and Material Supplying | 43.8349 0 2006: 459.9835
|  | Electromechanical assembly | 43.8349 0 2006: 50.8177
|  | Civil works | 43.8349 0 2006: 77.8837
|  | Equipment and material transportation | 43.8349 0 2006: 36.7987
| 2,5,2 | Indirect Costs | 43.8349 0 2006: 157.51
|  | Easement (cost of land) | 43.8349 0 2006: 51.18
|  | General Expenses | 43.8349 0 2006: 62.5484
|  | Utilities | 43.8349 0 2006: 43.7838
| 2.6 | Mazuko Substation 138/66/33 kV 20-26/12,3-16/8-10,5 MVA | 43.8349 0 2006: 4304.0392
| 2,6,1 | Direct Costs | 43.8349 0 2006: 3652.42
|  | Equipment and Material Supplying | 43.8349 0 2006: 2898.5903
|  | Electromechanical assembly | 43.8349 0 2006: 189.5063
|  | Civil works | 43.8349 0 2006: 332.435
|  | Equipment and material transportation | 43.8349 0 2006: 231.8872
| 2,6,2 | Indirect Costs | 43.8349 0 2006: 651.6192
|  | Easement (cost of land) | 43.8349 0 2006: 30.708
|  | General Expenses | 43.8349 0 2006: 365.2419
|  | Utilities | 43.8349 0 2006: 255.6693
| 2.7 | Puerto Maldonado Substation 66/33/10 kV 12,3-16/3,9-5/12,3-16 MVA | 43.8349 0 2006: 2829.6007
| 2,7,1 | Direct Costs | 43.8349 0 2006: 2418.4622
|  | Equipment and Material Supplying | 43.8349 0 2006: 1958.9432
|  | Electromechanical assembly | 43.8349 0 2006: 162.0847
|  | Civil works | 43.8349 0 2006: 140.7188
|  | Equipment and material transportation | 43.8349 0 2006: 156.7155
| 2,7,2 | Indirect Costs | 43.8349 0 2006: 411.1386
|  | Easement (cost of land) | 43.8349 0 2006: 0
|  | General Expenses | 43.8349 0 2006: 241.8462
|  | Utilities | 43.8349 0 2006: 169.2923
| 2.8 | Communication Systems | 43.8349 0 2006: 1232.3739
| 2,8,1 | Direct Costs | 43.8349 0 2006: 1053.311
|  | Equipment and Material Supplying | 43.8349 0 2006: 747.3741
|  | Equipment and Materials assembly | 43.8349 0 2006: 268.5682
|  | Equipment and material transportation | 43.8349 0 2006: 37.3687
| 2,8,2 | Indirect Costs | 43.8349 0 2006: 179.0629
|  | General Expenses | 43.8349 0 2006: 105.3311
|  | Utilities | 43.8349 0 2006: 73.7318
| 3 | PREOPERATIVE EXPENSES | 43.8349 0 2006: 866.4614
| 3.1 | Finantial and administrative expenses (0,5% de 2) | 43.8349 0 2006: 184.0614
| 3.2 | Overseeing of the works (2,5% of 2) | 43.8349 0 2006: 682.4
| 4 | INITIAL WORKING CAPITAL | 43.8349 0 2006: 0
| 5 | CONTINGENCIES (1% de 2) | 43.8349 0 2006: 368.1228
| 6 | TOTAL INVESTMENTS WITHOUT SALES TAX | 43.8349 0 2006: 38409.9043
#REF! |  | Sales general tax (IGV) | 7297.8818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
#REF! |  | Total of investments with Project | 45707.7861 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| A.1.1 | Depreciation | 17.9056 20 2026: -14602.2044 | -13037.6825
#REF! | A.2 | Costs without Project
#REF! |  | Investment Costs in New Groups | 0 | 1080.9216 | 900.768 | 0 | 1238.556 | 1080.9216 | 900.768 | 0 | 1013.364 | 2094.2856 | 0 | 1013.364 | 0 | 2026.728 | 2319.4776 | 0 | 0 | 3107.6496 | 0 | 1463.748 | 2094.2856
#REF! |  | Sales genaral tax (IGV) | 0 | 205.3751 | 171.1459 | 0 | 235.3256 | 205.3751 | 171.1459 | 0 | 192.5392 | 397.9143 | 0 | 192.5392 | 0 | 385.0783 | 440.7007 | 0 | 0 | 590.4534 | 0 | 278.1121 | 397.9143
#REF! |  | Total Investments without Project | 0 | 1286.2967 | 1071.9139 | 0 | 1473.8816 | 1286.2967 | 1071.9139 | 0 | 1205.9032 | 2492.1999 | 0 | 1205.9032 | 0 | 2411.8063 | 2760.1783 | 0 | 0 | 3698.103 | 0 | 1741.8601 | 2492.1999
#REF! | B | Operation and Maintenance Costs-mil S/.
#REF! | B.1 | Operation and Maintenance Costs-WITH PROJECT |  | 9815.4022 | 10931.8046 | 12100.3703 | 12840.8654 | 13577.3901 | 13970.7727 | 14372.9426 | 14871.5507 | 15292.1542 | 15722.422 | 16250.0328 | 16700.572 | 17161.7381 | 17721.2399 | 18204.6941 | 18699.8312 | 19294.3932 | 19814.0308 | 20346.51 | 20979.6088
#REF! | 1.1 | Purchase of energy |  | 4074.1967 | 4767.892 | 5494.9151 | 5940.653 | 6384.5264 | 6602.823 | 6826.076 | 7111.6928 | 7345.3854 | 7584.5728 | 7886.6803 | 8137.4387 | 8394.2862 | 8714.668 | 8984.3353 | 9260.7476 | 9601.3719 | 9891.9819 | 10190.0604 | 10553.0985
#REF! | 1.2 | Purchase of power |  | 4157.608 | 4547.7985 | 4955.3053 | 5228.4947 | 5499.6938 | 5663.3221 | 5830.5252 | 6028.994 | 6203.6543 | 6382.2027 | 6592.3386 | 6778.997 | 6969.8835 | 7192.7074 | 7392.4131 | 7596.7164 | 7833.3368 | 8047.2294 | 8266.1209 | 8517.7418
#REF! | 1.3 | Other costs due to operation and maintenance-mil S/, (3) |  | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433
#REF! | 1.4 | Loses Cost |  | 246.9541 | 279.4707 | 313.5066 | 335.0744 | 356.5266 | 367.9844 | 379.698 | 394.2206 | 406.4712 | 419.0033 | 434.3706 | 447.4931 | 460.9251 | 477.2213 | 491.3025 | 505.7239 | 523.0413 | 538.1763 | 553.6854 | 572.1252
#REF! | B.2 | Operation and Maintenance Costs-WITHOUT PROJECT | 19021.6864 | 19029.9198 | 19521.6373 | 20554.941 | 21330.434 | 23163.9956 | 22455.0276 | 24464.1216 | 24218.7011 | 27208.1065 | 26115.9191 | 28489.6327 | 29185.3221 | 30262.3661 | 30864.5816 | 32022.3998 | 35395.1548 | 34467.0992 | 35757.0091 | 36579.5445 | 41681.3557
#REF! | 2.1 | Operation and Maintenance Costs | 15984.6104 | 15991.5293 | 16404.7372 | 17273.0597 | 17924.7344 | 19465.5426 | 18869.7711 | 20558.0854 | 20351.8497 | 22863.9551 | 21946.1505 | 23940.8678 | 24525.4808 | 25430.5597 | 25936.6232 | 26909.5797 | 29743.8276 | 28963.9489 | 30047.9068 | 30739.113 | 35026.3493
#REF! |  | Sales general tax IGV | 3037.076 | 3038.3906 | 3116.9001 | 3281.8813 | 3405.6995 | 3698.4531 | 3585.2565 | 3906.0362 | 3866.8514 | 4344.1515 | 4169.7686 | 4548.7649 | 4659.8413 | 4831.8064 | 4927.9584 | 5112.8201 | 5651.3272 | 5503.1503 | 5709.1023 | 5840.4315 | 6655.0064
#REF! |  | Total Investments without projects | 19021.6864 | 19029.9198 | 19521.6373 | 20554.941 | 21330.434 | 23163.9956 | 22455.0276 | 24464.1216 | 24218.7011 | 27208.1065 | 26115.9191 | 28489.6327 | 29185.3221 | 30262.3661 | 30864.5816 | 32022.3998 | 35395.1548 | 34467.0992 | 35757.0091 | 36579.5445 | 41681.3557
#REF! | C | Total Costs with Project (A+B+c1) | 45707.7861 | 9815.4022 | 10931.8046 | 12100.3703 | 12840.8654 | 13577.3901 | 13970.7727 | 14372.9426 | 14871.5507 | 15292.1542 | 15722.422 | 16250.0328 | 16716.7701 | 17234.8995 | 17857.4231 | 18401.4594 | 18959.08 | 19622.3703 | 20208.4888 | 20809.5487 | 6915.4737
| c1 | Income tax | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.1981 | 73.1613 | 136.1832 | 196.7653 | 259.2488 | 327.9771 | 394.4579 | 463.0387 | 538.0693
#REF! | D | Total Costs without Project | 19021.6864 | 20316.2165 | 20593.5512 | 20554.941 | 22804.3156 | 24450.2923 | 23526.9415 | 24464.1216 | 25424.6043 | 29700.3064 | 26115.9191 | 29695.5359 | 29185.3221 | 32674.1724 | 33624.76 | 32022.3998 | 35395.1548 | 38165.2023 | 35757.0091 | 38321.4046 | 44173.5555
#REF! | E | Total of Incremental Costs (C-D) | 26686.0997 | -10500.8144 | -9661.7467 | -8454.5708 | -9963.4502 | -10872.9022 | -9556.1688 | -10091.1791 | -10553.0535 | -14408.1522 | -10393.4971 | -13445.5031 | -12468.552 | -15439.2729 | -15767.3369 | -13620.9404 | -16436.0748 | -18542.8319 | -15548.5203 | -17511.8559 | -37258.0819
#REF! |  | Loses and Earnings State
#REF! | 1 | Total sellings of energy |  | 11333.5037 | 12648.5955 | 14024.4641 | 14930.5592 | 15830.5066 | 16354.4299 | 16891.3253 | 17538.1618 | 18102.2949 | 18680.7213 | 19370.452 | 19978.8864 | 20603.066 | 21340.0483 | 21997.2803 | 22671.853 | 23460.8747 | 24171.8448 | 24901.9084 | 25748.2295
#REF! | 2 | Purchase of energy and power |  | -7984.8506 | -9036.2199 | -10136.7138 | -10834.0733 | -11527.6936 | -11898.1607 | -12276.9032 | -12746.4663 | -13142.5685 | -13547.7722 | -14044.6484 | -14468.9426 | -14903.2447 | -15430.1541 | -15885.4459 | -16351.7401 | -16911.6674 | -17401.0349 | -17902.4958 | -18498.7151
#REF! | 3 | Other operation and maintenance costs |  | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433 | -1336.6433
#REF! | 4 | Investment Annualization |  | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759 | -5864.7759
#REF! | 5 | Depreciation Annualization |  | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469 | 1745.469
#REF! | 6 | Utilities before the taxes |  | No Exist | No Exist | No Exist | No Exist | No Exist | No Exist | No Exist | No Exist | No Exist | No Exist | No Exist | 53.9936 | 243.8711 | 453.944 | 655.8842 | 864.1627 | 1093.2571 | 1314.8598 | 1543.4624 | 1793.5643
#REF! | 7 | Income tax |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.1981 | 73.1613 | 136.1832 | 196.7653 | 259.2488 | 327.9771 | 394.4579 | 463.0387 | 538.0693
#REF!
#REF! | NOTA:
#REF! | 1 | Necessary replacements on the horizon for the project must be scheaduled
#REF! | 2 | According to Superintendencia de Banca y seguros; in November 31st 2005; exchange rate : | 43.8349 0 2006: 3.412; 20.4144 1 2007: S/. / US$
| 3 | Income tax | 43.8349 0 2006: 30%

## F-05-Cost-Soci
FORM 5
INCREMENTAL COSTS
| At Social Prices | [22 empty] | COMPRA DE ENERGÍA |  |  | TC= | #REF!
Premises
1. Costs of O&M with project, determined according to the OSINERG-GART forms and validated bye Electro Sur Este -ELSE
| 2. Facilities lifetime |  | 30 | years cording to the Electric Concesión Law
| 3. Cost of the purchasing of energy and power | [22 empty] | 100%
| Item | Sale fare | PPB | PEBP | PEBF
|  | 10 kV | S/kw-mes | cS/kw-h | cS/kw-h
| 1 | Tarifa en la S.E. San Gabán 138 kV (Barra base de Machupicchu) sin IGV | 29.47 | 9.96 | 8.33
|  | Tarifa en la S.E. San Gabán 138 kV (Barra base de Machupicchu) con IGV | 35.0693 | 11.8524 | 9.9127
| 2 | Tarifa en Barra Cálculada para Mazuko 33 kV sin IGV | 31.0448 | 11.5118 | 9.8113
|  | Tarifa en Barra Cálculada para Mazuko 33 kV con IGV | 36.9434 | 13.6991 | 11.6754
| 3 | Tarifa en Barra Cálculada para Pto. Maldonado 10 kV sin IGV | 36.836 | 17.1549 | 15.0468
|  | Tarifa en Barra Cálculada para Pto. Maldonado 10 kV con IGV | 43.8349 | 20.4144 | 17.9056
| HEADING |  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | PPB | PEBP | PEBF
|  |  | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | S/kw-mes | cS/kw-h | cS/kw-h
2 | A | Investment costs - mil S/. | [21 empty] | 26.23 | 10.63 | 7.79 | 22.9kV | SUMINISTRO AZANGARO
3 | A.1 | Costs with Project | 37428.2274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -11943.5967
4 | A.1.1 | Investments | 43.8349 0 2006: 37428.2274
5 | 1 | INTANGIBLES | 43.8349 0 2006: 363.04
6 | 1.1 | Updating of the Final Engineering Study | 43.8349 0 2006: 272.96
7 | 1.2 | Oversight of the Studies and Administrative costs (8% of A) | 43.8349 0 2006: 21.8368
8 | 1.3 | File Management and Technical Easement | 43.8349 0 2006: 68.24
9 | 2 | INVESTMENTS IN ASSETS | 43.8349 0 2006: 35830.79
10 | 2.1 | San Gabán-Mazuko 138kV line-67,6 km-200 mm² AAAC | 43.8349 0 2006: 11269.9767
11 | 2,1,1 | Direct Costs | 43.8349 0 2006: 9562.7926
12 |  | Equipment and Material Supplying | 43.8349 0 2006: 4678.3992
13 |  | Electromechanical assembly and Civil Works | 43.8349 0 2006: 4488.0333
14 |  | Equipment and material transportation | 43.8349 0 2006: 396.3601
15 | 2,1,2 | Indirect Costs | 43.8349 0 2006: 1707.1841
16 |  | Easement (cost of land) | 43.8349 0 2006: 34.5721
17 |  | General Expenses | 43.8349 0 2006: 983.8894
18 |  | Utilities | 43.8349 0 2006: 688.7226
19 | 2.2 | LT-66kV Mazk-Pto Mald-section I- 26,8 km 200 mm² AAAC | 43.8349 0 2006: 3572.1041
20 | 2,2,1 | Direct Costs | 43.8349 0 2006: 3029.3476
21 |  | Equipment and Material Supplying | 43.8349 0 2006: 1429.1606
22 |  | Electromechanical assembly and Civil Works | 43.8349 0 2006: 1478.8115
23 |  | Equipment and material transportation | 43.8349 0 2006: 121.3755
24 | 2,2,2 | Indirect Costs | 43.8349 0 2006: 542.7565
25 |  | Easement (cost of land) | 43.8349 0 2006: 12.8018
26 |  | General Expenses | 43.8349 0 2006: 311.7381
27 |  | Utilities | 43.8349 0 2006: 218.2166
28 | 2.3 | LT-66kV Mazk-Pto Mald-section II- 125,9 km 200 mm² AAAC | 43.8349 0 2006: 11311.5975
29 | 2,3,1 | Direct Costs | 43.8349 0 2006: 9562.4014
30 |  | Equipment and Material Supplying | 43.8349 0 2006: 4963.8852
31 |  | Electromechanical assembly and Civil Works | 43.8349 0 2006: 4249.4481
32 |  | Equipment and material transportation | 43.8349 0 2006: 349.0681
33 | 2,3,2 | Indirect Costs | 43.8349 0 2006: 1749.1961
34 |  | Easement (cost of land) | 43.8349 0 2006: 60.1399
35 |  | General Expenses | 43.8349 0 2006: 993.5625
36 |  | Utilities | 43.8349 0 2006: 695.4937
37 | 2.4 | LT-66kV Mazk-Pto Mald-section III- 5,3 km 200 mm² AAAC | 43.8349 0 2006: 753.3587
38 | 2,4,1 | Direct Costs | 43.8349 0 2006: 631.8795
39 |  | Equipment and Material Supplying | 43.8349 0 2006: 351.5646
40 |  | Electromechanical assembly and Civil Works | 43.8349 0 2006: 250.6793
41 |  | Equipment and material transportation | 43.8349 0 2006: 29.6355
42 | 2,4,2 | Indirect Costs | 43.8349 0 2006: 121.4792
43 |  | Easement (cost of land) | 43.8349 0 2006: 10.8502
44 |  | General Expenses | 43.8349 0 2006: 65.0759
45 |  | Utilities | 43.8349 0 2006: 45.5531
46 | 2.5 | Expansion of the San Gabán 138 kV Substation | 43.8349 0 2006: 771.89
47 | 2,5,1 | Direct Costs | 43.8349 0 2006: 614.38
48 |  | Equipment and Material Supplying | 43.8349 0 2006: 448.8809
49 |  | Electromechanical assembly | 43.8349 0 2006: 50.8177
50 |  | Civil works | 43.8349 0 2006: 77.8837
51 |  | Equipment and material transportation | 43.8349 0 2006: 36.7987
52 | 2,5,2 | Indirect Costs | 43.8349 0 2006: 157.51
53 |  | Easement (cost of land) | 43.8349 0 2006: 51.18
54 |  | General Expenses | 43.8349 0 2006: 62.5484
55 |  | Utilities | 43.8349 0 2006: 43.7838
56 | 2.6 | Mazuko Substation 138/66/33 kV 20-26/12,3-16/8-10,5 MVA | 43.8349 0 2006: 4235.8092
57 | 2,6,1 | Direct Costs | 43.8349 0 2006: 3584.19
58 |  | Equipment and Material Supplying | 43.8349 0 2006: 2830.3642
59 |  | Electromechanical assembly | 43.8349 0 2006: 189.5063
60 |  | Civil works | 43.8349 0 2006: 332.435
61 |  | Equipment and material transportation | 43.8349 0 2006: 231.8872
62 | 2,6,2 | Indirect Costs | 43.8349 0 2006: 651.6192
63 |  | Easement (cost of land) | 43.8349 0 2006: 30.708
64 |  | General Expenses | 43.8349 0 2006: 365.2419
65 |  | Utilities | 43.8349 0 2006: 255.6693
66 | 2.7 | Puerto Maldonado Substation 66/33/10 kV 12,3-16/3,9-5/12,3-16 MVA | 43.8349 0 2006: 2784.3903
67 | 2,7,1 | Direct Costs | 43.8349 0 2006: 2373.2517
68 |  | Equipment and Material Supplying | 43.8349 0 2006: 1913.7328
69 |  | Electromechanical assembly | 43.8349 0 2006: 162.0847
70 |  | Civil works | 43.8349 0 2006: 140.7188
71 |  | Equipment and material transportation | 43.8349 0 2006: 156.7155
72 | 2,7,2 | Indirect Costs | 43.8349 0 2006: 411.1386
73 |  | Easement (cost of land) | 43.8349 0 2006: 0
74 |  | General Expenses | 43.8349 0 2006: 241.8462
75 |  | Utilities | 43.8349 0 2006: 169.2923
76 | 2.8 | Communication Systems | 43.8349 0 2006: 1131.6684
77 | 2,8,1 | Direct Costs | 43.8349 0 2006: 952.6055
78 |  | Equipment and Material Supplying | 43.8349 0 2006: 684.0373
79 |  | Equipment and Materials assembly | 43.8349 0 2006: 268.5682
80 |  | Equipment and material transportation | 43.8349 0 2006: 0
81 | 2,8,2 | Indirect Costs | 43.8349 0 2006: 179.0629
82 |  | General Expenses | 43.8349 0 2006: 105.3311
83 |  | Utilities | 43.8349 0 2006: 73.7318
84 | 3 | PREOPERATIVE EXPENSES | 43.8349 0 2006: 866.2746
85 | 3.1 | Finantial and administrative expenses (0,5% de 2) | 43.8349 0 2006: 183.8746
86 | 3.2 | Overseeing of the works (2,5% of 2) | 43.8349 0 2006: 682.4
87 | 4 | INITIAL WORKING CAPITAL | 43.8349 0 2006: 0
88 | 5 | CONTINGENCIES (1% de 2) | 43.8349 0 2006: 368.1228
89 | 6 | TOTAL INVESTMENTS WITHOUT SALES TAX | 43.8349 0 2006: 37428.2274
90 |  | Sales general tax (IGV) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
91 |  | Total of investments with Project | 37428.2274 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
92 | A.1.1 | Depreciation | 17.9056 20 2026: -11943.5967 | -10663.9256
93 | A.2 | Costs without Project
94 |  | Investment Costs in New Groups | 0 | 1080.9216 | 900.768 | 0 | 1238.556 | 1080.9216 | 900.768 | 0 | 1013.364 | 2094.2856 | 0 | 1013.364 | 0 | 2026.728 | 2319.4776 | 0 | 0 | 3107.6496 | 0 | 1463.748 | 2094.2856
95 |  | Sales genaral tax (IGV) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
96 |  | Total Investments without Project | 0 | 1080.9216 | 900.768 | 0 | 1238.556 | 1080.9216 | 900.768 | 0 | 1013.364 | 2094.2856 | 0 | 1013.364 | 0 | 2026.728 | 2319.4776 | 0 | 0 | 3107.6496 | 0 | 1463.748 | 2094.2856
97 | B | Operation and Maintenance Costs-mil S/.
98 | B.1 | Operation and Maintenance Costs-WITH PROJECT |  | 8280.5869 | 9224.2482 | 10212.0089 | 10837.813 | 11460.2657 | 11792.5726 | 12132.3032 | 12553.5695 | 12908.8733 | 13272.3421 | 13718.1113 | 14098.7067 | 14488.2807 | 14960.9942 | 15369.3994 | 15787.6757 | 16290.0123 | 16728.9901 | 17178.8183 | 17713.7167
99 | 1.1 | Purchase of energy |  | 3455.1023 | 4043.3872 | 4659.9355 | 5037.9412 | 5414.3659 | 5599.4912 | 5788.8199 | 6031.0358 | 6229.2176 | 6432.0593 | 6688.2601 | 6900.9145 | 7118.7327 | 7390.4309 | 7619.121 | 7853.531 | 8142.3957 | 8388.8461 | 8641.6301 | 8949.5027
100 | 1.2 | Purchase of power |  | 3493.7883 | 3821.6794 | 4164.1221 | 4393.6931 | 4621.5914 | 4759.0942 | 4899.601 | 5066.3816 | 5213.1549 | 5363.1955 | 5539.7804 | 5696.6361 | 5857.045 | 6044.2919 | 6212.1118 | 6383.7953 | 6582.636 | 6762.3776 | 6946.32 | 7157.7662
101 | 1.3 | Other costs due to operation and maintenance-mil S/, (3) |  | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296 | 1123.2296
102 | 1.4 | Loses Cost |  | 208.4667 | 235.952 | 264.7217 | 282.949 | 301.0787 | 310.7576 | 320.6526 | 332.9225 | 343.2712 | 353.8576 | 366.8412 | 377.9265 | 389.2733 | 403.0417 | 414.937 | 427.1198 | 441.751 | 454.5367 | 467.6385 | 483.2181
103 | B.2 | Operation and Maintenance Costs-WITHOUT PROJECT | 15984.6104 | 15991.5293 | 16404.7372 | 17273.0597 | 17924.7344 | 19465.5426 | 18869.7711 | 20558.0854 | 20351.8497 | 22863.9551 | 21946.1505 | 23940.8678 | 24525.4808 | 25430.5597 | 25936.6232 | 26909.5797 | 29743.8276 | 28963.9489 | 30047.9068 | 30739.113 | 35026.3493
104 | 2.1 | Operation and Maintenance Costs | 15984.6104 | 15991.5293 | 16404.7372 | 17273.0597 | 17924.7344 | 19465.5426 | 18869.7711 | 20558.0854 | 20351.8497 | 22863.9551 | 21946.1505 | 23940.8678 | 24525.4808 | 25430.5597 | 25936.6232 | 26909.5797 | 29743.8276 | 28963.9489 | 30047.9068 | 30739.113 | 35026.3493
105 |  | Sales general tax IGV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
106 |  | Total costs with project | 15984.6104 | 15991.5293 | 16404.7372 | 17273.0597 | 17924.7344 | 19465.5426 | 18869.7711 | 20558.0854 | 20351.8497 | 22863.9551 | 21946.1505 | 23940.8678 | 24525.4808 | 25430.5597 | 25936.6232 | 26909.5797 | 29743.8276 | 28963.9489 | 30047.9068 | 30739.113 | 35026.3493
#REF! | C | Total Costs with Projet (A+B) | 37428.2274 | 8280.5869 | 9224.2482 | 10212.0089 | 10837.813 | 11460.2657 | 11792.5726 | 12132.3032 | 12553.5695 | 12908.8733 | 13272.3421 | 13718.1113 | 14098.7067 | 14488.2807 | 14960.9942 | 15369.3994 | 15787.6757 | 16290.0123 | 16728.9901 | 17178.8183 | 5770.12
#REF! | D | Total costs without project | 15984.6104 | 17072.4509 | 17305.5052 | 17273.0597 | 19163.2904 | 20546.4642 | 19770.5391 | 20558.0854 | 21365.2137 | 24958.2407 | 21946.1505 | 24954.2318 | 24525.4808 | 27457.2877 | 28256.1008 | 26909.5797 | 29743.8276 | 32071.5985 | 30047.9068 | 32202.861 | 37120.6349
#REF! | E | Total incremental costs (C-D) | 21443.617 | -8791.864 | -8081.257 | -7061.0508 | -8325.4775 | -9086.1984 | -7977.9664 | -8425.7822 | -8811.6442 | -12049.3674 | -8673.8084 | -11236.1206 | -10426.774 | -12969.007 | -13295.1067 | -11540.1803 | -13956.1518 | -15781.5863 | -13318.9167 | -15024.0427 | -31350.5149
#REF!
#REF! | NOTA:
#REF! | 1 | Necessary replacements on the horizon for the project must be scheaduled
#REF! | 2 | According to Superintendencia de Banca y seguros; in November 31st 2005; exchange rate : | 43.8349 0 2006: 3.412; 20.4144 1 2007: S/. / US$
#REF! | 4 | The evaluation does not include tax named IGV
#REF! | 5 | INDICATOR
#REF! |  | Investment cost at private prices | 43.8349 0 2006: 45707.7861; 20.4144 1 2007: ( thousand US$)
#REF! |  | Investment cost at social prices | 43.8349 0 2006: 37428.2274; 20.4144 1 2007: ( thousand US$)
#REF! |  | Correction factor for the investment | 43.8349 0 2006: 81.89%; 20.4144 1 2007: p.u.
#REF!

## F-06-Beneficios
FORM 6
INCREMENTAL BENEFITS
AT PRIVATE PRICES
| ITEM | DESCRIPTION | PERIOD
|  | Nº | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
1 |  | Year | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
1 | 1 | Situation with Project -Mil S/. |  | 11333.5037 | 12648.5955 | 14024.4641 | 14930.5592 | 15830.5066 | 16354.4299 | 16891.3253 | 17538.1618 | 18102.2949 | 18680.7213 | 19370.452 | 19978.8864 | 20603.066 | 21340.0483 | 21997.2803 | 22671.853 | 23460.8747 | 24171.8448 | 24901.9084 | 25748.2295
| 1.1 | Sellings of Energy in Mazuko |  | 3166.5377 | 4167.5912 | 5217.9594 | 5786.689 | 6356.5218 | 6538.9062 | 6722.4568 | 7003.749 | 7189.7316 | 7376.9817 | 7662.0772 | 7851.9701 | 8043.24 | 8332.4681 | 8526.6092 | 8722.2463 | 9015.9636 | 9214.7194 | 9415.1001 | 9713.6933
1 | 1.1 | Benefit due to the selling of energy |  | 1674.2427 | 2359.1435 | 3078.1376 | 3460.1036 | 3842.4467 | 3953.5774 | 4065.1098 | 4244.5356 | 4356.9107 | 4469.7274 | 4650.4786 | 4764.2213 | 4878.4492 | 5060.6564 | 5175.9014 | 5291.6793 | 5475.4855 | 5592.38 | 5709.8594 | 5895.4207
1 | 1.2 | Benefict due to the selling of Power |  | 1492.295 | 1808.4477 | 2139.8218 | 2326.5854 | 2514.0751 | 2585.3288 | 2657.347 | 2759.2133 | 2832.8209 | 2907.2543 | 3011.5986 | 3087.7488 | 3164.7908 | 3271.8117 | 3350.7077 | 3430.567 | 3540.4782 | 3622.3394 | 3705.2408 | 3818.2726
| 1.2 | Selling of Energy in Puerto Maldonado |  | 8166.966 | 8481.0043 | 8806.5047 | 9143.8702 | 9473.9848 | 9815.5237 | 10168.8685 | 10534.4129 | 10912.5633 | 11303.7395 | 11708.3748 | 12126.9163 | 12559.8259 | 13007.5802 | 13470.6712 | 13949.6067 | 14444.9111 | 14957.1254 | 15486.8083 | 16034.5362
| 1.3 | Benefit due to the selling of energy |  | 4740.8359 | 4942.2843 | 5151.6112 | 5369.1066 | 5582.7004 | 5804.2578 | 6034.0597 | 6272.3967 | 6519.569 | 6775.8872 | 7041.6721 | 7317.2554 | 7602.9801 | 7899.2005 | 8206.2829 | 8524.606 | 8854.5609 | 9196.5522 | 9550.9976 | 9918.329
| 1.4 | Benefict due to the selling of Power |  | 3426.1301 | 3538.72 | 3654.8935 | 3774.7636 | 3891.2844 | 4011.2659 | 4134.8088 | 4262.0162 | 4392.9943 | 4527.8523 | 4666.7027 | 4809.6609 | 4956.8459 | 5108.3797 | 5264.3883 | 5425.0008 | 5590.3502 | 5760.5733 | 5935.8107 | 6116.2072
1 | 2 | Situation without Project | 18298.1026 | 19042.1472 | 19772.9327 | 20523.4757 | 21289.3015 | 22083.0346 | 22905.6488 | 23758.1506 | 24641.5803 | 25557.0131 | 26505.5602 | 27488.3699 | 28506.6289 | 29561.5637 | 30654.4415 | 31786.5718 | 32959.3079 | 34174.0479 | 35432.2364 | 36735.3661 | 38084.9792
1 | 2.1 | Benefit due to the selling of energy- thermic generation | 15436.2799 | 16035.7083 | 16657.701 | 17303.0641 | 17972.631 | 18667.2638 | 19387.8539 | 20135.323 | 20910.624 | 21714.7426 | 22548.6975 | 23413.5422 | 24310.3659 | 25240.2944 | 26204.4919 | 27204.1615 | 28240.5473 | 29314.9349 | 30428.6536 | 31583.077 | 32779.6251
1 | 2.2 | Benefict due to the selling of Power-thermic generation | 2861.8227 | 3006.4389 | 3115.2316 | 3220.4117 | 3316.6705 | 3415.7708 | 3517.7949 | 3622.8277 | 3730.9563 | 3842.2706 | 3956.8627 | 4074.8277 | 4196.2631 | 4321.2693 | 4449.9496 | 4582.4103 | 4718.7606 | 4859.1129 | 5003.5828 | 5152.2891 | 5305.3541
1 | 3 | Incremental Benefits | -18298.1026 | -7708.6435 | -7124.3371 | -6499.0117 | -6358.7423 | -6252.528 | -6551.2189 | -6866.8253 | -7103.4185 | -7454.7182 | -7824.839 | -8117.9179 | -8527.7425 | -8958.4977 | -9314.3932 | -9789.2915 | -10287.4549 | -10713.1732 | -11260.3915 | -11833.4577 | -12336.7496
12%
1 |  | Important Variables
1 |  | Sale Fares | PPB | PEBP | PEBF
1 |  | 10 kV | S/kw-mes | cS/kw-h | cS/kw-h
Isolated System
1 |  | Sale Fare in busbar for F-type isolated thermic systems (without Project-Currently) Without Sales tax | 35.3 | 59.62 | 59.62
1 |  | Sale Fare in busbar for F-type isolated thermic systems (with Project-Currently) With Sales tax | 42.007 | 70.9478 | 70.9478
Interconnected System
1 |  | Sale Fare in busbar calculated for Mazuko-33 kV –SINAC (With Project) without Sales taxes | 31.0448 | 11.5118 | 9.8113
1 |  | Sale Fare in busbar calculated for Mazuko-33 kV –SINAC (With Project) with Sales taxes | 36.9434 | 13.6991 | 11.6754
1 |  | Sale Fare in busbar calculated for Pto Maldonado -10 kV–SINAC (With Project)-without Sales tax | 36.836 | 17.1549 | 15.0468
1 |  | Sale Fare in busbar calculated for Pto Maldonado -10 kV–SINAC (With Project)-with Sales tax | 43.8349 | 20.4144 | 17.9056
1
1 | A PRECIOS SOCIALES
1
1 | ITEM | DESCRIPTION | PERIOD
1 |  | Nº | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
1 |  | Year | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
1 | 1 | Situation with Project -Mil S/. | 0 | 16603.7329 | 17303.6684 | 18030.7136 | 18785.8567 | 19531.0974 | 20303.9418 | 21105.3563 | 21936.3394 | 22797.9231 | 23691.1741 | 24617.1945 | 25577.1235 | 26572.138 | 27603.4543 | 28672.3292 | 29780.0612 | 30927.9921 | 32117.508 | 33350.0414 | 34627.0718
|  | Puerto Maldonado | 0 | 14955.0372 | 15590.5093 | 16250.834 | 16936.9265 | 17610.7114 | 18309.6174 | 19034.5309 | 19786.3685 | 20566.0773 | 21374.6367 | 22213.0591 | 23082.3908 | 23983.7135 | 24918.1452 | 25886.8413 | 26890.9961 | 27931.844 | 29010.6604 | 30128.7637 | 31287.5163
|  | Mazuko | 0 | 490.0997 | 509.1702 | 528.9062 | 549.3293 | 570.4617 | 592.3259 | 614.9456 | 638.345 | 662.5489 | 687.583 | 713.4738 | 740.2485 | 767.9351 | 796.5627 | 826.1609 | 856.7605 | 888.393 | 921.091 | 954.888 | 989.8185
|  | Huapetuhe | 0 | 1158.596 | 1203.9889 | 1250.9734 | 1299.6008 | 1349.9243 | 1401.9985 | 1455.8797 | 1511.6259 | 1569.2969 | 1628.9544 | 1690.6616 | 1754.4842 | 1820.4893 | 1888.7464 | 1959.3269 | 2032.3046 | 2107.7551 | 2185.7566 | 2266.3897 | 2349.737
|  | Cargas Mineras | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 2 | Situation without Project | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
1 | 3 | Incremental Benefits | 0 | 16603.7329 | 17303.6684 | 18030.7136 | 18785.8567 | 19531.0974 | 20303.9418 | 21105.3563 | 21936.3394 | 22797.9231 | 23691.1741 | 24617.1945 | 25577.1235 | 26572.138 | 27603.4543 | 28672.3292 | 29780.0612 | 30927.9921 | 32117.508 | 33350.0414 | 34627.0718
1 |  | Important Variables
1 | 1 | Electrical Energy's Price without sales tax: |  |  | cS/kw-h |  | Ahorro
| 5 | Regulated fare to final client in Cusco (Interconnected System) |  | 37.39% | 35.58
| 2 | Regulated fare to final client in Pto. Maldonado (Isolated System-ELSE) |  | 100% | 95.15 |  | 59.57 | cS/kw-h
| 3 | Regulated fare to final client in Mazuko (Isolated System-Municipality) |  | 97.13% | 92.4195 |  | 56.8395 | cS/kw-h
| 4 | Regulated fare to final client in Huepetue (Isolated System-Municipality) |  | 137.6% | 130.9664 |  | 95.3864 | cS/kw-h
| 6 | Regulated price to final client according to GART (PUFInt-Gart) |  | 38.14% | 36.2916
| 7 | Mining charges
|  | Equiv. Price of energy and power (with Connection) |  | 16.02% | 18.7804 |  | 117.2514 | cS/kw-h
|  | Equiv. Price of energy and power (without Connection) |  | 100% | 117.2514
| 7 | According to Superintendencia de Banca y seguros; in November 31st, 2005; exchange rate | [7 empty] | 3.412 | S/. / US$
Note: In the situation with project the benefit will be the saving (Interconnected fare - Isolated fare)xenergy consumption, in the case without project the benefit is cero
|  | The miners' benefit is not considered |  | 0

## F-07-Eval
FORM 7
NET PRESENT VALUE OF BENEFITS
AT PRIVATE PRICES
ITEM | Description | PERIODO
| Nº | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| Year | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
1 | Incremental Benefits ( mil S/.) |  | -7708.6435 | -7124.3371 | -6499.0117 | -6358.7423 | -6252.528 | -6551.2189 | -6866.8253 | -7103.4185 | -7454.7182 | -7824.839 | -8117.9179 | -8527.7425 | -8958.4977 | -9314.3932 | -9789.2915 | -10287.4549 | -10713.1732 | -11260.3915 | -11833.4577 | -12336.7496
2 | Benefits due to the selling of CO2 CERs |  | 904.4161 | 939.5098 | 975.7631 | 1013.8235 | 1052.9902 | 1093.962 | 1136.0978 | 1179.9214
3 | Incremental costs ( mil S/.) | 45707.7861 | -10500.8144 | -9661.7467 | -8454.5708 | -9963.4502 | -10872.9022 | -9556.1688 | -10091.1791 | -10553.0535 | -14408.1522 | -10393.4971 | -13445.5031 | -12468.552 | -15439.2729 | -15767.3369 | -13620.9404 | -16436.0748 | -18542.8319 | -15548.5203 | -17511.8559 | -37258.0819
4 | Net Benefits ( mil S/.) | -45707.7861 | 3696.587 | 3476.9193 | 2931.3222 | 4618.5314 | 5673.3644 | 4098.9119 | 4360.4516 | 4629.5564 | 6953.434 | 2568.6581 | 5327.5852 | 3940.8095 | 6480.7752 | 6452.9437 | 3831.6489 | 6148.6199 | 7829.6588 | 4288.1287 | 5678.3982 | 24921.3322
ECONOMIC INDICATORS
| Discount Rate % | 12%
| VNA (12%) mil S/. | -10148.7708
| IRR (%) | 8.912%
| Cost-Benefit relation (pu) | 0.77796
| Repay time (years) | 12.0973
A PRECIOS SOCIALES
ITEM | Description | PERIODO
| Nº | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| Year | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
1 | Incremental Benefits ( mil S/.) |  | 16603.7329 | 17303.6684 | 18030.7136 | 18785.8567 | 19531.0974 | 20303.9418 | 21105.3563 | 21936.3394 | 22797.9231 | 23691.1741 | 24617.1945 | 25577.1235 | 26572.138 | 27603.4543 | 28672.3292 | 29780.0612 | 30927.9921 | 32117.508 | 33350.0414 | 34627.0718
2 | Benefits due to the selling of CO2 CERs |  | 904.4161 | 939.5098 | 975.7631 | 1013.8235 | 1052.9902 | 1093.962 | 1136.0978 | 1179.9214
3 | Incremental costs ( mil S/.) | 21443.617 | -8791.864 | -8081.257 | -7061.0508 | -8325.4775 | -9086.1984 | -7977.9664 | -8425.7822 | -8811.6442 | -12049.3674 | -8673.8084 | -11236.1206 | -10426.774 | -12969.007 | -13295.1067 | -11540.1803 | -13956.1518 | -15781.5863 | -13318.9167 | -15024.0427 | -31350.5149
4 | Net Benefits ( mil S/.) | -21443.617 | 26300.0129 | 26324.4352 | 26067.5275 | 28125.1577 | 29670.286 | 29375.8703 | 30667.2363 | 31927.905 | 34847.2905 | 32364.9825 | 35853.3151 | 36003.8975 | 39541.145 | 40898.5609 | 40212.5094 | 43736.213 | 46709.5783 | 45436.4248 | 48374.0841 | 65977.5867
ECONOMIC INDICATORS
| Discount Rate % | 14%
| VNA (12%) mil S/. | 186658.1198
| IRR (%) | 123.7%
| Cost-Benefit relation (pu) | 9.7046
| Repay time (years) | 1.15
COSTOS PRIVADOS
ax²+bx+c=0
[6 empty] | a= | 1869.09 | b= | -22610.95 | c | 0
[6 empty] | x1 | 12.0973 | x2 | 0
[6 empty] | t | 12.0973 | años
TIEMPO DE REPAGO
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
|  | -45707.7861 | -45707.786 | -39635.4832 | -37549.026 | -34613.8658 | -31394.6464 | -29318.0101 | -27345.5632 | -25475.7631 | -22968.285 | -22141.2459 | -20609.6924 | -19598.1848 | -18112.9584 | -16792.5582 | -16092.5303 | -15089.5572 | -13949.2117 | -13391.5852 | -12732.2847 | -10148.7708
COSTOS sociales
ax²+bx+c=0
[6 empty] | a= | -477.11 | b= | 21439.5 | c | -24025.12
[6 empty] | x1 | 1.15 | x2 | 43.7861
[6 empty] | t | 1.15 | años
TIEMPO DE REPAGO
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
|  | -21443.617 | -45707.786 | 23024.2159 | 41578.5671 | 59452.6132 | 76288.3303 | 91171.0604 | 105043.3607 | 117938.506 | 130504.7883 | 140925.4465 | 151232.4178 | 160473.7216 | 169535.5315 | 177904.1873 | 185250.8625 | 192385.1862 | 199188.172 | 205096.706 | 210713.265 | 217552.948
| Descripción Nº | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| Año | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
| Ganancias ( mil S/.) | 11333.5037 | 12648.5955 | 14024.4641 | 14930.5592 | 15830.5066 | 16354.4299 | 16891.3253 | 17538.1618 | 18102.2949 | 18680.7213 | 19370.452 | 19978.8864 | 20603.066 | 21340.0483 | 21997.2803 | 22671.853 | 23460.8747 | 24171.8448 | 24901.9084 | 25748.2295
| Costos ( mil S/.) | 9815.4022 | 10931.8046 | 12100.3703 | 12840.8654 | 13577.3901 | 13970.7727 | 14372.9426 | 14871.5507 | 15292.1542 | 15722.422 | 16250.0328 | 16716.7701 | 17234.8995 | 17857.4231 | 18401.4594 | 18959.08 | 19622.3703 | 20208.4888 | 20809.5487 | #REF!
| Pérdidas ( mil S/.) | 1518.1015 | 1716.791 | 1924.0938 | 2089.6938 | 2253.1165 | 2383.6572 | 2518.3828 | 2666.6111 | 2810.1407 | 2958.2993 | 3120.4192 | 3262.1163 | 3368.1665 | 3482.6252 | 3595.821 | 3712.773 | 3838.5044 | 3963.3561 | 4092.3597 | #REF!
[11 empty] | 11.1684 | 450
40.2923

## F-08-Sost
FORM 8
ANALYSIS OF PROJECT SUSTAINABILITY
1 | Entity who will be in charge of operation and maintenance |  |  | : | Sociedad Eléctrica del Sur Oeste
2 | Technical and logistical Capacity |  |  | : | Sociedad Eléctrica del Sur Oeste
3 | Participation of beneficiary population |  |  | : | At the stage of providing the service, the participation of the beneficiaries will be tangible through timely payment of its mensual
bills for the electricity service.
4 | Flows of operating cost
| COSTS AND SOURCES | Years
|  | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
| Compra de Energía (mil S) | 8478.7589 | 9595.1613 | 10763.727 | 11504.2221 | 12240.7468 | 12634.1294 | 13036.2993 | 13534.9075 | 13955.5109 | 14385.7787 | 14913.3895 | 15363.9287 | 15825.0949 | 16384.5967 | 16868.0508 | 17363.1879 | 17957.7499 | 18477.3876 | 19009.8667 | 19642.9655
| Costos de Oper. y Mant. mil S | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433 | 1336.6433
| Tarifas o Cuotas -(Venta de energía) | 11333.5037 | 12648.5955 | 14024.4641 | 14930.5592 | 15830.5066 | 16354.4299 | 16891.3253 | 17538.1618 | 18102.2949 | 18680.7213 | 19370.452 | 19978.8864 | 20603.066 | 21340.0483 | 21997.2803 | 22671.853 | 23460.8747 | 24171.8448 | 24901.9084 | 25748.2295
| Cobertura % | 115.5% | 115.7% | 115.9% | 116.3% | 116.6% | 117.1% | 117.5% | 117.9% | 118.4% | 118.8% | 119.2% | 119.6% | 120.1% | 120.4% | 120.8% | 121.2% | 121.6% | 122% | 122.4% | 122.7%
Costs with IGV

## F-09
FORM 9
PRELIMINARY SENSITIVITY ANALYSIS
1. | Mention the most important cost and benefit variables
| (0) : Base Case | Considers the demand of Puerto Maldonado and its circuits of Planchon and Laberinto; Mazuko,
Huepetuhe and the mine demands (in Mazuco)
| (1) : Sensitivity | Economic Indicators considering only 50% of the mine demand compared to the base case
| (2) : Sensitivity | Economic Indicators considering that aditional demands will be connected, in 2009
PSE Iberia, in 2010 PSE Puerto Maldonado and in 2011 PSE Mazuko. PSE in Small Electric System (by the acronyms in Spanish)
| (3) : Sensitivity | Base Case, considering a variation in investment of -10%
| (4) : Sensitivity | Base Case, considering a variation in investment of +10%
| (5) : Sensitivity | Base Case, considering a variation in diesel cost of -5%
| (6) : Sensitivity | Base Case, considering a variation in diesel cost of +5%
| (7) : Sensitivity | Sensitivity for the tariff of energy sold of + 7,55%
| (8) : Sensitivity | Sensitivity without considering the CERs benefits
2. | Sensitivity analysis
AT PRIVATE PRICES
| Results | Unit |  | Sensitivity
| Variables | % | (Base Case "0") | (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8)
| Discount Rate | % | 12% | 12% | 12% | 12% | 12% | 12% | 12% | 12% | 12%
| Net Present Value of the Net Benefit NPV | thousand S/. | -10148.7708 | -11593.2326 | -19764.2785 | -5951.5535 | -14417.9953 | -17231.539 | -3066.0026 | -2066.6506 | -15186.2822
| IRR | % | 8.912% | 8.456% | 5.291% | 10.01% | 7.972% | 6.563% | 11.1% | 11.38% | 7.543%
| Benefit/Cost relation- B/C | pu | 0.77796 | 0.74636 | 0.56759 | 0.85532 | 0.71324 | 0.62301 | 0.93292 | 0.95479 | 0.66775
| Repayment Period (years) | years | 12.0973 | 12.0973 | 12.0973 | 12.0973 | 12.0973 | 12.0973 | 12.0973 | 12.0973 | 12.0973
AT SOCIAL PRICES
| Results | Unit |  | Sensitivity (1): Sensitivity
| Variables | % | (Base Case "0") | (1) | (2) | (3) | (4) | (5) | (6) | (7) | (8)
| Discount Rate | % | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14% | 14%
| Net Present Value of the Net Benefit NPV | thousand S/. | 186658.1198 | 194768.4988 | 179623.7664 | 186731.2421 | 186585.0076 | 180876.3046 | 192439.9351 | 186658.1198 | 181970.0293
| IRR | % | 123.7% | 126.9% | 123% | 124.1% | 123.3% | 117.5% | 130.2% | 123.7% | 119.4%
| Benefit/Cost relation- B/C | pu | 9.7046 | 10.0828 | 9.3766 | 9.7378 | 9.6716 | 9.2058 | 10.2321 | 9.7046 | 9.486
| Repayment Period (years) | years | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15 | 1.15
|  | SENSITIVITY |  | 1 | 2 | 3 and 4 | 5 and 6 | 7 | 8
|  | FACTOR |  | 100% | 0% | 100% | 100% | 100% | 100%
|  | LEAVE |  | 100% | 0% | 100% | 100% | 100% | 100%
|  | PUT |  | 50% | 100% | 90 o 110% | 95 o 105% | 107.5% | 0%

## F-10
FORM 10
LOGIC FRAMEWORK
SELECTED ALTERNATIVE
Description | Summary of Objectives | Indicators | Means of Verification | Assumptions
TARGET | Increase the socio-economic development and good quality of life, ensuring an efficient product and a reduced tariff | * Quality Product (voltage) * Quality of Supply (Interruptions) * Quality of street lighting and commercial services * Interconección new special loads (UPIS, Puerto Maldonado Housing Association, the Mining Area Huepetuhe) | * Quality Product (voltage) * Tolerances indicators variations of voltage levels, number and total duration of interruptions fixed in the Standard Technical Quality of Service Electric (NTCSE) * Standard Technical Lighting Public Roads RM No. 013-2003-EM-DM and R.M. No. 18 | * Compliance with the technical standards of electricity services quality from the Company Electrosur Este SAA, which are audited by OSINERG.
* Growth of household and special connections.
PURPOSE | * Electricity supply to Tambopata and El Manu (additional benefit to small electric systems - PSE - of Puerto Maldonado, Mazuko and Iberia for future interconnection), in Madre de Dios. * Reduction of costs of purchase prices | * 23 377 families will have electric service at the end of the year in Madre de Dios. * Increased demand in kW (meters totalisators) | * INEI (National Institute of Estadistics and Informatics) as a source to know the level of growth in macroeconomic indicators. | * Electrification.Coefficient
|  | * Growth of productive activities and tourist trade in the region. | * Surveys to obtain social and economic information in the area of the project | *Population increase rate
* Revenue of the new PSE to the system
* Introduction of new mine loads and big production loads
COMPONENTS | * Expansion of subestation San Gaban in one cell 138 kV | * km of installed line. | * Surverys to the stakeholders | * The company has the financial resources to execute the project in the estimated schelude.
| * Implementation of the transmission lines in 138 kV San Gaban- Mazuko of 67,6 km and in 66 kV Mazuko Pto Maldonado of 158 km | * Installed MVA. | * Execution of the transmission line San Gaban-Mazuko-Puerto Maldonado and subestations works.
| * Implementation of the substation Puerto Maldonado 66/33/10 kV 16-12,3/3,9-5/12,3-16 MVA in the facilities of the thermal power plant |  | * Execution of the line and sub station work
* Implementation of the substation Mazuko 138/66/33 Kv 20-26/12,3-16/8-10,5 MVA
ACTIONS | * Call for consultant companies for the construction of the project | * Economic indicators, environmental studies | * Approved Feasibility study for the project | * The material prices for the project do not suffer important variations
| * Approval of the deinitive project | * Approval of resources for the project execution | * Work file, for closure
| * Call for companies for the execution of the project. |  |  | * The project has positive economic indicators, the EIA (environmental impact study) is in process and has the certificate of non existence of archaeological rests (CIRA)

## Res-Inver
ANEX Nº 3.1.1
SUMMARY OF INVESTMENT ESTIMATED
PROJECT : ENERGY INTERCONNECTION CH. SAN GABÁN - PUERTO MALDONADO
November del 2005
Exchange Rate: |  | 3.412 | S/. / US$
ITEM | DESCRIPCIÓN | INVERSIONES
|  | A precios Privados |  | A precios Sociales | [7 empty] | No dot erase
|  | US $ | S/. | US $ | S/. | [6 empty] | Sensitivity | 100%
1 | INTANGIBLES | 106400 | 363036.8 | 106400 | 363036.8
1.1 | Updating of the Final Engineering Study | 80000 | 272960 | 80000 | 272960 |  |  |  | 0.30303 | 69.7879
1.2 | Oversight of the Studies and Administrative costs (8% of A) | 6400 | 21836.8 | 6400 | 21836.8
1.3 | Technical Study and managemente of "servdumbre " (area below the line) | 20000 | 68240 | 20000 | 68240
2 | INVESTMENTS IN ASSETS | 10789063.14 | 36812283.42 | 10501407.02 | 35830800.71
2.1 | Línea 138 kV San Gabán-Mazuko-67,6 km-200 mm² AAAC | 3383962.02 | 11546078.4122 | 3303041.24 | 11269976.7109
2,1,1 | Direct Costs | 2883614.97 | 9838894.2776 | 2802694.19 | 9562792.5763
| Equipment and Material Supplying | 1452081.16 | 4954500.92 | 1371160.38 | 4678399.22
| Electromechanical assembly and Civil Works | 1315367.32 | 4488033.3 | 1315367.32 | 4488033.3
| Equipment and material transportation | 116166.49 | 396360.06 | 116166.49 | 396360.06
2,1,2 | Indirect Costs | 500347.05 | 1707184.14 | 500347.05 | 1707184.14
| Easement (cost of land) | 10132.5 | 34572.09 | 10132.5 | 34572.09
| General Expenses | 288361.5 | 983889.44 | 288361.5 | 983889.44
| Utilities | 201853.05 | 688722.61 | 201853.05 | 688722.61
2.2 | LT-66kV Mazk-Pto Mald-Tramo I- 26,8 km 200 mm² AAAC | 1072724.8544 | 3660137.19 | 1046923.8268 | 3572104.08
2,2,1 | Direct Costs | 913652.0144 | 3117380.67 | 887850.9868 | 3029347.56
| Equipment and Material Supplying | 444664.032 | 1517193.68 | 418863.0044 | 1429160.57
| Electromechanical assembly and Civil Works | 433414.8598 | 1478811.5 | 433414.8598 | 1478811.5
| Equipment and material transportation | 35573.1226 | 121375.49 | 35573.1226 | 121375.49
2,2,2 | Indirect Costs | 159072.84 | 542756.52 | 159072.84 | 542756.52 |  |  | 158
| Easement (cost of land) | 3752 | 12801.82 | 3752 | 12801.82
| General Expenses | 91365.2 | 311738.06 | 91365.2 | 311738.06
| Utilities | 63955.64 | 218216.64 | 63955.64 | 218216.64
2.3 | LT-66kV Mazk-Pto Mald-Tramo II- 125,9 km 200 mm² AAAC | 3424625.1783 | 11684821.1 | 3315239.5991 | 11311597.5
2,3,1 | Direct Costs | 2911965.1083 | 9935624.95 | 2802579.5291 | 9562401.35
| Equipment and Material Supplying | 1564217.1009 | 5337108.75 | 1454831.5216 | 4963885.15
| Electromechanical assembly and Civil Works | 1245442.0074 | 4249448.13 | 1245442.0074 | 4249448.13
| Equipment and material transportation | 102306 | 349068.07 | 102306 | 349068.07
2,3,2 | Indirect Costs | 512660.07 | 1749196.15 | 512660.07 | 1749196.15
| Easement (cost of land) | 17626 | 60139.91 | 17626 | 60139.91
| General Expenses | 291196.51 | 993562.49 | 291196.51 | 993562.49
| Utilities | 203837.56 | 695493.75 | 203837.56 | 695493.75 | [6 empty] | 158
2.4 | LT-66kV Mazk-Pto Mald-Tramo III- 5,3 km 200 mm² AAAC | 226330.1292 | 772238.41 | 220796.8035 | 753358.7
2,4,1 | Direct Costs | 190726.6092 | 650759.2 | 185193.2835 | 631879.49
| Equipment and Material Supplying | 108571.0217 | 370444.33 | 103037.6959 | 351564.62
| Electromechanical assembly and Civil Works | 73469.9058 | 250679.32 | 73469.9058 | 250679.32
| Equipment and material transportation | 8685.6817 | 29635.55 | 8685.6817 | 29635.55
2,4,2 | Indirect Costs | 35603.52 | 121479.21 | 35603.52 | 121479.21
| Easement (cost of land) | 3180 | 10850.16 | 3180 | 10850.16
| General Expenses | 19072.66 | 65075.92 | 19072.66 | 65075.92
| Utilities | 13350.86 | 45553.13 | 13350.86 | 45553.13
2.5 | Expansion of the San Gabán 138 kV Substation | 229482.94 | 782995.79 | 226228.95 | 771893.17 | 98.58% | 260749 | 31266.06
2,5,1 | Direct Costs | 183318.75 | 625483.58 | 180064.76 | 614380.96
| Equipment and Material Supplying | 134813.46 | 459983.53 | 131559.47 | 448880.91
| Electromechanical assembly | 14893.8 | 50817.65 | 14893.8 | 50817.65
| Civil works | 22826.41 | 77883.71 | 22826.41 | 77883.71
| Equipment and material transportation | 10785.08 | 36798.69 | 10785.08 | 36798.69
2,5,2 | Indirect Costs | 46164.19 | 157512.21 | 46164.19 | 157512.21
| Easement (cost of land) | 15000 | 51180 | 15000 | 51180
| General Expenses | 18331.88 | 62548.37 | 18331.88 | 62548.37
| Utilities | 12832.31 | 43783.84 | 12832.31 | 43783.84
2.6 | Mazuko Subestation138/66/33 kV 20-26/12,3-16/8-10,5 MVA | 1261441.36 | 4304037.91 | 1241445.45 | 4235811.8675 | 98.41% | 1064939
2,6,1 | Direct Costs | 1070462.7 | 3652418.73 | 1050466.79 | 3584192.6875
| Equipment and Material Supplying | 849528.21 | 2898590.25 | 829532.3 | 2830364.21
| Electromechanical assembly | 55541.12 | 189506.3 | 55541.12 | 189506.3
| Civil works | 97431.11 | 332434.95 | 97431.11 | 332434.95
| Equipment and material transportation | 67962.26 | 231887.23 | 67962.26 | 231887.23
2,6,2 | Indirect Costs | 190978.66 | 651619.18 | 190978.66 | 651619.18
| Easement (cost of land) | 9000 | 30708 | 9000 | 30708
| General Expenses | 107046.27 | 365241.87 | 107046.27 | 365241.87
| Utilities | 74932.39 | 255669.31 | 74932.39 | 255669.31
2.7 | Puerto Maldonado Substation 66/33/10 kV 12,3-16/3,9-5/12,3-16 MVA | 829308.54 | 2829600.74 | 816058.12 | 2784390.3036 | 98.4% | 1064939
2,7,1 | Direct Costs | 708810.72 | 2418462.18 | 695560.3 | 2373251.7436
| Equipment and Material Supplying | 574133.41 | 1958943.19 | 560882.99 | 1913732.76
| Electromechanical assembly | 47504.31 | 162084.71 | 47504.31 | 162084.71
| Civil works | 41242.33 | 140718.83 | 41242.33 | 140718.83
| Equipment and material transportation | 45930.67 | 156715.45 | 45930.67 | 156715.45
2,7,2 | Indirect Costs | 120497.82 | 411138.56 | 120497.82 | 411138.56
| Easement (cost of land) | 0 | 0 | 0 | 0
| General Expenses | 70881.07 | 241846.21 | 70881.07 | 241846.21
| Utilities | 49616.75 | 169292.35 | 49616.75 | 169292.35
2.8 | Communication Systems | 361188.12 | 1232373.8654 | 331673.03 | 1131668.3784 | 91.83% | 400000
2,8,1 | Direct Costs | 308707.79 | 1053310.98 | 279192.7 | 952605.49
| Equipment and Material Supplying | 219042.81 | 747374.07 | 200479.86 | 684037.28
| Equipment and Materials assembly | 78712.84 | 268568.21 | 78712.84 | 268568.21
| Equipment and material transportation | 10952.14 | 37368.7 | 0 | 0
2,8,2 | Indirect Costs | 52480.33 | 179062.88 | 52480.33 | 179062.88
| General Expenses | 30870.78 | 105331.1 | 30870.78 | 105331.1
| Utilities | 21609.55 | 73731.78 | 21609.55 | 73731.78
3 | PREOPERATIVE EXPENSES | 253945.3157 | 866461.42 | 253890.555 | 866274.57
3.1 | Finantial and administrative expenses (0,5% de 2) | 53945.3157 | 184061.42 | 53890.555 | 183874.57
3.2 | Overseeing of the works (2,5% of 2) | 200000 | 682400 | 200000 | 682400
4 | INITIAL WORKING CAPITAL | 0 | 0 | 0 | 0
5 | CONTINGENCIES (1% de 2) | 107890.6314 | 368122.8343 | 107890.6314 | 368122.8343
6 | TOTAL INVESTMENTS WITHOUT SALES TAX | 11257299.0871 | 38409904.4743 | 10969588.2064 | 37428234.9143 | 97.44% |  |  |  |  | 97.44%
| Sales genaral tax (IGV 19% Total cost) | 2138886.8265 | 7297881.8501 | 0 | 0
7 | TOTAL COST WITH I.G.V. (sale tax) | 13396185.9136 | 45707786.3245 | 10969588.2064 | 37428234.9143
| COMPARISON - Social/Private | 81.89%