## Assumptions
Wellspun India Ltd., Gujarat
Assumptions and Basis Therefor
| Details | Unit | Value | Basis
A | Furnace Oil Generator | Units | Value | Basis
1 | Furnace Oil (FO) Generator Output | kWe | 14000 | Technical Specification
2 | Auxiliary consumption | % | 4 | Plant data
3 | Net Calorific Value of FO | Kcal/Kg | 9842 | Supplier Invoice
4 | Heat rate at Generator terminal | Kcal/kwhe | 2059 | Supplier Data
5 | Genset loading | % | 81.3 | Plant Data
6 | No. fo days working | days | 350 | Plant Data
7 | No. of hours working | hours | 24 | Plant Data
8 | Lube oil consumption | Grams/kwhe | 0.7 | Plant Data
9 | Lube Oil cost | Rs./Kg. | 90 | Supplier Invoice
10 | FO landed cost | Rs./Kg. | 10.923 | Supplier Invoice
11 | Escalation assumed in FO and Lube oil cost | % p.a. | 4 | Past supplier invoice
12 | Spares and O&M cost | Re/kWh | 0.25 | Plant Data
13 | Stocking periof of FO | days | 15 | Plant Data
14 | O & M expenses | month | 1 | Plant Data
15 | Lube oil | monh | 2 | Plant Data
16 | Bank interest | % | 9 | Term Loan paper
B | Natural Gas
1 | Natural Gas (NG) Generator output - GTG | kWe | 5900 | Technical Specification
| - GDG | kWe | 6790 | Technical Specification
2 | Auxiliary consumption - GTG | % | 1.08 | Technical Specification
| - GDG | % | 2.25 | Technical Specification
3 | Net Calorific Value of FO | Kcal/SCM | 8350
4 | Heat rate at Generator terminal - GTG | Kcal/kwhe | 2808 | Technical input from supplier
| - GDG | Kcal/kwhe | 1960 | Technical input from supplier
5 | Genset loading - GTG | % | 95 | Plant Data
| - GDG |  | 70 | Plant Data
6 | No. fo days working | days | 350 | Plant Data
7 | No. of hours working | hours | 24 | Plant Data
8 | Lube oil consumption - GTG | Grams/kwhe | 0.1 | Plant Data
| - GDG | Grams/kwhe | 0.42 | Plant Data
9 | Total equipment cost - GTG | Rs. Lakhs | 1857 | Plant CAPEX document
| - GDG | Rs. lakhs | 1463 | Plant CAPEX Document
10 | Amortisation period of loan | Year | 6
11 | Initial Moratorium | Year | 1
12 | Interest on term loan | % | 9 | Term Loan paper
13 | NG landed cost | Rs./SCM | 10.67 | Supplier data
14 | Lube oil cost | Rs./Kg. | 90 | Plant Data
15 | Escalation assumed in NG and Lube oil cost | % p.a. | 4 | Plant Data
14 | Spares and O&M cost | Re/kWh | 0.25 | Plant Data
15 | Rate of depreciation | % | 10.34 | Plant Data
16 | Steam generation | TPH | 14 | Plant data
17 | Steam credit | Re./Kg. | 0.73 | Computation given in 'Steam cost' worksheet
Note: 1 million = 10 lakhs

## Furnace Oil
Techno-Commercial Analysis Cogen Plant
Summary Sheet
|  |  | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15
| Site: Gujarat |  | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO
Parameters
1 | Technical Inputs:
| Output @Generator | KWe | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000
| Aux. Consumption | KWe | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560
| Aux Consumption as % of Gross output | % | bar: Year 1 to Year 15
| Net Electrical output | KWe | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440
| Type of fuel |  | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO
| NCV | Kcal/kg | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842
| Heat Rate at Generator Terminal | Kcal/kwhe | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38
| Kwh generated @generator terminal | Kwhe/kg | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791
| Genset - Loading | % | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3%
| Genset - operating hours per Annum |  | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400
2 | Performance data:
| Gross Power Generation/Annum | Million Units | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088
| Aux Power Consumption/Annum | Million Units | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704
| Net Power Generation/Annum | Million Units | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048
| Lube oil Consumption including annual replacements | Grams/kwhe | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
| Lube Oil Cost per Kg | Rs/kg | 90 | 93.6 | 97.344 | 101.2378 | 105.2873 | 109.4988 | 113.8787 | 118.4339 | 123.1712 | 128.0981 | 133.222 | 138.5509 | 144.0929 | 149.8566 | 155.8509
3 | Equipment Price
| Total Equipment Cost including building & installation | Lakh Rupees | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Owners Costs (Civils, boiler etc) | Lakh Rupees | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Project Cost | Lakh Rupees | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Project specific - operating cost parameters
| Fuel - Landed cost | Rs/kg | 10.923 | 11.3599 | 11.8143 | 12.2869 | 12.7784 | 13.2895 | 13.8211 | 14.3739 | 14.9489 | 15.5468 | 16.1687 | 16.8155 | 17.4881 | 18.1876 | 18.9151
| Fuel Calorific Value | Kcal/kg | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842
| Fuel Cost/kwh | Rs/kwh | 2.2856 | 2.377 | 2.4721 | 2.571 | 2.6738 | 2.7807 | 2.892 | 3.0077 | 3.128 | 3.2531 | 3.3832 | 3.5185 | 3.6593 | 3.8056 | 3.9579
| Lube Oil Cost per Kwh | Rs/kwh | 0.063 | 0.06552 | 0.068141 | 0.070866 | 0.073701 | 0.076649 | 0.079715 | 0.082904 | 0.08622 | 0.089669 | 0.093255 | 0.096986 | 0.10087 | 0.1049 | 0.1091
| Spares and O & M Cost | Rs/kwh | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Fuel consumption per day | kg/day | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803
6 | Power Generation Cost-
a) | Fixed Cost: Interest cost | Rs/kwh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b) | Operating Cost:
| Fuel cost | Rs/kwh | 2.2856 | 2.377 | 2.4721 | 2.571 | 2.6738 | 2.7807 | 2.892 | 3.0077 | 3.128 | 3.2531 | 3.3832 | 3.5185 | 3.6593 | 3.8056 | 3.9579
| Lube oil cost | Rs/kwh | 0.063 | 0.06552 | 0.068141 | 0.070866 | 0.073701 | 0.076649 | 0.079715 | 0.082904 | 0.08622 | 0.089669 | 0.093255 | 0.096986 | 0.10087 | 0.1049 | 0.1091
| Spares and O & M Expenses | Rs/kwh | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Working Capital Interest | Rs/Kwh | 0.0091784 | 0.0094864 | 0.0098067 | 0.01014 | 0.010486 | 0.010847 | 0.011221 | 0.011611 | 0.012016 | 0.012438 | 0.012876 | 0.013332 | 0.013806 | 0.014299 | 0.014812
| Sub -Total | Rs/kwh | 2.6078 | 2.702 | 2.8 | 2.902 | 3.008 | 3.1182 | 3.2329 | 3.3522 | 3.4762 | 3.6052 | 3.7393 | 3.8789 | 4.0239 | 4.1748 | 4.3318
c) | Cost of Generation (a+b) | Rs/kwh | 2.6078 | 2.702 | 2.8 | 2.902 | 3.008 | 3.1182 | 3.2329 | 3.3522 | 3.4762 | 3.6052 | 3.7393 | 3.8789 | 4.0239 | 4.1748 | 4.3318
Working Capital Estimation
| `````` | Stocking period | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15
| Furnace Oil stock | 15 days | 9.3652 | 9.7398 | 10.1294 | 10.5346 | 10.9559 | 11.3942 | 11.8499 | 12.3239 | 12.8169 | 13.3296 | 13.8628 | 14.4173 | 14.994 | 15.5937 | 16.2175
| O & M Expenses | 1 month | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918
| Lube Oil stock | 2 month | 1.0039 | 1.044 | 1.0858 | 1.1292 | 1.1744 | 1.2214 | 1.2702 | 1.3211 | 1.3739 | 1.4289 | 1.486 | 1.5454 | 1.6073 | 1.6716 | 1.7384
| Total current assets |  | 12.3609 | 12.7757 | 13.207 | 13.6556 | 14.1222 | 14.6074 | 15.112 | 15.6368 | 16.1826 | 16.7503 | 17.3406 | 17.9546 | 18.5931 | 19.2571 | 19.9477
| Less: Margin money at 25% |  | 3.0902 | 3.1939 | 3.3018 | 3.4139 | 3.5305 | 3.6519 | 3.778 | 3.9092 | 4.0457 | 4.1876 | 4.3352 | 4.4886 | 4.6483 | 4.8143 | 4.9869
| Less: Sundry creditors | 0 days | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bank Borrowing |  | 9.2707 | 9.5818 | 9.9053 | 10.2417 | 10.5916 | 10.9556 | 11.334 | 11.7276 | 12.137 | 12.5627 | 13.0055 | 13.4659 | 13.9448 | 14.4428 | 14.9608
| Interst on Bank borrowing ( 9%) |  | 0.83436 | 0.86236 | 0.89148 | 0.92176 | 0.95325 | 0.986 | 1.0201 | 1.0555 | 1.0923 | 1.1306 | 1.1705 | 1.2119 | 1.255 | 1.2999 | 1.3465
Note on B31: What is the objective of this section? To show various componant of cost

## NG
Techno-Commercial Analysis Cogen Plant
Summary Sheet
|  |  | Year | 1 |  | Year | 2 |  | Year | 3 |  | Year | 4 |  | Year | 5 |  | Year | 6 |  | Year | 7 |  | Year | 8 |  | Year | 9 |  | Year | 10 |  | Year | 11 |  | Year | 12 |  | Year | 13 |  | Year | 14 |  | Year | 15
| Site: Gujarat |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas
| Parameters |  | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total
1 | Technical Inputs:
| Output @Generator | KWe | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690
| Aux. Consumption | KWe | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66
| Aux Consumption as % of Gross output | % | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707%
| Net Electrical output | KWe | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34
| Type of fuel |  | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS
| NCV | Kcal/SCM | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350
| Heat Rate at Generator Terminal | Kcal/kwhe | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424
| Kwh generated @generator terminal | Kwhe/SCM | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106
| Genset - Loading | % | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70%
| Genset - operating hours per Annum |  | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400
2 | Performance data:
| Gross Power Generation/Annum | Million Units | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072
| Aux Power Consumption/Annum | Million Units | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199
| Net Power Generation/Annum | Million Units | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873
| Lube oil Consumption including annual replacements | Grams/kwhe | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424
| Lube Oil Cost per Kg | Rs/kg | 90 | 90 | 90 | 93.6 | 93.6 | 93.6 | 97.344 | 97.344 | 97.344 | 101.2378 | 101.2378 | 101.2378 | 105.2873 | 105.2873 | 105.2873 | 109.4988 | 109.4988 | 109.4988 | 113.8787 | 113.8787 | 113.8787 | 118.4339 | 118.4339 | 118.4339 | 123.1712 | 123.1712 | 123.1712 | 128.0981 | 128.0981 | 128.0981 | 133.222 | 133.222 | 133.222 | 138.5509 | 138.5509 | 138.5509 | 144.0929 | 144.0929 | 144.0929 | 149.8566 | 149.8566 | 149.8566 | 155.8509 | 155.8509 | 155.8509
3 | Equipment Price
| Total Equipment Cost including building & installation | Lakh Rupees | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320
| Owners Costs (Civils, boiler etc) | Lakh Rupees
| Total Project Cost | Lakh Rupees | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320
4 | Cost of Capital considerations:
| Term Loan 100% of Total Project Cost | Lakh Rupees | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1485.6 | 1170.4 | 2656 | 1114.2 | 877.8 | 1992 | 742.8 | 585.2 | 1328 | 371.4 | 292.6 | 664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Prencipal repayment | Lakh Rupees |  |  |  | 371.4 | 292.6 | 664 | 371.4 | 292.6 | 664 | 371.4 | 292.6 | 664 | 371.4 | 292.6 | 664 | 371.4 | 292.6 | 664 | [12 empty] | 0 | 0 | 0
| Net Term loan for interest payment | Lakh Rupees | 1857 | 1463 | 3320 | 1485.6 | 1170.4 | 2656 | 1114.2 | 877.8 | 1992 | 742.8 | 585.2 | 1328 | 371.4 | 292.6 | 664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rate of Interest on loan | % | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9%
| Deprecaition on the capital equipment | 10.34% | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 39.62 | 31.22 | 70.84
5 | Project specific - operating cost parameters
| Fuel - Landed cost | Rs/SCM | 10.67 | 10.67 | 10.67 | 11.0968 | 11.0968 | 11.0968 | 11.5407 | 11.5407 | 11.5407 | 12.0023 | 12.0023 | 12.0023 | 12.4824 | 12.4824 | 12.4824 | 12.9817 | 12.9817 | 12.9817 | 13.501 | 13.501 | 13.501 | 14.041 | 14.041 | 14.041 | 14.6026 | 14.6026 | 14.6026 | 15.1867 | 15.1867 | 15.1867 | 15.7942 | 15.7942 | 15.7942 | 16.426 | 16.426 | 16.426 | 17.083 | 17.083 | 17.083 | 17.7663 | 17.7663 | 17.7663 | 18.477 | 18.477 | 18.477
| Fuel Calorific Value | Kcal/SCM | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350
| Fuel Cost/kwh | Rs/kwh | 3.5882 | 2.5046 | 3.1285 | 3.7317 | 2.6048 | 3.2536 | 3.881 | 2.7089 | 3.3838 | 4.0362 | 2.8173 | 3.5191 | 4.1977 | 2.93 | 3.6599 | 4.3656 | 3.0472 | 3.8063 | 4.5402 | 3.1691 | 3.9585 | 4.7218 | 3.2958 | 4.1169 | 4.9107 | 3.4277 | 4.2815 | 5.1071 | 3.5648 | 4.4528 | 5.3114 | 3.7074 | 4.6309 | 5.5238 | 3.8557 | 4.8161 | 5.7448 | 4.0099 | 5.0088 | 5.9746 | 4.1703 | 5.2091 | 6.2136 | 4.3371 | 5.4175
| Lube Oil Cost per Kwh | Rs/kwh | 0.009 | 0.0378 | 0.025582 | 0.00936 | 0.039312 | 0.026605 | 0.0097344 | 0.040884 | 0.027669 | 0.010124 | 0.04252 | 0.028776 | 0.010529 | 0.044221 | 0.029927 | 0.01095 | 0.045989 | 0.031124 | 0.011388 | 0.047829 | 0.032369 | 0.011843 | 0.049742 | 0.033664 | 0.012317 | 0.051732 | 0.03501 | 0.01281 | 0.053801 | 0.036411 | 0.013322 | 0.055953 | 0.037867 | 0.013855 | 0.058191 | 0.039382 | 0.014409 | 0.060519 | 0.040957 | 0.014986 | 0.06294 | 0.042596 | 0.015585 | 0.065457 | 0.044299
| Spares and O & M Cost | Rs/kwh | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Gas consumption per day | SCM/day | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735
6 | Power Generation Cost-
a) | Fixed Cost: Interest cost | Rs/kwh | 0.35907 | 0.34074 | 0.35076 | 0.32316 | 0.30667 | 0.31568 | 0.25135 | 0.23852 | 0.24553 | 0.17953 | 0.17037 | 0.17538 | 0.10772 | 0.10222 | 0.10523 | 0.035907 | 0.034074 | 0.035076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b) | Operating Cost:
| Fuel cost | Rs/kwh | 3.5882 | 2.5046 | 3.1285 | 3.7317 | 2.6048 | 3.2536 | 3.881 | 2.7089 | 3.3838 | 4.0362 | 2.8173 | 3.5191 | 4.1977 | 2.93 | 3.6599 | 4.3656 | 3.0472 | 3.8063 | 4.5402 | 3.1691 | 3.9585 | 4.7218 | 3.2958 | 4.1169 | 4.9107 | 3.4277 | 4.2815 | 5.1071 | 3.5648 | 4.4528 | 5.3114 | 3.7074 | 4.6309 | 5.5238 | 3.8557 | 4.8161 | 5.7448 | 4.0099 | 5.0088 | 5.9746 | 4.1703 | 5.2091 | 6.2136 | 4.3371 | 5.4175
| Lube oil cost | Rs/kwh | 0.009 | 0.0378 | 0.025582 | 0.00936 | 0.039312 | 0.026605 | 0.0097344 | 0.040884 | 0.027669 | 0.010124 | 0.04252 | 0.028776 | 0.010529 | 0.044221 | 0.029927 | 0.01095 | 0.045989 | 0.031124 | 0.011388 | 0.047829 | 0.032369 | 0.011843 | 0.049742 | 0.033664 | 0.012317 | 0.051732 | 0.03501 | 0.01281 | 0.053801 | 0.036411 | 0.013322 | 0.055953 | 0.037867 | 0.013855 | 0.058191 | 0.039382 | 0.014409 | 0.060519 | 0.040957 | 0.014986 | 0.06294 | 0.042596 | 0.015585 | 0.065457 | 0.044299
| Spares and O & M Expenses | Rs/kwh | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Depreciation Cost | Rs/kwh | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.085121 | 0.080793 | 0.083158 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sub -Total | Rs/kwh | 4.2597 | 3.1839 | 3.807 | 4.4036 | 3.2855 | 3.9332 | 4.5532 | 3.3913 | 4.0644 | 4.7089 | 3.5013 | 4.2009 | 4.8707 | 3.6157 | 4.3428 | 5.0391 | 3.7347 | 4.4904 | 5.2141 | 3.8584 | 4.6439 | 5.3962 | 3.9871 | 4.8035 | 5.5855 | 4.1209 | 4.9695 | 5.455 | 3.9494 | 4.8224 | 5.5747 | 4.0133 | 4.9188 | 5.7877 | 4.1639 | 5.1055 | 6.0092 | 4.3204 | 5.2997 | 6.2396 | 4.4832 | 5.5017 | 6.4792 | 4.6526 | 5.7118
c) | Cost of Generation (a+b) | Rs/kwh | 4.6188 | 3.5246 | 4.1578 | 4.7268 | 3.5922 | 4.2489 | 4.8046 | 3.6298 | 4.3099 | 4.8884 | 3.6717 | 4.3762 | 4.9785 | 3.7179 | 4.448 | 5.075 | 3.7687 | 4.5254 | 5.2141 | 3.8584 | 4.6439 | 5.3962 | 3.9871 | 4.8035 | 5.5855 | 4.1209 | 4.9695 | 5.455 | 3.9494 | 4.8224 | 5.5747 | 4.0133 | 4.9188 | 5.7877 | 4.1639 | 5.1055 | 6.0092 | 4.3204 | 5.2997 | 6.2396 | 4.4832 | 5.5017 | 6.4792 | 4.6526 | 5.7118
| Steam generation from engine exhaust:- | TPH | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14
| Steam credit @0.73/kg | 0.73 | 1.7512 | 0 | 0.81935 | 1.8212 | 0 | 0.85212 | 1.8941 | 0 | 0.88621 | 1.9698 | 0 | 0.92165 | 2.0486 | 0 | 0.95852 | 2.1306 | 0 | 0.99686 | 2.2158 | 0 | 1.0367 | 2.3044 | 0 | 1.0782 | 2.3966 | 0 | 1.1213 | 2.4925 | 0 | 1.1662 | 2.5922 | 0 | 1.2128 | 2.6958 | 0 | 1.2613 | 2.8037 | 0 | 1.3118 | 2.9158 | 0 | 1.3643 | 3.0325 | 0 | 1.4188
| Net Cost of Generation | Rs/kwh | 2.8676 | 3.5246 | 3.3384 | 2.9056 | 3.5922 | 3.3968 | 2.9105 | 3.6298 | 3.4237 | 2.9186 | 3.6717 | 3.4546 | 2.9298 | 3.7179 | 3.4895 | 2.9444 | 3.7687 | 3.5286 | 2.9983 | 3.8584 | 3.6071 | 3.0918 | 3.9871 | 3.7253 | 3.1889 | 4.1209 | 3.8482 | 2.9626 | 3.9494 | 3.6562 | 2.9826 | 4.0133 | 3.7059 | 3.0919 | 4.1639 | 3.8442 | 3.2055 | 4.3204 | 3.9879 | 3.3238 | 4.4832 | 4.1375 | 3.4467 | 4.6526 | 4.293
| Working Capital Estimation | Stocking period | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
| Natural gas | 0
| O & M Expenses | 1 month | 1: 1.8127
| Lube Oil Cost | 2 month | 1: 0.37097
| Total |  | 1: 2.1836
| less (sundry creditors for gas) | 10 days | 1: 7.7771
| Bank Borrowing |  | 1: -5.5935

## NPVat 9%FO (14)
Net Present Value at 9%
1. Total savings/loss from Switch over
Year | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15
Cost per unit with FO based electricity generation | 2.6078 | 2.702 | 2.8 | 2.902 | 3.008 | 3.1182 | 3.2329 | 3.3522 | 3.4762 | 3.6052 | 3.7393 | 3.8789 | 4.0239 | 4.1748 | 4.3318
Cost per unit with Gas based electricity generation | 3.3384 | 3.3968 | 3.4237 | 3.4546 | 3.4895 | 3.5286 | 3.6071 | 3.7253 | 3.8482 | 3.6562 | 3.7059 | 3.8442 | 3.9879 | 4.1375 | 4.293
Savings in power cost / unit | -0.73069 | -0.69475 | -0.62371 | -0.55262 | -0.4815 | -0.41034 | -0.37421 | -0.37312 | -0.37199 | -0.050985 | 0.033401 | 0.034678 | 0.036006 | 0.037387 | 0.038823
Total units produced in a year (Lac KWH/yr) from FO | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048
Cost of Generation from FO | 2370.5711 | 2456.2496 | 2545.3554 | 2638.0253 | 2734.4021 | 2834.6339 | 2938.875 | 3047.2857 | 3160.0329 | 3277.2899 | 3399.2373 | 3526.0625 | 3657.9608 | 3795.1349 | 3937.7961
Total units produced in a year (Lac KWH/yr) from NG | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726
Cost of Generation from NG | 2843.9289 | 2893.6039 | 2916.581 | 2942.8676 | 2972.596 | 3005.904 | 3072.8147 | 3173.4771 | 3278.1659 | 3114.5943 | 3156.9857 | 3274.7464 | 3397.2176 | 3524.5876 | 3657.0523
Total saving in a year Rs./lacs | -473.3579 | -437.3542 | -371.2256 | -304.8422 | -238.1939 | -171.2701 | -133.9397 | -126.1913 | -118.133 | 162.6957 | 242.2515 | 251.3161 | 260.7432 | 270.5474 | 280.7437
2. NPV without CDM benefits
Year | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15
Savings in one year Cash inflows (Rs. / lacs) | -473.3579 | -437.3542 | -371.2256 | -304.8422 | -238.1939 | -171.2701 | -133.9397 | -126.1913 | -118.133 | 162.6957 | 242.2515 | 251.3161 | 260.7432 | 270.5474 | 280.7437
Depreciation Cost | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 70.84
CDM Credits (Rs. / lacs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repayment of Term loan |  | -664 | -664 | -664 | -664 | -664
Cash inflows (Expected Savings) (Rs. / lacs) | -130.0699 | -758.0662 | -691.9376 | -625.5542 | -558.9059 | -491.9821 | 209.3483 | 217.0967 | 225.155 | 233.5357 | 242.2515 | 251.3161 | 260.7432 | 270.5474 | 280.7437
NPV @9% without CDM Credits | -1539.3381
3. NPV with CDM benefits
Year | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15
Savings in one year Cash inflows (Rs. / lacs) | -473.3579 | -437.3542 | -371.2256 | -304.8422 | -238.1939 | -171.2701 | -133.9397 | -126.1913 | -118.133 | 162.6957 | 242.2515 | 251.3161 | 260.7432 | 270.5474 | 280.7437
Depreciation Cost | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 70.84 | 0 | 0 | 0 | 0 | 0
CDM Credits (Rs. / lacs) | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 0 | 0 | 0 | 0 | 0
Repayment of Term loan | 0 | -664 | -664 | -664 | -664 | -664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cash inflows (Expected Savings) (Rs. / lacs) | 150.2755 | -477.7208 | -411.5922 | -345.2089 | -278.5606 | -211.6367 | 489.6936 | 497.442 | 505.5004 | 513.881 | 242.2515 | 251.3161 | 260.7432 | 270.5474 | 280.7437
NPV @9% with CDM Credits | 259.8226
Note:1million =10 lacs

## GT aux
Computation of Auxiliary Consumption for Natural Gas
Components | Voltage | Power
Starting electric motor (peak load) | 3 x 380 V | 140 | kW (*)
HP liquid fuel pump motor | 3 x 380 V | 10 | kW (*)
(liquid fuel only)
Electrostatic filter | 3 x 380 V | 1.5 | kW
Air cooling ventilation fans ( 4) | 3 x 380 V | 20 | kW
Oil cooler fans ( 4) | 3 x 380 V | 12 | kW
Lube oil heater (2) | 3 x 380 V | 9 | kW (*)
Lighting (4) | 1 x 220 V | 0.5 | kW (*)
Ancilliary equipment | 1 x 220 V | 1.5 | KW
Enclosure heater (4) | 1 x 220 V | 4 | kW (*)
Generator heater | 1 x 220 V | 1 | kW (*)
24 VDC Battery charger | 1 x 220 V | 2.5 | kW
Pre/post lube oil pump motor | 3 x 380 V | 1.4 | kW (*)
Cubicle air conditioner | 24 V/DC | 1.2 | kW
DC-emergency lube oil pump | 24 V/DC | 0.3 | KW (*)
Total |  | 204.9 | KW
Equipments of stand by nature |  | 165.9 | KW
Actual load |  | 39 | KW
Load factor of stand by load |  | 15% | %
Stand by load |  | 24.885 | KW
Total aux load |  | 63.885 | KW
Auxiliary Consumption |  | 0.010828
147.5

## GE aux
Computation of Auxiliary Consumption for Natural Gas
Components | Voltage | Power
Pre-lubrication Pump | 3Ph,360/660 V | 15 | kW (*)
Pre-heating Pump | 3Ph,220/380 V | 4 | kW (*)
After Cooling Pump | 3Ph,220/244 V | 0.37 | kW (*)
LT water circuit pump | 3Ph,373/456 or 415 V | 18.5 | kW
Alternator Driving End Cooling | 3Ph,220/380 v | 0.37 | kW
Exhaust gas purging System | 3Ph,230/400 V | 0.8 | kW (*)
HT Circuit Cooling Tower Pump | 3Ph,415 V | 45 | KW
HT Circuit Cooling Tower Fan | 3Ph,415 V | 22 | KW
LT Circuit Cooling Tower Pump | 3Ph,415 V | 45 | KW
LT Circuit Cooling Tower Fan | 3Ph,415 V | 11 | KW
Lighting | 1 x 220 V | 7 | kW (*)
Generator heater | 1 x 220 V | 1 | kW (*)
Turning Gear Drive | 3Ph,400 V | 1.5 | kW (*)
Jacket Water Pre-heating Unit | 3Ph,400 V | 27 | kW (*)
Crankcase Ventilation Unit | 3Ph,200 to 255 V-346 to 440V | 2.2 | KW
Total |  | 200.74 | KW
Equipments of stand by nature |  | 56.67 | KW
Actual load |  | 144.07 | KW
Load factor of stand by load |  | 15% | %
Stand by load |  | 8.5005 | KW
Total aux load |  | 152.5705 | KW
Auxiliary Consumption |  | 0.02247 | %

## steam cost
STEAM COST COMPUTATION
DESCRIPTION | UNIT | FO BOILER | BASIS
Net steam required from fired boiler | Tons / hr | 7
Type of fuel |  | FO
Net Calorific value of fuel | Kcal/kg | 9842 | Supplier Invoice
Thermal efficiency | % | 83 | CII Report
Enthalpy of steam at 7.5 bar | Kcal/kg | 660.2 | From steam table
Feed water temperature | deg C | 65 | Plant Data
Fuel consumption/kg steam | kg/kg steam | 0.072862 | Calculated
Steam generation / kg fuel | Kg/ltr/kg | 13.7246 | Calculated
Cost of fuel | Rs / kg | 9930 | Supplier Invoice
Fuel cost | Rs/kg steam | 0.72352 | Calculated
Fuel consumption/day | kg/day | 12240.8267 | Calculated
Connected electrical load | kw | 53
Power consumption | Kwh | 42 | Plant Data
Manpower:
Operator @Rs 4500/- PM | No. | 3 | Plant Data
Fireman @ 2500/- PM | No. | 0 | Plant Data
Helper @ 2500/- PM | No. | 3 | Plant Data
Power cost @ 2,40/kwh | RsLacs/Month | 0.03024 | Calculated
Manpower cost | RsLacs/Month | 0.21 | Calculated
Steam consumption | Tons / month | 5040 | Plant Data
Steam cost / month | RsLacs/Month | 36.4654 | Calculated
Operating cost | RsLacs/Month | 36.7057 | Calculated
Steam cost | Rs/kg | 0.72829 | Calculated