## Assumptions
Wellspun India Ltd., Gujarat
Assumptions and Basis Therefor
| Details | Unit | Value | Basis
A | Furnace Oil Generator | Units | Value | Basis
1 | Furnace Oil (FO) Generator Output | kWe | 14000 | Technical Specification
2 | Auxiliary consumption | % | 4 | Plant data
3 | Net Calorific Value of FO | Kcal/Kg | 9842 | Supplier Invoice
4 | Heat rate at Generator terminal | Kcal/kwhe | 2059 | Supplier Data
5 | Genset loading | % | 81.3 | Plant Data
6 | No. fo days working | days | 350 | Plant Data
7 | No. of hours working | hours | 24 | Plant Data
8 | Lube oil consumption | Grams/kwhe | 0.7 | Plant Data
9 | Lube Oil cost | Rs./Kg. | 90 | Supplier Invoice
10 | FO landed cost | Rs./Kg. | 9.93 | Supplier Invoice
11 | Escalation assumed in FO and Lube oil cost | % p.a. | 4 | Past supplier invoice
12 | Spares and O&M cost | Re/kWh | 0.25 | Plant Data
13 | Stocking periof of FO | days | 15 | Plant Data
14 | O & M expenses | month | 1 | Plant Data
15 | Lube oil | monh | 2 | Plant Data
16 | Bank interest | % | 9 | Term Loan paper
B | Natural Gas
1 | Natural Gas (NG) Generator output - GTG | kWe | 5900 | Technical Specification
| - GDG | kWe | 6790 | Technical Specification
2 | Auxiliary consumption - GTG | % | 1.08 | Technical Specification
| - GDG | % | 2.25 | Technical Specification
3 | Net Calorific Value of FO | Kcal/SCM | 8350
4 | Heat rate at Generator terminal - GTG | Kcal/kwhe | 2808 | Technical input from supplier
| - GDG | Kcal/kwhe | 1960 | Technical input from supplier
5 | Genset loading - GTG | % | 95 | Plant Data
| - GDG |  | 70 | Plant Data
6 | No. fo days working | days | 350 | Plant Data
7 | No. of hours working | hours | 24 | Plant Data
8 | Lube oil consumption - GTG | Grams/kwhe | 0.1 | Plant Data
| - GDG | Grams/kwhe | 0.42 | Plant Data
9 | Total equipment cost - GTG | Rs. Lakhs | 1857 | Plant CAPEX document
| - GDG | Rs. lakhs | 1463 | Plant CAPEX Document
10 | Amortisation period of loan | Year | 6
11 | Initial Moratorium | Year | 1
12 | Interest on term loan | % | 9 | Term Loan paper
13 | NG landed cost | Rs./SCM | 9.7 | Supplier data
14 | Lube oil cost | Rs./Kg. | 90 | Plant Data
15 | Escalation assumed in NG and Lube oil cost | % p.a. | 4 | Plant Data
14 | Spares and O&M cost | Re/kWh | 0.25 | Plant Data
15 | Rate of depreciation | % | 10.34 | Plant Data
16 | Steam generation | TPH | 14 | Plant data
17 | Steam credit | Re./Kg. | 0.73 | Computation given in 'Steam cost' worksheet
Note: 1 million = 10 lakhs

## Furnace Oil
Techno-Commercial Analysis Cogen Plant
Summary Sheet
|  |  | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15
| Site: Gujarat |  | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO | DG - HFO
Parameters
1 | Technical Inputs:
| Output @Generator | KWe | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000 | 14000
| Aux. Consumption | KWe | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560 | 560
| Aux Consumption as % of Gross output | % | bar: Year 1 to Year 15
| Net Electrical output | KWe | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440 | 13440
| Type of fuel |  | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO | HFO
| NCV | Kcal/kg | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842
| Heat Rate at Generator Terminal | Kcal/kwhe | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38 | 2059.38
| Kwh generated @generator terminal | Kwhe/kg | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791 | 4.7791
| Genset - Loading | % | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3% | 81.3%
| Genset - operating hours per Annum |  | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400
2 | Performance data:
| Gross Power Generation/Annum | Million Units | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088 | 95.6088
| Aux Power Consumption/Annum | Million Units | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704 | 4.704
| Net Power Generation/Annum | Million Units | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048 | 90.9048
| Lube oil Consumption including annual replacements | Grams/kwhe | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
| Lube Oil Cost per Kg | Rs/kg | 90 | 93.6 | 97.344 | 101.2378 | 105.2873 | 109.4988 | 113.8787 | 118.4339 | 123.1712 | 128.0981 | 133.222 | 138.5509 | 144.0929 | 149.8566 | 155.8509
3 | Equipment Price
| Total Equipment Cost including building & installation | Lakh Rupees | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Owners Costs (Civils, boiler etc) | Lakh Rupees | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total Project Cost | Lakh Rupees | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Project specific - operating cost parameters
| Fuel - Landed cost | Rs/kg | 9.93 | 10.3272 | 10.7403 | 11.1699 | 11.6167 | 12.0814 | 12.5646 | 13.0672 | 13.5899 | 14.1335 | 14.6988 | 15.2868 | 15.8982 | 16.5342 | 17.1955
| Fuel Calorific Value | Kcal/kg | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842 | 9842
| Fuel Cost/kwh | Rs/kwh | 2.0778 | 2.1609 | 2.2473 | 2.3372 | 2.4307 | 2.528 | 2.6291 | 2.7342 | 2.8436 | 2.9573 | 3.0756 | 3.1987 | 3.3266 | 3.4597 | 3.5981
| Lube Oil Cost per Kwh | Rs/kwh | 0.063 | 0.06552 | 0.068141 | 0.070866 | 0.073701 | 0.076649 | 0.079715 | 0.082904 | 0.08622 | 0.089669 | 0.093255 | 0.096986 | 0.10087 | 0.1049 | 0.1091
| Spares and O & M Cost | Rs/kwh | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Fuel consumption per day | kg/day | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803 | 57158.7803
6 | Power Generation Cost-
a) | Fixed Cost: Interest cost | Rs/kwh | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b) | Operating Cost:
| Fuel cost | Rs/kwh | 2.0778 | 2.1609 | 2.2473 | 2.3372 | 2.4307 | 2.528 | 2.6291 | 2.7342 | 2.8436 | 2.9573 | 3.0756 | 3.1987 | 3.3266 | 3.4597 | 3.5981
| Lube oil cost | Rs/kwh | 0.063 | 0.06552 | 0.068141 | 0.070866 | 0.073701 | 0.076649 | 0.079715 | 0.082904 | 0.08622 | 0.089669 | 0.093255 | 0.096986 | 0.10087 | 0.1049 | 0.1091
| Spares and O & M Expenses | Rs/kwh | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Working Capital Interest | Rs/Kwh | 0.0085462 | 0.0088289 | 0.0091229 | 0.0094287 | 0.0097467 | 0.010077 | 0.010421 | 0.010779 | 0.011151 | 0.011538 | 0.01194 | 0.012359 | 0.012794 | 0.013246 | 0.013717
| Sub -Total | Rs/kwh | 2.3993 | 2.4853 | 2.5746 | 2.6675 | 2.7642 | 2.8647 | 2.9692 | 3.0779 | 3.191 | 3.3086 | 3.4308 | 3.558 | 3.6903 | 3.8278 | 3.9709
c) | Cost of Generation (a+b) | Rs/kwh | 2.3993 | 2.4853 | 2.5746 | 2.6675 | 2.7642 | 2.8647 | 2.9692 | 3.0779 | 3.191 | 3.3086 | 3.4308 | 3.558 | 3.6903 | 3.8278 | 3.9709
Working Capital Estimation
| `````` | Stocking period | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15
| Furnace Oil stock | 15 days | 8.5138 | 8.8544 | 9.2085 | 9.5769 | 9.9599 | 10.3583 | 10.7727 | 11.2036 | 11.6517 | 12.1178 | 12.6025 | 13.1066 | 13.6309 | 14.1761 | 14.7431
| O & M Expenses | 1 month | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918 | 1.9918
| Lube Oil stock | 2 month | 1.0039 | 1.044 | 1.0858 | 1.1292 | 1.1744 | 1.2214 | 1.2702 | 1.3211 | 1.3739 | 1.4289 | 1.486 | 1.5454 | 1.6073 | 1.6716 | 1.7384
| Total current assets |  | 11.5095 | 11.8903 | 12.2862 | 12.698 | 13.1262 | 13.5716 | 14.0348 | 14.5165 | 15.0175 | 15.5385 | 16.0804 | 16.6439 | 17.23 | 17.8395 | 18.4734
| Less: Margin money at 25% |  | 2.8774 | 2.9726 | 3.0715 | 3.1745 | 3.2816 | 3.3929 | 3.5087 | 3.6291 | 3.7544 | 3.8846 | 4.0201 | 4.161 | 4.3075 | 4.4599 | 4.6184
| Less: Sundry creditors | 0 days | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Bank Borrowing |  | 8.6322 | 8.9177 | 9.2146 | 9.5235 | 9.8447 | 10.1787 | 10.5261 | 10.8874 | 11.2631 | 11.6539 | 12.0603 | 12.4829 | 12.9225 | 13.3796 | 13.8551
| Interst on Bank borrowing ( 9%) |  | 0.77689 | 0.80259 | 0.82932 | 0.85711 | 0.88602 | 0.91608 | 0.94735 | 0.97986 | 1.0137 | 1.0488 | 1.0854 | 1.1235 | 1.163 | 1.2042 | 1.247
Note on B31: What is the objective of this section? To show various componant of cost

## NG
Techno-Commercial Analysis Cogen Plant
Summary Sheet
|  |  | Year | 1 |  | Year | 2 |  | Year | 3 |  | Year | 4 |  | Year | 5 |  | Year | 6 |  | Year | 7 |  | Year | 8 |  | Year | 9 |  | Year | 10 |  | Year | 11 |  | Year | 12 |  | Year | 13 |  | Year | 14 |  | Year | 15
| Site: Gujarat |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas |  |  | Gas
| Parameters |  | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total | GTG | GDG | Total
1 | Technical Inputs:
| Output @Generator | KWe | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690 | 5900 | 6790 | 12690
| Aux. Consumption | KWe | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66 | 63.885 | 152.775 | 216.66
| Aux Consumption as % of Gross output | % | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707% | 1.083% | 2.25% | 1.707%
| Net Electrical output | KWe | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34 | 5836.115 | 6637.225 | 12473.34
| Type of fuel |  | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS | GAS
| NCV | Kcal/SCM | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350
| Heat Rate at Generator Terminal | Kcal/kwhe | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424 | 2808 | 1960 | 2448.2424
| Kwh generated @generator terminal | Kwhe/SCM | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106 | 2.9736 | 4.2602 | 3.4106
| Genset - Loading | % | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70% |  | 95% | 70%
| Genset - operating hours per Annum |  | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400 | 8400
2 | Performance data:
| Gross Power Generation/Annum | Million Units | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072 | 47.082 | 39.9252 | 87.0072
| Aux Power Consumption/Annum | Million Units | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199 | 0.53663 | 1.2833 | 1.8199
| Net Power Generation/Annum | Million Units | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873 | 46.5454 | 38.6419 | 85.1873
| Lube oil Consumption including annual replacements | Grams/kwhe | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424 | 0.1 | 0.42 | 0.28424
| Lube Oil Cost per Kg | Rs/kg | 90 | 90 | 90 | 93.6 | 93.6 | 93.6 | 97.344 | 97.344 | 97.344 | 101.2378 | 101.2378 | 101.2378 | 105.2873 | 105.2873 | 105.2873 | 109.4988 | 109.4988 | 109.4988 | 113.8787 | 113.8787 | 113.8787 | 118.4339 | 118.4339 | 118.4339 | 123.1712 | 123.1712 | 123.1712 | 128.0981 | 128.0981 | 128.0981 | 133.222 | 133.222 | 133.222 | 138.5509 | 138.5509 | 138.5509 | 144.0929 | 144.0929 | 144.0929 | 149.8566 | 149.8566 | 149.8566 | 155.8509 | 155.8509 | 155.8509
3 | Equipment Price
| Total Equipment Cost including building & installation | Lakh Rupees | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320
| Owners Costs (Civils, boiler etc) | Lakh Rupees
| Total Project Cost | Lakh Rupees | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1857 | 1463 | 3320
4 | Cost of Capital considerations:
| Term Loan 100% of Total Project Cost | Lakh Rupees | 1857 | 1463 | 3320 | 1857 | 1463 | 3320 | 1485.6 | 1170.4 | 2656 | 1114.2 | 877.8 | 1992 | 742.8 | 585.2 | 1328 | 371.4 | 292.6 | 664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Prencipal repayment | Lakh Rupees |  |  |  | 371.4 | 292.6 | 664 | 371.4 | 292.6 | 664 | 371.4 | 292.6 | 664 | 371.4 | 292.6 | 664 | 371.4 | 292.6 | 664 | [12 empty] | 0 | 0 | 0
| Net Term loan for interest payment | Lakh Rupees | 1857 | 1463 | 3320 | 1485.6 | 1170.4 | 2656 | 1114.2 | 877.8 | 1992 | 742.8 | 585.2 | 1328 | 371.4 | 292.6 | 664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Rate of Interest on loan | % | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9% | 9%
| Deprecaition on the capital equipment | 10.34% | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 192.0138 | 151.2742 | 343.288 | 36.0285 | 28.384 | 64.408
5 | Project specific - operating cost parameters
| Fuel - Landed cost | Rs/SCM | 9.7 | 9.7 | 9.7 | 10.088 | 10.088 | 10.088 | 10.4915 | 10.4915 | 10.4915 | 10.9112 | 10.9112 | 10.9112 | 11.3476 | 11.3476 | 11.3476 | 11.8015 | 11.8015 | 11.8015 | 12.2736 | 12.2736 | 12.2736 | 12.7645 | 12.7645 | 12.7645 | 13.2751 | 13.2751 | 13.2751 | 13.8061 | 13.8061 | 13.8061 | 14.3584 | 14.3584 | 14.3584 | 14.9327 | 14.9327 | 14.9327 | 15.53 | 15.53 | 15.53 | 16.1512 | 16.1512 | 16.1512 | 16.7973 | 16.7973 | 16.7973
| Fuel Calorific Value | Kcal/SCM | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350 | 8350
| Fuel Cost/kwh | Rs/kwh | 3.262 | 2.2769 | 2.8441 | 3.3925 | 2.368 | 2.9578 | 3.5282 | 2.4627 | 3.0761 | 3.6693 | 2.5612 | 3.1992 | 3.8161 | 2.6636 | 3.3272 | 3.9687 | 2.7702 | 3.4602 | 4.1275 | 2.881 | 3.5987 | 4.2926 | 2.9962 | 3.7426 | 4.4643 | 3.1161 | 3.8923 | 4.6428 | 3.2407 | 4.048 | 4.8285 | 3.3703 | 4.2099 | 5.0217 | 3.5052 | 4.3783 | 5.2225 | 3.6454 | 4.5534 | 5.4314 | 3.7912 | 4.7356 | 5.6487 | 3.9428 | 4.925
| Lube Oil Cost per Kwh | Rs/kwh | 0.009 | 0.0378 | 0.025582 | 0.00936 | 0.039312 | 0.026605 | 0.0097344 | 0.040884 | 0.027669 | 0.010124 | 0.04252 | 0.028776 | 0.010529 | 0.044221 | 0.029927 | 0.01095 | 0.045989 | 0.031124 | 0.011388 | 0.047829 | 0.032369 | 0.011843 | 0.049742 | 0.033664 | 0.012317 | 0.051732 | 0.03501 | 0.01281 | 0.053801 | 0.036411 | 0.013322 | 0.055953 | 0.037867 | 0.013855 | 0.058191 | 0.039382 | 0.014409 | 0.060519 | 0.040957 | 0.014986 | 0.06294 | 0.042596 | 0.015585 | 0.065457 | 0.044299
| Spares and O & M Cost | Rs/kwh | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Gas consumption per day | SCM/day | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735 | 44747.5556 | 26173.7179 | 70921.2735
6 | Power Generation Cost-
a) | Fixed Cost: Interest cost | Rs/kwh | 0.35907 | 0.34074 | 0.35076 | 0.32316 | 0.30667 | 0.31568 | 0.25135 | 0.23852 | 0.24553 | 0.17953 | 0.17037 | 0.17538 | 0.10772 | 0.10222 | 0.10523 | 0.035907 | 0.034074 | 0.035076 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
b) | Operating Cost:
| Fuel cost | Rs/kwh | 3.262 | 2.2769 | 2.8441 | 3.3925 | 2.368 | 2.9578 | 3.5282 | 2.4627 | 3.0761 | 3.6693 | 2.5612 | 3.1992 | 3.8161 | 2.6636 | 3.3272 | 3.9687 | 2.7702 | 3.4602 | 4.1275 | 2.881 | 3.5987 | 4.2926 | 2.9962 | 3.7426 | 4.4643 | 3.1161 | 3.8923 | 4.6428 | 3.2407 | 4.048 | 4.8285 | 3.3703 | 4.2099 | 5.0217 | 3.5052 | 4.3783 | 5.2225 | 3.6454 | 4.5534 | 5.4314 | 3.7912 | 4.7356 | 5.6487 | 3.9428 | 4.925
| Lube oil cost | Rs/kwh | 0.009 | 0.0378 | 0.025582 | 0.00936 | 0.039312 | 0.026605 | 0.0097344 | 0.040884 | 0.027669 | 0.010124 | 0.04252 | 0.028776 | 0.010529 | 0.044221 | 0.029927 | 0.01095 | 0.045989 | 0.031124 | 0.011388 | 0.047829 | 0.032369 | 0.011843 | 0.049742 | 0.033664 | 0.012317 | 0.051732 | 0.03501 | 0.01281 | 0.053801 | 0.036411 | 0.013322 | 0.055953 | 0.037867 | 0.013855 | 0.058191 | 0.039382 | 0.014409 | 0.060519 | 0.040957 | 0.014986 | 0.06294 | 0.042596 | 0.015585 | 0.065457 | 0.044299
| Spares and O & M Expenses | Rs/kwh | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25 | 0.25
| Depreciation Cost | Rs/kwh | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.41253 | 0.39148 | 0.40298 | 0.077405 | 0.073454 | 0.075608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Sub -Total | Rs/kwh | 3.9335 | 2.9562 | 3.5226 | 4.0644 | 3.0488 | 3.6374 | 4.2004 | 3.145 | 3.7568 | 4.3419 | 3.2452 | 3.8809 | 4.4891 | 3.3493 | 4.0101 | 4.6422 | 3.4576 | 4.1443 | 4.8014 | 3.5703 | 4.284 | 4.9669 | 3.6874 | 4.4292 | 5.1391 | 3.8093 | 4.5803 | 4.983 | 3.618 | 4.41 | 5.0919 | 3.6763 | 4.4978 | 5.2855 | 3.8134 | 4.6677 | 5.487 | 3.9559 | 4.8444 | 5.6964 | 4.1041 | 5.0282 | 5.9143 | 4.2583 | 5.2193
c) | Cost of Generation (a+b) | Rs/kwh | 4.2926 | 3.2969 | 3.8734 | 4.3875 | 3.3554 | 3.9531 | 4.4518 | 3.3836 | 4.0023 | 4.5215 | 3.4156 | 4.0563 | 4.5968 | 3.4516 | 4.1153 | 4.6781 | 3.4917 | 4.1794 | 4.8014 | 3.5703 | 4.284 | 4.9669 | 3.6874 | 4.4292 | 5.1391 | 3.8093 | 4.5803 | 4.983 | 3.618 | 4.41 | 5.0919 | 3.6763 | 4.4978 | 5.2855 | 3.8134 | 4.6677 | 5.487 | 3.9559 | 4.8444 | 5.6964 | 4.1041 | 5.0282 | 5.9143 | 4.2583 | 5.2193
| Steam generation from engine exhaust:- | TPH | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14 | 14 |  | 14
| Steam credit @0.73/kg | 0.73 | 1.7512 | 0 | 0.81935 | 1.8212 | 0 | 0.85212 | 1.8941 | 0 | 0.88621 | 1.9698 | 0 | 0.92165 | 2.0486 | 0 | 0.95852 | 2.1306 | 0 | 0.99686 | 2.2158 | 0 | 1.0367 | 2.3044 | 0 | 1.0782 | 2.3966 | 0 | 1.1213 | 2.4925 | 0 | 1.1662 | 2.5922 | 0 | 1.2128 | 2.6958 | 0 | 1.2613 | 2.8037 | 0 | 1.3118 | 2.9158 | 0 | 1.3643 | 3.0325 | 0 | 1.4188
| Net Cost of Generation | Rs/kwh | 2.5414 | 3.2969 | 3.054 | 2.5663 | 3.3554 | 3.101 | 2.5577 | 3.3836 | 3.1161 | 2.5517 | 3.4156 | 3.1347 | 2.5482 | 3.4516 | 3.1568 | 2.5475 | 3.4917 | 3.1826 | 2.5856 | 3.5703 | 3.2473 | 2.6625 | 3.6874 | 3.351 | 2.7425 | 3.8093 | 3.459 | 2.4906 | 3.618 | 3.2438 | 2.4997 | 3.6763 | 3.2849 | 2.5897 | 3.8134 | 3.4063 | 2.6833 | 3.9559 | 3.5326 | 2.7806 | 4.1041 | 3.6639 | 2.8818 | 4.2583 | 3.8005
| Working Capital Estimation | Stocking period | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
| Natural gas | 0
| O & M Expenses | 1 month | 1: 1.8127
| Lube Oil Cost | 2 month | 1: 0.37097
| Total |  | 1: 2.1836
| less (sundry creditors for gas) | 10 days | 1: 7.0701
| Bank Borrowing |  | 1: -4.8865

## NPVat 9%FO (14)
Net Present Value at 9%
1. Total savings/loss from Switch over
Year | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15
Cost per unit with FO based electricity generation | 2.3993 | 2.4853 | 2.5746 | 2.6675 | 2.7642 | 2.8647 | 2.9692 | 3.0779 | 3.191 | 3.3086 | 3.4308 | 3.558 | 3.6903 | 3.8278 | 3.9709
Cost per unit with Gas based electricity generation | 3.054 | 3.101 | 3.1161 | 3.1347 | 3.1568 | 3.1826 | 3.2473 | 3.351 | 3.459 | 3.2438 | 3.2849 | 3.4063 | 3.5326 | 3.6639 | 3.8005
Savings in power cost / unit | -0.6547 | -0.61572 | -0.54151 | -0.46714 | -0.3926 | -0.31788 | -0.27806 | -0.27312 | -0.26798 | 0.06473 | 0.14589 | 0.15167 | 0.15768 | 0.16392 | 0.17042
Total units produced in a year (Lac KWH/yr) from FO | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048 | 909.048
Cost of Generation from FO | 2181.115 | 2259.2153 | 2340.4397 | 2424.913 | 2512.7652 | 2604.1316 | 2699.1526 | 2797.9744 | 2900.7492 | 3007.6349 | 3118.796 | 3234.4036 | 3354.6355 | 3479.6766 | 3609.7194
Total units produced in a year (Lac KWH/yr) from NG | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726 | 851.8726
Cost of Generation from NG | 2601.6508 | 2641.6345 | 2654.5329 | 2670.3376 | 2689.1648 | 2711.1356 | 2766.2555 | 2854.6555 | 2946.5915 | 2763.3249 | 2798.3548 | 2901.7703 | 3009.3224 | 3121.1766 | 3237.5049
Total saving in a year Rs./lacs | -420.5358 | -382.4192 | -314.0932 | -245.4246 | -176.3996 | -107.004 | -67.1029 | -56.6811 | -45.8423 | 244.31 | 320.4412 | 332.6333 | 345.3131 | 358.5001 | 372.2145
2. NPV without CDM benefits
Year | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15
Savings in one year Cash inflows (Rs. / lacs) | -420.5358 | -382.4192 | -314.0932 | -245.4246 | -176.3996 | -107.004 | -67.1029 | -56.6811 | -45.8423 | 244.31 | 320.4412 | 332.6333 | 345.3131 | 358.5001 | 372.2145
Depreciation Cost | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 64.408
CDM Credits (Rs. / lacs) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Repayment of Term loan |  | -664 | -664 | -664 | -664 | -664
Cash inflows (Expected Savings) (Rs. / lacs) | -77.2478 | -703.1312 | -634.8052 | -566.1366 | -497.1116 | -427.716 | 276.1851 | 286.6069 | 297.4457 | 308.718 | 320.4412 | 332.6333 | 345.3131 | 358.5001 | 372.2145
NPV @9% without CDM Credits | -1005.2301
3. NPV with CDM benefits
Year | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Year 6 | Year 7 | Year 8 | Year 9 | Year 10 | Year 11 | Year 12 | Year 13 | Year 14 | Year 15
Savings in one year Cash inflows (Rs. / lacs) | -420.5358 | -382.4192 | -314.0932 | -245.4246 | -176.3996 | -107.004 | -67.1029 | -56.6811 | -45.8423 | 244.31 | 320.4412 | 332.6333 | 345.3131 | 358.5001 | 372.2145
Depreciation Cost | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 343.288 | 64.408 | 0 | 0 | 0 | 0 | 0
CDM Credits (Rs. / lacs) | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 280.3454 | 0 | 0 | 0 | 0 | 0
Repayment of Term loan | 0 | -664 | -664 | -664 | -664 | -664 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Cash inflows (Expected Savings) (Rs. / lacs) | 203.0976 | -422.7859 | -354.4598 | -285.7912 | -216.7662 | -147.3706 | 556.5305 | 566.9523 | 577.7911 | 589.0634 | 320.4412 | 332.6333 | 345.3131 | 358.5001 | 372.2145
NPV @9% with CDM Credits | 793.9306
Note:1million =10 lacs

## GT aux
Computation of Auxiliary Consumption for Natural Gas
Components | Voltage | Power
Starting electric motor (peak load) | 3 x 380 V | 140 | kW (*)
HP liquid fuel pump motor | 3 x 380 V | 10 | kW (*)
(liquid fuel only)
Electrostatic filter | 3 x 380 V | 1.5 | kW
Air cooling ventilation fans ( 4) | 3 x 380 V | 20 | kW
Oil cooler fans ( 4) | 3 x 380 V | 12 | kW
Lube oil heater (2) | 3 x 380 V | 9 | kW (*)
Lighting (4) | 1 x 220 V | 0.5 | kW (*)
Ancilliary equipment | 1 x 220 V | 1.5 | KW
Enclosure heater (4) | 1 x 220 V | 4 | kW (*)
Generator heater | 1 x 220 V | 1 | kW (*)
24 VDC Battery charger | 1 x 220 V | 2.5 | kW
Pre/post lube oil pump motor | 3 x 380 V | 1.4 | kW (*)
Cubicle air conditioner | 24 V/DC | 1.2 | kW
DC-emergency lube oil pump | 24 V/DC | 0.3 | KW (*)
Total |  | 204.9 | KW
Equipments of stand by nature |  | 165.9 | KW
Actual load |  | 39 | KW
Load factor of stand by load |  | 15% | %
Stand by load |  | 24.885 | KW
Total aux load |  | 63.885 | KW
Auxiliary Consumption |  | 0.010828
147.5

## GE aux
Computation of Auxiliary Consumption for Natural Gas
Components | Voltage | Power
Pre-lubrication Pump | 3Ph,360/660 V | 15 | kW (*)
Pre-heating Pump | 3Ph,220/380 V | 4 | kW (*)
After Cooling Pump | 3Ph,220/244 V | 0.37 | kW (*)
LT water circuit pump | 3Ph,373/456 or 415 V | 18.5 | kW
Alternator Driving End Cooling | 3Ph,220/380 v | 0.37 | kW
Exhaust gas purging System | 3Ph,230/400 V | 0.8 | kW (*)
HT Circuit Cooling Tower Pump | 3Ph,415 V | 45 | KW
HT Circuit Cooling Tower Fan | 3Ph,415 V | 22 | KW
LT Circuit Cooling Tower Pump | 3Ph,415 V | 45 | KW
LT Circuit Cooling Tower Fan | 3Ph,415 V | 11 | KW
Lighting | 1 x 220 V | 7 | kW (*)
Generator heater | 1 x 220 V | 1 | kW (*)
Turning Gear Drive | 3Ph,400 V | 1.5 | kW (*)
Jacket Water Pre-heating Unit | 3Ph,400 V | 27 | kW (*)
Crankcase Ventilation Unit | 3Ph,200 to 255 V-346 to 440V | 2.2 | KW
Total |  | 200.74 | KW
Equipments of stand by nature |  | 56.67 | KW
Actual load |  | 144.07 | KW
Load factor of stand by load |  | 15% | %
Stand by load |  | 8.5005 | KW
Total aux load |  | 152.5705 | KW
Auxiliary Consumption |  | 0.02247 | %

## steam cost
STEAM COST COMPUTATION
DESCRIPTION | UNIT | FO BOILER | BASIS
Net steam required from fired boiler | Tons / hr | 7
Type of fuel |  | FO
Net Calorific value of fuel | Kcal/kg | 9842 | Supplier Invoice
Thermal efficiency | % | 83 | CII Report
Enthalpy of steam at 7.5 bar | Kcal/kg | 660.2 | From steam table
Feed water temperature | deg C | 65 | Plant Data
Fuel consumption/kg steam | kg/kg steam | 0.072862 | Calculated
Steam generation / kg fuel | Kg/ltr/kg | 13.7246 | Calculated
Cost of fuel | Rs / kg | 9930 | Supplier Invoice
Fuel cost | Rs/kg steam | 0.72352 | Calculated
Fuel consumption/day | kg/day | 12240.8267 | Calculated
Connected electrical load | kw | 53
Power consumption | Kwh | 42 | Plant Data
Manpower:
Operator @Rs 4500/- PM | No. | 3 | Plant Data
Fireman @ 2500/- PM | No. | 0 | Plant Data
Helper @ 2500/- PM | No. | 3 | Plant Data
Power cost @ 2,40/kwh | RsLacs/Month | 0.03024 | Calculated
Manpower cost | RsLacs/Month | 0.21 | Calculated
Steam consumption | Tons / month | 5040 | Plant Data
Steam cost / month | RsLacs/Month | 36.4654 | Calculated
Operating cost | RsLacs/Month | 36.7057 | Calculated
Steam cost | Rs/kg | 0.72829 | Calculated