## EFFECTIVE WHR GENERATION
CALCULATION OF EFFECTIVE WHR STEAM
| a | b | c | d | e | f | g | h | i | j | k
Month | WHR # 1 Steam Generation | FBC Steam Generation | WHR # 2 Steam Generation | Total Steam Generation (a+b+c) | TG # 1 Steam Consumption | TG # 2 Steam Consumption | TG # 3 Steam Consumption | TG # 4 Steam Consumption | Total Steam Consumption (e+f+g+h) | Vent Steam from WHR # 1 | Effective WHR # 1 Steam (a-j)
Jan, 06 | 11850 | 40467 | 18165 | 70482 | 20578 | 23229 | 24884 | 0 | 68691 | 1791 | 10059
Feb, 06 | 13795 | 27033 | 20367 | 61195 | 14492 | 22075 | 23883 | 0 | 60450 | 745 | 13050
Mar, 06 | 15303 | 24784 | 17443 | 57530 | 11117 | 19955 | 23590 | 0 | 54662 | 2868 | 12435
April, 06 | 14189 | 45151 | 19292 | 78632 | 30194 | 26413 | 19786 | 0 | 76393 | 2239 | 11950
May, 06 | 14708 | 45477 | 23899 | 84084 | 29958 | 27193 | 26151 | 0 | 83302 | 782 | 13926
Jun, 06 | 3257 | 44021 | 24237 | 71515 | 30068 | 16975 | 23676 | 0 | 70719 | 796 | 2461
July, 06 | 13933 | 44640 | 7756 | 66329 | 32583 | 20063 | 13465 | 0 | 66111 | 218 | 13715
Aug, 06 | 14645 | 39884 | 6621 | 61150 | 24443 | 18646 | 15381 | 0 | 58470 | 2680 | 11965
Sep, 06 | 13189 | 45783 | 13976 | 72948 | 31251 | 19398 | 20336 | 0 | 70985 | 1963 | 11226
Oct, 06 | 9198 | 49400 | 29234 | 87832 | 34987 | 24032 | 28703 | 0 | 87722 | 110 | 9088
Nov, 06 | 15490 | 45967 | 27606 | 89063 | 29926 | 24995 | 27803 | 5965 | 88689 | 374 | 15116
Dec, 06 | 14674 | 46961 | 22959 | 84594 | 6449 | 4963 | 9600 | 62807 | 83819 | 775 | 13899
Total | 154231 | 499568 | 231555 | 885354 | 296046 | 247937 | 257258 | 68772 | 870013 | 15341 | 138890
Note on K5: Vent Steam Source: Vent steam data is obtained from the daily reports maintained in the plant. In case the WHR # 1 is not operating on a particular day, the vent steam generation for that day has been conseidered 0.

## STEAM CONSUMED IN TG4
Net Steam Consumed in the TG#4
TG # 4 Steam Consumption | Auxiliary Steam Consumption in TG#4 | Net Steam Consumed in TG#4
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
0 | 0 | 0
6032 | 67 | 5965
63002 | 195 | 62807
69034 | 262 | 68772

## CSEB GENERATION
CSEB GENERATION
Generation (kWh) |  |  |  | Gross Generation [TG#1+TG#2+ TG # 3+ TG # 4] (kWh) | Auxiliary Consumption (kWh)
TG#1 | TG#2 | TG#3 | TG#4
4072480 | 4397600 | 5731456 |  | 14201536 | 1460115
2968160 | 3976800 | 5158784 |  | 12103744 | 1086280
2115040 | 3498560 | 5170064 |  | 10783664 | 1174585
6170560 | 4561920 | 4048656 |  | 14781136 | 1504445
6102720 | 5025600 | 5796080 |  | 16924400 | 1738020
6134400 | 2827040 | 5038640 |  | 14000080 | 1646785
6247680 | 3615040 | 2891840 |  | 12754560 | 1478800
4936320 | 3465280 | 3344000 |  | 11745600 | 1482025
5836160 | 2919680 | 4065120 |  | 12820960 | 1654095
7083840 | 4174880 | 6383816 |  | 17642536 | 1771415
6007520 | 4293000 | 5904800 |  | 16205320 | 1870350
1331700 | 850500 | 2161700 | 14423200 | 18767100 | 1903367
59006580 | 43605900 | 55694956 | 14423200 | 172730636 | 18770282

## EFFECTIVE POWER GENERATION
CALCULATION OF NET WHR POWER GENERATION
| l | m | n | o | p | q | r | s | t | u | A | B | C | D | E | F | G | H
Month | Generation (kWh) |  |  |  | Gross Generation [TG#1+TG#2+ TG # 3+ TG # 4] (kWh) (l+m+n+o) | Auxiliary Consumption (kWh) | Net Generation (kWh) (p-q) | Effective WHRSG #1 Steam Flow (tonnes) | FBC Steam Flow (tonnes) | WHR # 2 Steam Generation (tonnes) | Enthalpy of WHR#1 steam (h1) (kcal/kg) | Enthalpy of FBC steam (h2) (kcal/kg) | Enthalpy of WHR#2 steam (h3) (kcal/kg) | Total enthalpy of WHR#1 steam H1 (Kcal) (A*s*1000) | Total Enthalpy of FBC steam H2 (kcal) (B*t*1000) | Total enthalpy of WHR#2 steam H3 (kcal) (C*u*1000) | Total Enthalpy (H1+H2+H3) (kcal) (D+E+F) | Net WHR #1 Power Supplied (kWh) [H1/(H1+H2+H3)]*EGnet
| TG#1 | TG#2 | TG#3 | TG#4
Jan, 06 | 4072480 | 4397600 | 5731456 |  | 14201536 | 1460115 | 12741421 | 10059 | 40467 | 18165 | 773.3353 | 775.7715 | 771.4961 | 7778979330.2462 | 31393144610.6544 | 14014227411.9824 | 53186351352.8829 | 1863546.7197
Feb, 06 | 2968160 | 3976800 | 5158784 |  | 12103744 | 1086280 | 11017464 | 13050 | 27033 | 20367 | 773.8129 | 774.7922 | 772.4038 | 10098258956.001 | 20944957948.3653 | 15731547298.6557 | 46774764203.022 | 2378573.2843
Mar, 06 | 2115040 | 3498560 | 5170064 |  | 10783664 | 1174585 | 9609079 | 12435 | 24784 | 17443 | 772.1171 | 774.1951 | 770.9946 | 9601276647.4646 | 19187651364.8438 | 13448458200.7836 | 42237386213.092 | 2184307.1761
April, 06 | 6170560 | 4561920 | 4048656 |  | 14781136 | 1504445 | 13276691 | 11950 | 45151 | 19292 | 770.6363 | 773.0964 | 770.9229 | 9209103741.3825 | 34906075968.1771 | 14872644807.3076 | 58987824516.8672 | 2072740.0233
May, 06 | 6102720 | 5025600 | 5796080 |  | 16924400 | 1738020 | 15186380 | 13926 | 45477 | 23899 | 769.657 | 771.3289 | 770.7557 | 10718243774.1562 | 35077726634.5924 | 18420290935.5507 | 64216261344.2993 | 2534736.8327
Jun, 06 | 6134400 | 2827040 | 5038640 |  | 14000080 | 1646785 | 12353295 | 2461 | 44021 | 24237 | 772.4515 | 771.6633 | 771.1856 | 1901003203.4926 | 33969391613.6881 | 18691226403.215 | 54561621220.3958 | 430406.0774
July, 06 | 6247680 | 3615040 | 2891840 |  | 12754560 | 1478800 | 11275760 | 13715 | 44640 | 7756 | 769.4421 | 771.4484 | 768.9644 | 10552897946.8478 | 34437455344.3824 | 5964087692.8878 | 50954440984.118 | 2335261.5053
Aug, 06 | 4936320 | 3465280 | 3344000 |  | 11745600 | 1482025 | 10263575 | 11965 | 39884 | 6621 | 772.4038 | 773.0964 | 771.52 | 9241810940.6597 | 30834177181.3421 | 5108234093.3378 | 45184222215.3395 | 2099273.0443
Sep, 06 | 5836160 | 2919680 | 4065120 |  | 12820960 | 1654095 | 11166865 | 11226 | 45783 | 13976 | 771.4245 | 773.8129 | 771.6633 | 8660011300.2673 | 35427478144.2601 | 10784766752.0707 | 54872256196.5981 | 1762369.2516
Oct, 06 | 7083840 | 4174880 | 6383816 |  | 17642536 | 1771415 | 15871121 | 9088 | 49400 | 29234 | 771.1379 | 773.8607 | 772.4038 | 7008100987.4611 | 38228719370.4 | 22580451403.1963 | 67817271761.0575 | 1640089.8453
Nov, 06 | 6007520 | 4293000 | 5904800 |  | 16205320 | 1870350 | 14334970 | 15116 | 45967 | 27606 | 772.0933 | 774.0279 | 772.9531 | 11670961662.8354 | 35579740853.0117 | 21338143322.2175 | 68588845838.0646 | 2439214.1793
Dec, 06 | 1331700 | 850500 | 2161700 | 14423200 | 18767100 | 1903367 | 16863733 | 13899 | 46961 | 22959 | 768.9166 | 772.7143 | 769.7287 | 10687171904.9871 | 36287434160.9885 | 17672200808.4309 | 64646806874.4065 | 2787850.2009
Total | 59006580 | 43605900 | 55694956 | 14423200 | 172730636 | 18770282 | 153960354 | 138890 | 499568 | 231555 | 771.4524 | 773.3173 | 771.2493 | 107127820395.801 | 386273953194.706 | 178626279129.636 | 672028052720.1429 | 24528368.1402
[17 empty] | Emission Reductions | 18607.4654
NET GENERATION = GROSS GENERATION - AUXILIARY CONSUMPTION | bar: E to H
Effective WHRSG#1 Steam Flow (tonnes) = WHR # 1 Steam Generation -Vent Steam | E: Emission Factor (kg CO2/kWh); H: 0.75861
Net WHR#1 Power Supplied (kWh)= ((Effective WHRSG #1 Steam Flow ) / (Effective WHRSG#1 Steam Flow + FBC Steam Flow +WHR # 2 Steam Generation))*Net Generation | bar: E to H
Net WHR Power Supplied (Million kWh )=( Net WHR Power Supplied (kWh)/1000000)
NOTE : TG # 3 , TG # 4 , GENERATION IS ALSO INCLUDED ,THE SAME WAS INTIMATED TO THE VERIFIER'S DURING THE LAST VERIFICATION
NOTE : WHRB # 2 STEAM GENERATION IS ALSO INCLUDED , THE SAME WAS INTIMATED TO THE VERIFIER'S DURING THE LAST VERIFICATION
CER
Note on I5: GPIL: After excluding vent steam
Note on S19: Net WHR#1 power generation through enthalpy aportioning method

## ENTHALPY
Month | Enthalpy (KCal/Kg)
| WHRB#1 (h1) | FBC (h2) | WHRB#2 (h3)
Jan'06 | 773.3353 | 775.7715 | 771.4961
Feb'06 | 773.8129 | 774.7922 | 772.4038
Mar'06 | 772.1171 | 774.1951 | 770.9946
Apr'06 | 770.6363 | 773.0964 | 770.9229
May'06 | 769.657 | 771.3289 | 770.7557
Jun'06 | 772.4515 | 771.6633 | 771.1856
Jul'06 | 769.4421 | 771.4484 | 768.9644
Aug'06 | 772.4038 | 773.0964 | 771.52
Sep'06 | 771.4245 | 773.8129 | 771.6633
Oct'06 | 771.1379 | 773.8607 | 772.4038
Nov'06 | 772.0933 | 774.0279 | 772.9531
Dec'06 | 768.9166 | 772.7143 | 769.7287
Average | 771.4524 | 773.3173 | 771.2493