## Baseline
Technical Energy Loss Calculations in Baseline Scenario
Months | Coal-Combusted | Coal-Audited | GCV | Energy Input | Steam values | Steam pressure | Steam Enthalpy | Feed Water | Feed Water temperature | Feed Water Enthalpy | Net Enthalpy | Boiler Efficiency | Technical Losses
Units | (tons) | (tons) | (kCal/kg) | (kCal) | (tons) | (kg/cm2) | (kCal) | (tons) | (°C) | (kCal) | (kCal) | (%) | (kCal)
April 2000 | 663.902 | 684.435 | 5258 | 3490796453.1 | 3353.7315 | 8.826 | 2225808218.8388 | 3454.3434 | 64 | 220941684.3886 | 2004866534.4503 | 57.4329 | 1485929918.6497
May 2000 | 634.4285 | 654.05 | 5794 | 3675878729 | 3508.0005 | 8.826 | 2328193638.8142 | 3613.2405 | 64 | 231104827.356 | 2097088811.4582 | 57.05 | 1578789917.5418
June 2000 | 722.8488 | 745.205 | 5621 | 4063133385.85 | 3673.8607 | 8.826 | 2438271885.9988 | 3784.0765 | 65 | 245809518.4727 | 2192462367.5261 | 53.9599 | 1870671018.3239
July 2000 | 699.0703 | 720.691 | 5723 | 4000779155.21 | 3515.1786 | 8.826 | 2332957608.1348 | 3620.634 | 65 | 235192469.5379 | 2097765138.5969 | 52.4339 | 1903014016.6131
August 2000 | 709.2611 | 731.197 | 5723 | 4059101218.07 | 3729.1047 | 8.826 | 2474936318 | 3840.9778 | 65 | 249505770.079 | 2225430547.9209 | 54.8257 | 1833670670.1491
September 2000 | 672.7939 | 693.602 | 6094 | 4100006270.36 | 3398.6498 | 8.826 | 2255619645.6976 | 3500.6093 | 65 | 227395797.0604 | 2028223848.6373 | 49.4688 | 2071782421.7227
October 2000 | 622.8389 | 642.102 | 5969 | 3717725632.86 | 3498.6163 | 8.4337 | 2324305313.6327 | 3603.5748 | 65 | 234084327.0297 | 2090220986.603 | 56.2231 | 1627504646.257
November 2000 | 667.4987 | 688.143 | 5996 | 4002322265.16 | 3392.2364 | 8.826 | 2251363160.1319 | 3494.0034 | 66 | 230463361.9358 | 2020899798.1961 | 50.4932 | 1981422466.9639
December 2000 | 725.5969 | 748.038 | 5863 | 4254174390.18 | 3590.5824 | 8.826 | 2383001685.2387 | 3698.2999 | 65 | 240237563.3873 | 2142764121.8514 | 50.3685 | 2111410268.3286
January 2001 | 749.6247 | 772.809 | 5703 | 4275109835.19 | 3651.4832 | 8.826 | 2423420395.3155 | 3761.0277 | 65 | 244312295.0521 | 2179108100.2633 | 50.972 | 2096001734.9267
February 2001 | 653.1117 | 673.311 | 5681 | 3710327397.27 | 3547.2306 | 8.826 | 2354229914.8267 | 3653.6475 | 65 | 237336994.7218 | 2116892920.1049 | 57.0541 | 1593434477.1651
March 2001 | 612.1486 | 631.081 | 5871 | 3593924254.47 | 3429.1888 | 8.826 | 2275887802.8817 | 3532.0645 | 66 | 232973855.0089 | 2042913947.8728 | 56.8435 | 1551010306.5972
2000-2001 | 8133.1241 | 8384.664 | 5774.6667 | 46943278986.72 | 42287.8634 | 8.7933 | 28067995587.5115 | 43556.4993 | 65 | 2829358464.0303 | 25238637123.4811 | 53.9271 | 21704641863.2389
[10 empty] | Temperature | Feed water in kJkg | Feed Water Enthalpy in kcal/kg
[10 empty] | 65 | 271.97 | 64.9589
[10 empty] | 66 | 276.16 | 65.9597
[10 empty] | 67 | 280.34 | 66.9581
[10 empty] | 68 | 284.52 | 67.9564
[10 empty] | 64 | 267.79 | 63.9605

## Daily Report_01-02
INDIAN RAYON AND INDUSTRIES LTD.,
UNIT : JAYA SHREE TEXTILES
RISHRA, HOOGHLY
BOILER DAILY REPORT
MONTH -APRIL -2001
Particulars | 2001-04-01 | 2001-04-02 | 2001-04-03 | 2001-04-04 | 2001-04-05 | 2001-04-06 | 2001-04-07 | Total | 1 Week | 2001-04-08 | 2001-04-09 | 2001-04-10 | 2001-04-11 | 2001-04-12 | 2001-04-13 | 2001-04-14 | Total | 2 Week | 2001-04-15 | 2001-04-16 | 2001-04-17 | 2001-04-18 | 2001-04-19 | 2001-04-20 | 2001-04-21 | Total | 3 Week | 2001-04-22 | 2001-04-23 | 2001-04-24 | 2001-04-25 | 2001-04-26 | 2001-04-27 | 2001-04-28 | 2001-04-29 | 2001-04-30 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 110477.6 | 124366.7 | 120359.7 | 125373 | 115362.9 | 111364.2 | 121366.5 | 828670.6 | 828670.6 | 110449 | 124338.1 | 120331.1 | 125344.4 | 115334.3 | 111335.6 | 121337.9 | 828470.4 | 828470.4 | 110606.2 | 124495.3 | 120488.3 | 125501.6 | 115491.5 | 111492.8 | 121495.1 | 829570.8 | 829570.8 | 88048.4 | 88937.5 | 89930.5 | 90943.8 | 91933.7 | 92935 | 93937.3 | 94974.5 | 95930 | 827570.7 | 827570.7 | 3314282.5
Coal Audited (kgs) | 19629 | 19526 | 19521 | 19531 | 19634 | 19515 | 19506 | 136862 | 136862 | 19188 | 19085 | 19079 | 19090 | 19190 | 19074 | 19063 | 133769 | 133769 | 19465 | 19362 | 19357 | 19367 | 19470 | 19354 | 19342 | 135717 | 135717 | 15297 | 15194 | 15189 | 15199 | 15302 | 15184 | 15171 | 15291 | 15150 | 136977 | 136977 | 543325
Actual Coal Consumed (Kgs) | 19040.13 | 18940.22 | 18935.37 | 18945.07 | 19044.98 | 18929.55 | 18920.82 | 132756.14 | 132756.14 | 18612.36 | 18512.45 | 18506.63 | 18517.3 | 18614.3 | 18501.78 | 18491.11 | 129755.93 | 129755.93 | 18881.05 | 18781.14 | 18776.29 | 18785.99 | 18885.9 | 18773.38 | 18761.74 | 131645.49 | 131645.49 | 14838.09 | 14738.18 | 14733.33 | 14743.03 | 14842.94 | 14728.48 | 14715.87 | 14832.27 | 14695.5 | 132867.69 | 132867.69 | 527025.25
Feed Water Temp. deg. C | 62 | 65 | 63 | 62 | 64 | 63 | 62 | 63 | 63 | 66 | 69 | 67 | 66 | 68 | 67 | 66 | 67 | 67 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 113791.928 | 128097.701 | 123970.491 | 129134.19 | 118823.787 | 114705.126 | 125007.495 | 853530.718 | 853530.718 | 113762.47 | 128068.243 | 123941.033 | 129104.732 | 118794.329 | 114675.668 | 124978.037 | 853324.512 | 853324.512 | 113924.386 | 128230.159 | 124102.949 | 129266.648 | 118956.245 | 114837.584 | 125139.953 | 854457.924 | 854457.924 | 90689.852 | 91605.625 | 92628.415 | 93672.114 | 94691.711 | 95723.05 | 96755.419 | 97823.735 | 98807.9 | 852397.821 | 852397.821 | 3413710.975
MONTH -MAY -2001
Particulars | 2001-05-02 | 2001-05-03 | 2001-05-04 | 2001-05-05 | 2001-05-06 | 2001-05-07 | 2001-05-08 | Total | 1 Week | 2001-05-09 | 2001-05-10 | 2001-05-11 | 2001-05-12 | 2001-05-13 | 2001-05-14 | 2001-05-15 | Total | 2 Week | 2001-05-16 | 2001-05-17 | 2001-05-18 | 2001-05-19 | 2001-05-20 | 2001-05-21 | 2001-05-22 | Total | 3 Week | 2001-05-23 | 2001-05-24 | 2001-05-25 | 2001-05-26 | 2001-05-27 | 2001-05-28 | 2001-05-29 | 2001-05-30 | 2001-05-31 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 109901.8 | 123790.9 | 119783.9 | 124797.2 | 114787.1 | 110788.4 | 120790.7 | 824640 | 824640 | 109964.7 | 123853.8 | 119846.8 | 124860.1 | 114850 | 110851.3 | 120853.5 | 825080.2 | 825080.2 | 110377.5 | 124266.6 | 120259.6 | 125272.9 | 115262.8 | 111264.2 | 121266.4 | 827970 | 827970 | 87401.7 | 88290.8 | 89283.8 | 90297.1 | 91287 | 92288.3 | 93290.6 | 94321.2 | 95289.5 | 821750 | 821750 | 3299440.2
Coal Audited (kgs) | 20242 | 20139 | 20134 | 20144 | 20248 | 20130 | 20119 | 141156 | 141156 | 20545 | 20442 | 20437 | 20447 | 20553 | 20432 | 20422 | 143278 | 143278 | 20100 | 19997 | 19992 | 20002 | 20105 | 19985 | 19976 | 140157 | 140157 | 16108 | 16005 | 16000 | 16010 | 16113 | 15995 | 15987 | 16097 | 15963 | 144278 | 144278 | 568869
Actual Coal Consumed (Kgs) | 19634.74 | 19534.83 | 19529.98 | 19539.68 | 19640.56 | 19526.1 | 19515.43 | 136921.32 | 136921.32 | 19928.65 | 19828.74 | 19823.89 | 19833.59 | 19936.41 | 19819.04 | 19809.34 | 138979.66 | 138979.66 | 19497 | 19397.09 | 19392.24 | 19401.94 | 19501.85 | 19385.45 | 19376.72 | 135952.29 | 135952.29 | 15624.76 | 15524.85 | 15520 | 15529.7 | 15629.61 | 15515.15 | 15507.39 | 15614.09 | 15484.11 | 139949.66 | 139949.66 | 551802.93
Feed Water Temp. deg. C | 62 | 65 | 63 | 62 | 64 | 63 | 62 | 63 | 63 | 66 | 69 | 67 | 66 | 68 | 67 | 66 | 67 | 67 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 64 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.8325
Feed Water Consumed (Kg) | 113198.854 | 127504.627 | 123377.417 | 128541.116 | 118230.713 | 114112.052 | 124414.421 | 849379.2 | 849379.2 | 113263.641 | 127569.414 | 123442.204 | 128605.903 | 118295.5 | 114176.839 | 124479.105 | 849832.606 | 849832.606 | 113688.825 | 127994.598 | 123867.388 | 129031.087 | 118720.684 | 114602.126 | 124904.392 | 852809.1 | 852809.1 | 90023.751 | 90939.524 | 91962.314 | 93006.013 | 94025.61 | 95056.949 | 96089.318 | 97150.836 | 98148.185 | 846402.5 | 846402.5 | 3398423.406
MONTH -JUNE -2001
Particulars | 2001-06-01 | 2001-06-02 | 2001-06-03 | 2001-06-04 | 2001-06-05 | 2001-06-06 | 2001-06-07 | Total | 1 Week | 2001-06-08 | 2001-06-09 | 2001-06-10 | 2001-06-11 | 2001-06-12 | 2001-06-13 | 2001-06-14 | Total | 2 Week | 2001-06-15 | 2001-06-16 | 2001-06-17 | 2001-06-21 | 2001-06-22 | 2001-06-23 | 2001-06-24 | Total | 3 Week | 2001-06-25 | 2001-06-26 | 2001-06-27 | 2001-06-28 | 2001-06-29 | 2001-06-30 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 105296.7 | 119185.9 | 115178.8 | 120192.1 | 110182 | 106183.3 | 116185.6 | 792404.4 | 792404.4 | 105755.5 | 119644.7 | 115637.6 | 120650.9 | 110640.8 | 106642.1 | 116644.4 | 795616 | 795616 | 105125 | 119014.2 | 115007.1 | 120020.4 | 110010.3 | 106011.6 | 116013.9 | 791202.5 | 791202.5 | 128768.5 | 129653.7 | 130646.6 | 134659.9 | 135630.7 | 136650.2 | 796009.6 | 796009.6 | 3175232.5
Coal Audited (kgs) | 19298 | 19195 | 19189 | 19200 | 19303 | 19185 | 19174 | 134544 | 134544 | 19003 | 18900 | 18895 | 18906 | 19006 | 18890 | 18879 | 132479 | 132479 | 19593 | 19490 | 19485 | 19494 | 19600 | 19479 | 19469 | 136610 | 136610 | 22501 | 22398 | 22393 | 22401 | 22506 | 22343 | 134542 | 134542 | 538175
Actual Coal Consumed (Kgs) | 18719.06 | 18619.15 | 18613.33 | 18624 | 18723.91 | 18609.45 | 18598.78 | 130507.68 | 130507.68 | 18432.91 | 18333 | 18328.15 | 18338.82 | 18435.82 | 18323.3 | 18312.63 | 128504.63 | 128504.63 | 19005.21 | 18905.3 | 18900.45 | 18909.18 | 19012 | 18894.63 | 18884.93 | 132511.7 | 132511.7 | 21825.97 | 21726.06 | 21721.21 | 21728.97 | 21830.82 | 21672.71 | 130505.74 | 130505.74 | 522029.75
Feed Water Temp. deg. C | 62 | 65 | 63 | 62 | 64 | 63 | 62 | 63 | 63 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 65 | 68 | 66 | 65 | 67 | 66 | 65 | 66 | 66 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 62 | 64
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 108455.601 | 122761.477 | 118634.164 | 123797.863 | 113487.46 | 109368.799 | 119671.168 | 816176.532 | 816176.532 | 108928.165 | 123234.041 | 119106.728 | 124270.427 | 113960.024 | 109841.363 | 120143.732 | 819484.48 | 819484.48 | 108278.75 | 122584.626 | 118457.313 | 123621.012 | 113310.609 | 109191.948 | 119494.317 | 814938.575 | 814938.575 | 132631.555 | 133543.311 | 134565.998 | 138699.697 | 139699.621 | 140749.706 | 819889.888 | 819889.888 | 3270489.475
MONTH -JULY -2001
Particulars | 2001-07-01 | 2001-07-02 | 2001-07-03 | 2001-07-04 | 2001-07-05 | 2001-07-06 | 2001-07-07 | Total | 1 Week | 2001-07-08 | 2001-07-09 | 2001-07-10 | 2001-07-11 | 2001-07-12 | 2001-07-13 | 2001-07-14 | Total | 2 Week | 2001-07-15 | 2001-07-16 | 2001-07-17 | 2001-07-18 | 2001-07-19 | 2001-07-20 | 2001-07-21 | Total | 3 Week | 2001-07-22 | 2001-07-23 | 2001-07-24 | 2001-07-25 | 2001-07-26 | 2001-07-27 | 2001-07-28 | 2001-07-29 | 2001-07-30 | 2001-07-31 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 108301.8 | 122191 | 118183.9 | 123197.2 | 113187.1 | 109188.4 | 119190.6 | 813440 | 813440 | 108206.2 | 122095.4 | 118088.3 | 123101.6 | 113091.5 | 109092.8 | 119095.2 | 812771 | 812771 | 109349.7 | 123239 | 119231.9 | 124245.2 | 114235.1 | 110236.4 | 120238.7 | 820776 | 820776 | 77106.8 | 77996 | 78988.9 | 80002.2 | 81992.1 | 83993.4 | 81995.7 | 85032.9 | 85992.5 | 87006.5 | 820107 | 820107 | 3267094
Coal Audited (kgs) | 18108 | 18004 | 18000 | 18012 | 18113 | 17995 | 17985 | 126217 | 126217 | 19492 | 19389 | 19384 | 19393 | 19497 | 19379 | 19368 | 135902 | 135902 | 18462 | 18359 | 18354 | 18364 | 18470 | 18348 | 18338 | 128695 | 128695 | 16184 | 16080 | 16075 | 16086 | 16186 | 16070 | 16061 | 16163 | 16091 | 16064 | 161060 | 161060 | 551874
Actual Coal Consumed (Kgs) | 17564.76 | 17463.88 | 17460 | 17471.64 | 17569.61 | 17455.15 | 17445.45 | 122430.49 | 122430.49 | 18907.24 | 18807.33 | 18802.48 | 18811.21 | 18912.09 | 18797.63 | 18786.96 | 131824.94 | 131824.94 | 17908.14 | 17808.23 | 17803.38 | 17813.08 | 17915.9 | 17797.56 | 17787.86 | 124834.15 | 124834.15 | 15698.48 | 15597.6 | 15592.75 | 15603.42 | 15700.42 | 15587.9 | 15579.17 | 15678.11 | 15608.27 | 15582.08 | 156228.2 | 156228.2 | 535317.78
Feed Water Temp. deg. C | 62 | 65 | 63 | 62 | 64 | 63 | 62 | 63 | 63 | 66 | 69 | 67 | 66 | 68 | 67 | 66 | 67 | 67 | 63 | 66 | 64 | 63 | 65 | 64 | 63 | 64 | 64 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 111550.854 | 125856.73 | 121729.417 | 126893.116 | 116582.713 | 112464.052 | 122766.318 | 837843.2 | 837843.2 | 111452.386 | 125758.262 | 121630.949 | 126794.648 | 116484.245 | 112365.584 | 122668.056 | 837154.13 | 837154.13 | 112630.191 | 126936.17 | 122808.857 | 127972.556 | 117662.153 | 113543.492 | 123845.861 | 845399.28 | 845399.28 | 79420.004 | 80335.88 | 81358.567 | 82402.266 | 84451.863 | 86513.202 | 84455.571 | 87583.887 | 88572.275 | 89616.695 | 844710.21 | 844710.21 | 3365106.82
MONTH -AUGUST -2001
Particulars | 2001-08-01 | 2001-08-02 | 2001-08-03 | 2001-08-04 | 2001-08-05 | 2001-08-06 | 2001-08-07 | Total | 1 Week | 2001-08-08 | 2001-08-09 | 2001-08-10 | 2001-08-11 | 2001-08-12 | 2001-08-13 | 2001-08-14 | Total | 2 Week | 2001-08-15 | 2001-08-16 | 2001-08-17 | 2001-08-18 | 2001-08-19 | 2001-08-20 | 2001-08-21 | Total | 3 Week | 2001-08-22 | 2001-08-23 | 2001-08-24 | 2001-08-25 | 2001-08-26 | 2001-08-27 | 2001-08-28 | 2001-08-29 | 2001-08-30 | 2001-08-31 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 108209.5 | 122098.7 | 118091.6 | 123104.9 | 113094.8 | 109096.1 | 119098.4 | 812794 | 812794 | 108782.1 | 122671.3 | 118664.2 | 123677.5 | 113667.4 | 109668.5 | 119671 | 816802 | 816802 | 108067.4 | 121956.6 | 117949.5 | 122962.8 | 112952.6 | 108954 | 118956 | 811798.9 | 811798.9 | 76875.9 | 77765.1 | 78758 | 79771.3 | 81761.2 | 83762.5 | 81764.8 | 84802 | 85762.6 | 86774.6 | 817798 | 817798 | 3259192.9
Coal Audited (kgs) | 11075 | 25390 | 21259 | 26427 | 16106 | 11985 | 22297 | 134539 | 134539 | 11366 | 25690 | 21554 | 26721 | 16402 | 12279 | 22592 | 136604 | 136604 | 11204 | 25523 | 21392 | 26559 | 16240 | 12118 | 22430 | 135466 | 135466 | 8513 | 9430 | 10454 | 11498 | 13549 | 15613 | 13554 | 16685 | 17675 | 18715 | 135686 | 135686 | 542295
Actual Coal Consumed (Kgs) | 10742.75 | 24628.3 | 20621.23 | 25634.19 | 15622.82 | 11625.45 | 21628.09 | 130502.83 | 130502.83 | 11025.02 | 24919.3 | 20907.38 | 25919.37 | 15909.94 | 11910.63 | 21914.24 | 132505.88 | 132505.88 | 10867.88 | 24757.31 | 20750.24 | 25762.23 | 15752.8 | 11754.46 | 21757.1 | 131402.02 | 131402.02 | 8257.61 | 9147.1 | 10140.38 | 11153.06 | 13142.53 | 15144.61 | 13147.38 | 16184.45 | 17144.75 | 18153.55 | 131615.42 | 131615.42 | 526026.15
Feed Water Temp. deg. C | 66 | 69 | 67 | 66 | 68 | 67 | 66 | 67 | 67 | 63 | 66 | 64 | 63 | 65 | 64 | 63 | 64 | 64 | 62 | 65 | 63 | 62 | 64 | 63 | 62 | 63 | 63 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 66 | 65
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 111455.785 | 125761.661 | 121634.348 | 126798.047 | 116487.644 | 112368.983 | 122671.352 | 837177.82 | 837177.82 | 112045.563 | 126351.439 | 122224.126 | 127387.825 | 117077.422 | 112958.555 | 123261.13 | 841306.06 | 841306.06 | 111309.422 | 125615.298 | 121487.985 | 126651.684 | 116341.178 | 112222.62 | 122524.68 | 836152.867 | 836152.867 | 79182.177 | 80098.053 | 81120.74 | 82164.439 | 84214.036 | 86275.375 | 84217.744 | 87346.06 | 88335.478 | 89377.838 | 842331.94 | 842331.94 | 3356968.687
MONTH -SEPTEMBER -2001
Particulars | 2001-09-01 | 2001-09-02 | 2001-09-03 | 2001-09-04 | 2001-09-05 | 2001-09-06 | 2001-09-07 | Total | 1 Week | 2001-09-08 | 2001-09-09 | 2001-09-10 | 2001-09-11 | 2001-09-12 | 2001-09-13 | 2001-09-14 | Total | 2 Week | 2001-09-15 | 2001-09-16 | 2001-09-17 | 2001-09-18 | 2001-09-19 | 2001-09-20 | 2001-09-21 | Total | 3 Week | 2001-09-22 | 2001-09-23 | 2001-09-24 | 2001-09-25 | 2001-09-26 | 2001-09-27 | 2001-09-28 | 2001-09-29 | 2001-09-30 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 97921.1 | 111806.3 | 107799.2 | 112808.5 | 102802.4 | 98806.4 | 108808.6 | 740752.5 | 740752.5 | 98765 | 112650.2 | 108643.1 | 113652.4 | 103646.3 | 99644.5 | 109652.5 | 746654 | 746654 | 99936.4 | 113821.6 | 109814.5 | 114823.8 | 104817.7 | 100819 | 110821 | 754854 | 754854 | 80624.5 | 81513.7 | 82506.6 | 83519 | 84509.8 | 85511.1 | 86513.4 | 87545.6 | 88512.3 | 760756 | 760756 | 3003016.5
Coal Audited (kgs) | 16769 | 16666 | 16661 | 16671 | 16774 | 16653 | 16645 | 116839 | 116839 | 18109 | 18006 | 18001 | 18012 | 18115 | 17996 | 17986 | 126225 | 126225 | 18463 | 18360 | 18355 | 18365 | 18470 | 18349 | 18339 | 128701 | 128701 | 15420 | 15316 | 15311 | 15322 | 15429 | 15307 | 15296 | 15410 | 15274 | 138085 | 138085 | 509850
Actual Coal Consumed (Kgs) | 16265.93 | 16166.02 | 16161.17 | 16170.87 | 16270.78 | 16153.41 | 16145.65 | 113333.83 | 113333.83 | 17565.73 | 17465.82 | 17460.97 | 17471.64 | 17571.55 | 17456.12 | 17446.42 | 122438.25 | 122438.25 | 17909.11 | 17809.2 | 17804.35 | 17814.05 | 17915.9 | 17798.53 | 17788.83 | 124839.97 | 124839.97 | 14957.4 | 14856.52 | 14851.67 | 14862.34 | 14966.13 | 14847.79 | 14837.12 | 14947.7 | 14815.78 | 133942.45 | 133942.45 | 494554.5
Feed Water Temp. deg. C | 68 | 71 | 72 | 69 | 73 | 72 | 72 | 71 | 71 | 73 | 76 | 74 | 73 | 75 | 74 | 73 | 74 | 74 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.8325
Feed Water Consumed (Kg) | 100858.733 | 115160.489 | 111033.176 | 116192.755 | 105886.472 | 101770.592 | 112072.858 | 762975.075 | 762975.075 | 101727.95 | 116029.706 | 111902.393 | 117061.972 | 106755.689 | 102633.835 | 112942.075 | 769053.62 | 769053.62 | 102934.492 | 117236.248 | 113108.935 | 118268.514 | 107962.231 | 103843.57 | 114145.63 | 777499.62 | 777499.62 | 83043.235 | 83959.111 | 84981.798 | 86024.57 | 87045.094 | 88076.433 | 89108.802 | 90171.968 | 91167.669 | 783578.68 | 783578.68 | 3093106.995
MONTH -OCTOBER -2001
Particulars | 2001-10-01 | 2001-10-02 | 2001-10-03 | 2001-10-04 | 2001-10-05 | 2001-10-06 | 2001-10-07 | Total | 1 Week | 2001-10-08 | 2001-10-09 | 2001-10-10 | 2001-10-11 | 2001-10-12 | 2001-10-13 | 2001-10-14 | Total | 2 Week | 2001-10-15 | 2001-10-16 | 2001-10-17 | 2001-10-18 | 2001-10-19 | 2001-10-20 | 2001-10-21 | Total | 3 Week | 2001-10-22 | 2001-10-23 | 2001-10-24 | 2001-10-25 | 2001-10-26 | 2001-10-27 | 2001-10-28 | 2001-10-29 | 2001-10-30 | 2001-10-31 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 107895.1 | 121875.3 | 117870.2 | 122910.5 | 112858.4 | 108872.1 | 118880.6 | 811162.2 | 811162.2 | 109177.1 | 123153 | 119153.2 | 124192.5 | 114140.4 | 110154.2 | 120162.6 | 820133 | 820133 | 109471.1 | 123451.3 | 119446.2 | 124483.3 | 114435.2 | 110446.3 | 120458.6 | 822192 | 822192 | 78131.4 | 79111 | 80106 | 81147 | 83094.2 | 85107.5 | 83161.7 | 86096 | 87102.8 | 88106.4 | 831164 | 831164 | 3284651.2
Coal Audited (kgs) | 17492 | 17389 | 17384 | 17393 | 17497 | 17378 | 17368 | 121901 | 121901 | 18658 | 18555 | 18549 | 18560 | 18665 | 18544 | 18534 | 130065 | 130065 | 19282 | 19179 | 19174 | 19189 | 19286 | 19169 | 19159 | 134438 | 134438 | 14338 | 14235 | 14230 | 14240 | 14343 | 14225 | 14210 | 14318 | 14245 | 14220 | 142604 | 142604 | 529008
Actual Coal Consumed (Kgs) | 16967.24 | 16867.33 | 16862.48 | 16871.21 | 16972.09 | 16856.66 | 16846.96 | 118243.97 | 118243.97 | 18098.26 | 17998.35 | 17992.53 | 18003.2 | 18105.05 | 17987.68 | 17977.98 | 126163.05 | 126163.05 | 18703.54 | 18603.63 | 18598.78 | 18613.33 | 18707.42 | 18593.93 | 18584.23 | 130404.86 | 130404.86 | 13907.86 | 13807.95 | 13803.1 | 13812.8 | 13912.71 | 13798.25 | 13783.7 | 13888.46 | 13817.65 | 13793.4 | 138325.88 | 138325.88 | 513137.76
Feed Water Temp. deg. C | 72 | 72 | 73 | 72 | 71 | 70 | 72 | 71.7143 | 71.7143 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 70 | 73 | 71 | 73 | 72 | 71 | 73 | 71.8571 | 71.8571 | 72 | 75 | 74 | 73 | 74 | 73 | 75 | 72 | 73 | 73 | 73.4 | 73.4 | 72.2429
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 111131.953 | 125531.559 | 121406.306 | 126597.815 | 116244.152 | 112138.263 | 122447.018 | 835497.066 | 835497.066 | 112452.413 | 126847.59 | 122727.796 | 127918.275 | 117564.612 | 113458.826 | 123767.478 | 844736.99 | 844736.99 | 112755.233 | 127154.839 | 123029.586 | 128217.799 | 117868.256 | 113759.689 | 124072.358 | 846857.76 | 846857.76 | 80475.342 | 81484.33 | 82509.18 | 83581.41 | 85587.026 | 87660.725 | 85656.551 | 88678.88 | 89715.884 | 90749.592 | 856098.92 | 856098.92 | 3383190.736
MONTH -NOVEMBER -2001
Particulars | 2001-11-01 | 2001-11-02 | 2001-11-03 | 2001-11-04 | 2001-11-05 | 2001-11-06 | 2001-11-07 | Total | 1 Week | 2001-11-08 | 2001-11-09 | 2001-11-10 | 2001-11-11 | 2001-11-12 | 2001-11-13 | 2001-11-14 | Total | 2 Week | 2001-11-15 | 2001-11-16 | 2001-11-17 | 2001-11-18 | 2001-11-19 | 2001-11-20 | 2001-11-21 | Total | 3 Week | 2001-11-22 | 2001-11-23 | 2001-11-24 | 2001-11-25 | 2001-11-26 | 2001-11-27 | 2001-11-28 | 2001-11-29 | 2001-11-30 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 123017.1 | 136997.3 | 132992.2 | 138032.5 | 127980.9 | 123991.7 | 134001.5 | 917013.2 | 917013.2 | 124160.1 | 138140.1 | 134135.1 | 139175.1 | 129123.1 | 125137.1 | 135145.1 | 925015.7 | 925015.7 | 124731.7 | 138711.7 | 134706.7 | 139746.7 | 129694.5 | 125707 | 135718.7 | 929017 | 929017 | 100128.1 | 101108.1 | 102103.1 | 103143.1 | 104091.1 | 105105.1 | 106114.1 | 107138.1 | 108088.1 | 937018.9 | 937018.9 | 3708064.8
Coal Audited (kgs) | 17442 | 17339 | 17334 | 17346 | 17447 | 17329 | 17319 | 121556 | 121556 | 18753 | 18649 | 18644 | 18655 | 18761 | 18639 | 18629 | 130730 | 130730 | 19077 | 18974 | 18969 | 18979 | 19086 | 18964 | 18954 | 133003 | 133003 | 15875 | 15772 | 15767 | 15778 | 15880 | 15762 | 15744 | 15866 | 15730 | 142174 | 142174 | 527463
Actual Coal Consumed (Kgs) | 16918.74 | 16818.83 | 16813.98 | 16825.62 | 16923.59 | 16809.13 | 16799.43 | 117909.32 | 117909.32 | 18190.41 | 18089.53 | 18084.68 | 18095.35 | 18198.17 | 18079.83 | 18070.13 | 126808.1 | 126808.1 | 18504.69 | 18404.78 | 18399.93 | 18409.63 | 18513.42 | 18395.08 | 18385.38 | 129012.91 | 129012.91 | 15398.75 | 15298.84 | 15293.99 | 15304.66 | 15403.6 | 15289.14 | 15271.68 | 15390.02 | 15258.1 | 137908.78 | 137908.78 | 511639.11
Feed Water Temp. deg. C | 74 | 77 | 75 | 74 | 76 | 75 | 74 | 75 | 75 | 70 | 73 | 71 | 70 | 72 | 71 | 70 | 71 | 71 | 71 | 74 | 72 | 71 | 73 | 72 | 71 | 72 | 72 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.8325
Feed Water Consumed (Kg) | 126707.613 | 141107.219 | 136981.966 | 142173.475 | 131820.327 | 127711.451 | 138021.545 | 944523.596 | 944523.596 | 127884.903 | 142284.303 | 138159.153 | 143350.353 | 132996.793 | 128891.213 | 139199.453 | 952766.171 | 952766.171 | 128473.651 | 142873.051 | 138747.901 | 143939.101 | 133585.335 | 129478.21 | 139790.261 | 956887.51 | 956887.51 | 103131.943 | 104141.343 | 105166.193 | 106237.393 | 107213.833 | 108258.253 | 109297.523 | 110352.243 | 111330.743 | 965129.467 | 965129.467 | 3819306.744
MONTH -DECEMBER -2001
Particulars | 2001-12-01 | 2001-12-02 | 2001-12-03 | 2001-12-04 | 2001-12-05 | 2001-12-06 | 2001-12-07 | Total | 1 Week | 2001-12-08 | 2001-12-09 | 2001-12-10 | 2001-12-11 | 2001-12-12 | 2001-12-13 | 2001-12-14 | Total | 2 Week | 2001-12-15 | 2001-12-16 | 2001-12-17 | 2001-12-18 | 2001-12-19 | 2001-12-20 | 2001-12-21 | Total | 3 Week | 2001-12-22 | 2001-12-23 | 2001-12-24 | 2001-12-25 | 2001-12-26 | 2001-12-27 | 2001-12-28 | 2001-12-29 | 2001-12-30 | 2001-12-31 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 140998.7 | 154997.4 | 151002.6 | 155972.9 | 146002.9 | 141982.9 | 151992.6 | 1042950 | 1042950 | 143710 | 157710 | 153710 | 158710 | 148710 | 144710 | 154710 | 1061970 | 1061970 | 143997.3 | 157982.3 | 153977.8 | 159122.2 | 148998.6 | 144992.9 | 154878.9 | 1063950 | 1063950 | 103297 | 104297 | 105297 | 106297 | 108297 | 110297 | 108297 | 111297 | 112297 | 113297 | 1082970 | 1082970 | 4251840
Coal Audited (kgs) | 22420 | 22316 | 22311 | 22322 | 22426 | 22306 | 22296 | 156397 | 156397 | 21109 | 21006 | 21002 | 21011 | 21112 | 20996 | 20986 | 147222 | 147222 | 23760 | 23657 | 23652 | 23663 | 23764 | 23646 | 23636 | 165778 | 165778 | 15738 | 15635 | 15630 | 15641 | 15743 | 15625 | 15614 | 15712 | 15645 | 15620 | 156603 | 156603 | 626000
Actual Coal Consumed (Kgs) | 21747.4 | 21646.52 | 21641.67 | 21652.34 | 21753.22 | 21636.82 | 21627.12 | 151705.09 | 151705.09 | 20475.73 | 20375.82 | 20371.94 | 20380.67 | 20478.64 | 20366.12 | 20356.42 | 142805.34 | 142805.34 | 23047.2 | 22947.29 | 22942.44 | 22953.11 | 23051.08 | 22936.62 | 22926.92 | 160804.66 | 160804.66 | 15265.86 | 15165.95 | 15161.1 | 15171.77 | 15270.71 | 15156.25 | 15145.58 | 15240.64 | 15175.65 | 15151.4 | 151904.91 | 151904.91 | 607220
Feed Water Temp. deg. C | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 145228.661 | 159647.322 | 155532.678 | 160652.087 | 150382.987 | 146242.387 | 156552.378 | 1074238.5 | 1074238.5 | 148021.3 | 162441.3 | 158321.3 | 163471.3 | 153171.3 | 149051.3 | 159351.3 | 1093829.1 | 1093829.1 | 148317.219 | 162721.769 | 158597.134 | 163895.866 | 153468.558 | 149342.687 | 159525.267 | 1095868.5 | 1095868.5 | 106395.91 | 107425.91 | 108455.91 | 109485.91 | 111545.91 | 113605.91 | 111545.91 | 114635.91 | 115665.91 | 116695.91 | 1115459.1 | 1115459.1 | 4379395.2
MONTH -JANUARY -2002
Particulars | 2002-01-01 | 2002-01-02 | 2002-01-03 | 2002-01-04 | 2002-01-05 | 2002-01-06 | 2002-01-07 | Total | 1week | 2002-01-08 | 2002-01-09 | 2002-01-10 | 2002-01-11 | 2002-01-12 | 2002-01-13 | 2002-01-14 | Total | 2 week | 2002-01-15 | 2002-01-16 | 2002-01-17 | 2002-01-18 | 2002-01-19 | 2002-01-20 | 2002-01-21 | Total | 3 week | 2002-01-22 | 2002-01-23 | 2002-01-24 | 2002-01-25 | 2002-01-26 | 2002-01-27 | 2002-01-28 | 2002-01-29 | 2002-01-30 | 2002-01-31 | Total | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 150808.6 | 164810 | 160806.1 | 165801.3 | 155800.2 | 151805 | 161828.8 | 1111660 | 1111660 | 152175.1 | 166192.3 | 162178 | 167194.5 | 157195.6 | 153196.7 | 163197.8 | 1121330 | 1121330 | 152570.1 | 166575.3 | 162581.9 | 167565.5 | 157564 | 153562.6 | 163570.6 | 1123990 | 1123990 | 108376 | 109376 | 110378 | 111340 | 113360 | 115376 | 113378 | 116366 | 117348 | 118362 | 1133660 | 1133660 | 4490640
Coal Audited (kgs) | 22347 | 22244 | 22239 | 22251 | 22352 | 22233 | 22224 | 155890 | 155890 | 23658 | 23555 | 23549 | 23560 | 23665 | 23544 | 23534 | 165065 | 165065 | 23982 | 23879 | 23874 | 23885 | 23987 | 23869 | 23859 | 167335 | 167335 | 17729 | 17626 | 17621 | 17631 | 17734 | 17615 | 17605 | 17703 | 17636 | 17610 | 176510 | 176510 | 664800
Actual Coal Consumed (Kgs) | 21676.59 | 21576.68 | 21571.83 | 21583.47 | 21681.44 | 21566.01 | 21557.28 | 151213.3 | 151213.3 | 22948.26 | 22848.35 | 22842.53 | 22853.2 | 22955.05 | 22837.68 | 22827.98 | 160113.05 | 160113.05 | 23262.54 | 23162.63 | 23157.78 | 23168.45 | 23267.39 | 23152.93 | 23143.23 | 162314.95 | 162314.95 | 17197.13 | 17097.22 | 17092.37 | 17102.07 | 17201.98 | 17086.55 | 17076.85 | 17171.91 | 17106.92 | 17081.7 | 171214.7 | 171214.7 | 644856
Feed Water Temp. deg. C | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 155332.858 | 169754.3 | 165630.283 | 170775.339 | 160474.206 | 156359.15 | 166683.664 | 1145009.8 | 1145009.8 | 156740.353 | 171178.069 | 167043.34 | 172210.335 | 161911.468 | 157792.601 | 168093.734 | 1154969.9 | 1154969.9 | 157147.203 | 171572.559 | 167459.357 | 172592.465 | 162290.92 | 158169.478 | 168477.718 | 1157709.7 | 1157709.7 | 111627.28 | 112657.28 | 113689.34 | 114680.2 | 116760.8 | 118837.28 | 116779.34 | 119856.98 | 120868.44 | 121912.86 | 1167669.8 | 1167669.8 | 4625359.2
MONTH -FEBRUARY -2002
Particulars | 2002-02-01 | 2002-02-02 | 2002-02-03 | 2002-02-04 | 2002-02-05 | 2002-02-06 | 2002-02-07 | Total | 1 Week | 2002-02-08 | 2002-02-09 | 2002-02-10 | 2002-02-11 | 2002-02-12 | 2002-02-13 | 2002-02-14 | Total | 2 Week | 2002-02-15 | 2002-02-16 | 2002-02-17 | 2002-02-18 | 2002-02-19 | 2002-02-20 | 2002-02-21 | Total | 3 Week | 2002-02-22 | 2002-02-23 | 2002-02-24 | 2002-02-25 | 2002-02-26 | 2002-02-27 | 2002-02-28 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 141131.1 | 155143.3 | 151129.2 | 156137.5 | 146142.4 | 142120 | 152114.5 | 1043918 | 1043918 | 142675.1 | 156674.3 | 152681 | 157680.6 | 147660.9 | 143668.1 | 153677 | 1054717 | 1054717 | 142422.1 | 156415.3 | 152420.5 | 157415.7 | 147410.6 | 143417 | 153417.8 | 1052919 | 1052919 | 143960.1 | 157959.4 | 153958.2 | 158961 | 148950.8 | 144964 | 154962.5 | 1063716 | 1063716 | 4215270
Coal Audited (kgs) | 22205 | 22102 | 22097 | 22106 | 22211 | 22092 | 22081 | 154894 | 154894 | 22369 | 22266 | 22261 | 22271 | 22371 | 22256 | 22245 | 156039 | 156039 | 22336 | 22233 | 22228 | 22238 | 22342 | 22223 | 22212 | 155812 | 155812 | 22499 | 22396 | 22391 | 22403 | 22505 | 22386 | 22375 | 156955 | 156955 | 623700
Actual Coal Consumed (Kgs) | 21538.85 | 21438.94 | 21434.09 | 21442.82 | 21544.67 | 21429.24 | 21418.57 | 150247.18 | 150247.18 | 21697.93 | 21598.02 | 21593.17 | 21602.87 | 21699.87 | 21588.32 | 21577.65 | 151357.83 | 151357.83 | 21665.92 | 21566.01 | 21561.16 | 21570.86 | 21671.74 | 21556.31 | 21545.64 | 151137.64 | 151137.64 | 21824.03 | 21724.12 | 21719.27 | 21730.91 | 21829.85 | 21714.42 | 21703.75 | 152246.35 | 152246.35 | 604989
Feed Water Temp. deg. C | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 71 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 71.5 | 74.5 | 72.5 | 72.5 | 73.5 | 72.5 | 74.5 | 73.0714 | 73.0714 | 73.0179
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.83
Feed Water Consumed (Kg) | 145365.033 | 159797.599 | 155663.076 | 160821.625 | 150526.672 | 146383.6 | 156677.935 | 1075235.54 | 1075235.54 | 146955.353 | 161374.529 | 157261.43 | 162411.018 | 152090.727 | 147978.143 | 158287.31 | 1086358.51 | 1086358.51 | 146694.763 | 161107.759 | 156993.115 | 162138.171 | 151832.918 | 147719.51 | 158020.334 | 1084506.57 | 1084506.57 | 148278.903 | 162698.182 | 158576.946 | 163729.83 | 153419.324 | 149312.92 | 159611.375 | 1095627.48 | 1095627.48 | 4341728.1
MONTH -MARCH -2002
Particulars | 2002-03-01 | 2002-03-02 | 2002-03-03 | 2002-03-04 | 2002-03-05 | 2002-03-06 | 2002-03-07 | Total | 1 Week | 2002-03-08 | 2002-03-09 | 2002-03-10 | 2002-03-11 | 2002-03-12 | 2002-03-13 | 2002-03-14 | Total | 2 Week | 2002-03-15 | 2002-03-16 | 2002-03-17 | 2002-03-18 | 2002-03-19 | 2002-03-20 | 2002-03-21 | Total | 3 Week | 2002-03-22 | 2002-03-23 | 2002-03-24 | 2002-03-25 | 2002-03-26 | 2002-03-27 | 2002-03-28 | 2002-03-29 | 2002-03-30 | 2002-03-31 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 156622.5 | 170622.4 | 166622.5 | 171623 | 161622.5 | 157621.4 | 167623.1 | 1152357.4 | 1152357.4 | 157893.1 | 171895.3 | 167884.2 | 172889.4 | 162891.5 | 158895.7 | 168895.8 | 1161245 | 1161245 | 158211.1 | 172212.3 | 168203.5 | 173212.2 | 163208.5 | 159212.6 | 169206.8 | 1163467 | 1163467 | 112206.1 | 113210.3 | 114212.2 | 115200.5 | 117183.4 | 119208.6 | 117215.8 | 120205.7 | 121205.3 | 122205.1 | 1172053 | 1172053 | 4649122.4
Coal Audited (kgs) | 24476 | 24373 | 24368 | 24378 | 24479 | 24363 | 24353 | 170790 | 170790 | 24672 | 24569 | 24564 | 24575 | 24677 | 24559 | 24548 | 172164 | 172164 | 24607 | 24504 | 24499 | 24509 | 24609 | 24494 | 24484 | 171706 | 171706 | 17386 | 17282 | 17277 | 17288 | 17391 | 17272 | 17262 | 17362 | 17293 | 17267 | 173080 | 173080 | 687740
Actual Coal Consumed (Kgs) | 23741.72 | 23641.81 | 23636.96 | 23646.66 | 23744.63 | 23632.11 | 23622.41 | 165666.3 | 165666.3 | 23931.84 | 23831.93 | 23827.08 | 23837.75 | 23936.69 | 23822.23 | 23811.56 | 166999.08 | 166999.08 | 23868.79 | 23768.88 | 23764.03 | 23773.73 | 23870.73 | 23759.18 | 23749.48 | 166554.82 | 166554.82 | 16864.42 | 16763.54 | 16758.69 | 16769.36 | 16869.27 | 16753.84 | 16744.14 | 16841.14 | 16774.21 | 16748.99 | 167887.6 | 167887.6 | 667107.8
Feed Water Temp. deg. C | 70 | 73 | 71 | 71 | 72 | 71 | 69 | 71 | 71 | 71 | 74 | 72 | 72 | 73 | 72 | 70 | 72 | 72 | 74 | 77 | 75 | 75 | 76 | 75 | 73 | 75 | 75 | 73 | 76 | 75 | 74 | 75 | 72 | 76 | 73 | 72 | 74 | 74 | 74 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.8325
Feed Water Consumed (Kg) | 161590 | 175741.072 | 171621.175 | 176771.69 | 166471.175 | 162350.042 | 172651.793 | 1186928.122 | 1186928.122 | 162629.893 | 177052.159 | 172920.726 | 178076.082 | 167778.245 | 163662.571 | 173962.674 | 1196082.35 | 1196082.35 | 162957.433 | 177378.669 | 173249.605 | 178408.566 | 168104.755 | 163988.978 | 174283.004 | 1198371.01 | 1198371.01 | 115572.283 | 116606.609 | 117638.566 | 118656.515 | 120698.902 | 122784.858 | 120732.274 | 123811.871 | 124841.459 | 125871.253 | 1207214.59 | 1207214.59 | 4788596.072

## CER Estimation_01-02
Monitored Parameters for the year 2001-2002
Months | Quantity of Coal Used | Coal-Audited | Gross Calorific Value of Coal | Heat Energy Input | Steam Load | Steam Pressure | Steam Pressure | Steam Enthalpy | Feed water Load | Feed Water Temerature | Feed Water Enthalpy | Number of Truck Trips
Units | (tons) | (tons) | (kCal/kg) | (kCal) | (tons) | (Bar) | (kg/cm2) | (kCal) | (tons) | (°C) | (kCal)
April 2001 | 527.0253 | 543.325 | 5882 | 3099962520.5 | 3314.2825 | 8.83 | 9 | 2199626663.033 | 3413.711 | 65 | 221750976.1584 | 60 | Temperature | Feed Water Enthalpy
May 2001 | 551.8029 | 568.869 | 5731 | 3162382591.83 | 3299.4402 | 8.8325 | 9 | 2189776109.0079 | 3398.4234 | 65 | 220757912.1956 | 81 | (0C) | (kJ/kg)
June 2001 | 522.0298 | 538.175 | 5828 | 3042389383 | 3175.2325 | 8.83 | 9 | 2107341805.754 | 3270.4895 | 64 | 209182284.5315 | 54 | 64 | 267.79
July 2001 | 535.3178 | 551.874 | 5927 | 3172828482.06 | 3267.094 | 8.83 | 9 | 2168308547.3357 | 3365.1068 | 65 | 218593702.7702 | 0 | 65 | 271.97
August 2001 | 526.0262 | 542.295 | 5723 | 3010447656.45 | 3259.1929 | 8.83 | 9 | 2163064736.5781 | 3356.9687 | 65 | 218065058.4444 | 82 | 66 | 276.16
September 2001 | 494.5545 | 509.85 | 5905 | 2920344322.5 | 3003.0165 | 8.8325 | 9 | 1993045301.0352 | 3093.107 | 72 | 222571022.6286 | 71 | 67 | 280.34
October 2001 | 513.1378 | 529.008 | 5586 | 2866387527.36 | 3284.6512 | 8.83 | 9 | 2179960929.1856 | 3383.1907 | 72.2429 | 243444608.6335 | 8 | 68 | 284.52
November 2001 | 511.6391 | 527.463 | 5777 | 2955739138.47 | 3708.0648 | 8.8325 | 9 | 2460972533.9751 | 3819.3067 | 73 | 278648479.6253 | 76 | 72 | 301.27
December 2001 | 607.22 | 626 | 5719 | 3472691180 | 4251.84 | 8.83 | 9 | 2821865858.1308 | 4379.3952 | 74 | 323894082.0741 | 0 | 73 | 305.46
January 2002 | 644.856 | 664.8 | 5840 | 3765959040 | 4490.64 | 8.83 | 9 | 2980352905.3672 | 4625.3592 | 74 | 342085243.2653 | 0 | 74 | 309.65
February 2002 | 604.989 | 623.7 | 5699 | 3447832311 | 4215.27 | 8.83 | 9 | 2797595040.2186 | 4341.7281 | 73.0179 | 316763228.2775 | 32
March 2002 | 667.1078 | 687.74 | 5621 | 3749812943.8 | 4649.1224 | 8.83 | 9 | 3085534679.2991 | 4788.5961 | 73 | 349365763.0665 | 78
2001-2002 | 6705.706 | 6913.099 | 5769.8333 | 38666777096.97 | 43917.847 | 8.8306 | 9 | 29147445108.9203 | 45235.3824 | 69.6051 | 3165122361.6709 | 542
Computation of Emission Reductions for the year 2001-2002
Months | Output Enthalpy | Baseline Boiler Efficiency | Baseline Technical Losses | Boiler Efficiency | Technical Losses | Reduction in Losses | Coal Reduction | Fixed Carbon Content (C%) in Coal | Emission Co-efficienct of Coal | Emission Reductions
| (kCal) | (%) | (kCal) | (%) | (kCal) | (kCal) | (kgs) | ('%) | (kgCO2/kCal) | (tons)
April 2001 | 1977875686.8746 | 53.9271 | 1689806040.1953 | 63.8032 | 1122086833.6254 | 567719206.5699 | 96518.0562 | 0.53945 | 0.00033628 | 190.9111
May 2001 | 1969018196.8123 | 53.9271 | 1682238607.9712 | 62.2638 | 1193364395.0177 | 488874212.9535 | 85303.4746 | 0.535 | 0.00034229 | 167.337
June 2001 | 1898159521.2225 | 53.9271 | 1621700213.7706 | 62.3904 | 1144229861.7775 | 477470351.9931 | 81926.965 | 0.55537 | 0.00034941 | 166.834
July 2001 | 1949714844.5656 | 53.9271 | 1665746711.4182 | 61.4504 | 1223113637.4944 | 442633073.9238 | 74680.7953 | 0.5487 | 0.00033945 | 150.2503
August 2001 | 1944999678.1337 | 53.9271 | 1661718290.0316 | 64.6083 | 1065447978.3163 | 596270311.7154 | 104188.4172 | 0.53335 | 0.00034171 | 203.7526
September 2001 | 1770474278.4066 | 53.9271 | 1512611813.5308 | 60.6255 | 1149870044.0935 | 362741769.4374 | 61429.5969 | 0.5443 | 0.00033798 | 122.5991
October 2001 | 1936516320.5521 | 53.9271 | 1654470499.3956 | 67.5595 | 929871206.8079 | 724599292.5877 | 129717.0234 | 0.5046 | 0.00033122 | 240.0024
November 2001 | 2182324054.3498 | 53.9271 | 1864477324.4223 | 73.8334 | 773415084.1202 | 1091062240.302 | 188863.1193 | 0.5447 | 0.00034572 | 377.2037
December 2001 | 2497971776.0567 | 53.9271 | 2134152223.7367 | 71.9319 | 974719403.9433 | 1159432819.7933 | 202733.4883 | 0.5325 | 0.00034141 | 395.8371
January 2002 | 2638267662.1019 | 53.9271 | 2254014577.6889 | 70.0557 | 1127691377.8981 | 1126323199.7908 | 192863.5616 | 0.54435 | 0.00034177 | 384.946
February 2002 | 2480831811.9411 | 53.9271 | 2119508626.526 | 71.9534 | 967000499.0589 | 1152508127.4671 | 202229.8873 | 0.5283 | 0.0003399 | 391.7395
March 2002 | 2736168916.2326 | 53.9271 | 2337656907.5232 | 72.9681 | 1013644027.5674 | 1324012879.9558 | 235547.568 | 0.51185 | 0.00033389 | 442.0717
2001-2002 | 25982322747.2494 | 53.9271 | 22198101836.2105 | 66.9536 | 12684454349.7206 | 9513647486.4898 | 1656001.9531 | 0.53521 | 0.00034009 | 3233.4847
Reduction in Losses (in GWhe) |  | 11.0624 | < 15

## Daily Report 02-03
INDIAN RAYON AND INDUSTRIES LTD.,
UNIT : JAYA SHREE TEXTILES
RISHRA, HOOGHLY
BOILER DAILY REPORT
MONTH -APRIL -2002
Particulars | 2002-04-01 | 2002-04-02 | 2002-04-03 | 2002-04-04 | 2002-04-05 | 2002-04-06 | 2002-04-07 | Total | 1 Week | 2002-04-08 | 2002-04-09 | 2002-04-10 | 2002-04-11 | 2002-04-12 | 2002-04-13 | 2002-04-14 | Total | 2 Week | 2002-04-15 | 2002-04-16 | 2002-04-17 | 2002-04-18 | 2002-04-19 | 2002-04-20 | 2002-04-21 | Total | 3 Week | 2002-04-22 | 2002-04-23 | 2002-04-24 | 2002-04-25 | 2002-04-26 | 2002-04-27 | 2002-04-28 | 2002-04-29 | 2002-04-30 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 150299 | 164166.2 | 160132.1 | 165274.4 | 155184.3 | 151164.6 | 161171.7 | 1107392.3 | 1107392.3 | 149171 | 163038.2 | 159004.1 | 164146.4 | 154056.3 | 150036.6 | 160043.7 | 1099496.3 | 1099496.3 | 152017 | 165884.2 | 161850.1 | 166992.4 | 156902.3 | 152882.6 | 162889.7 | 1119418.3 | 1119418.3 | 119473.9 | 120341.1 | 121307 | 122449.3 | 123359.2 | 124339.5 | 125346.6 | 126463.8 | 127282.7 | 1110363.1 | 1110363.1 | 4436670
Coal Audited (kgs) | 23104 | 23001 | 22996 | 23006 | 23109 | 22991 | 22980 | 161187 | 161187 | 24282 | 24179 | 24172 | 24185 | 24288 | 24169 | 24159 | 169434 | 169434 | 24576 | 24473 | 24471 | 24479 | 24581 | 24463 | 24453 | 171496 | 171496 | 20048 | 19945 | 19940 | 19952 | 20053 | 19935 | 19925 | 20039 | 19906 | 179743 | 179743 | 681860
Actual Coal Consumed (Kgs) | 22410.88 | 22310.97 | 22306.12 | 22315.82 | 22415.73 | 22301.27 | 22290.6 | 156351.39 | 156351.39 | 23553.54 | 23453.63 | 23446.84 | 23459.45 | 23559.36 | 23443.93 | 23434.23 | 164350.98 | 164350.98 | 23838.72 | 23738.81 | 23736.87 | 23744.63 | 23843.57 | 23729.11 | 23719.41 | 166351.12 | 166351.12 | 19446.56 | 19346.65 | 19341.8 | 19353.44 | 19451.41 | 19336.95 | 19327.25 | 19437.83 | 19308.82 | 174350.71 | 174350.71 | 661404.2
Feed Water Temp. deg. C | 72 | 75 | 73 | 73 | 74 | 73 | 71 | 73 | 73 | 71 | 74 | 72 | 72 | 73 | 72 | 70 | 72 | 72 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.8325
Feed Water Consumed (Kg) | 154807.97 | 169091.186 | 164936.063 | 170232.632 | 159839.829 | 155699.538 | 166006.851 | 1140614.069 | 1140614.069 | 153646.13 | 167929.346 | 163774.223 | 169070.792 | 158677.989 | 154537.698 | 164845.011 | 1132481.189 | 1132481.189 | 156577.51 | 170860.726 | 166705.603 | 172002.172 | 161609.369 | 157469.078 | 167776.391 | 1153000.849 | 1153000.849 | 123058.117 | 123951.333 | 124946.21 | 126122.779 | 127059.976 | 128069.685 | 129106.998 | 130257.714 | 131101.181 | 1143673.993 | 1143673.993 | 4569770.1
MONTH -MAY -2002
Particulars | 2002-05-02 | 2002-05-03 | 2002-05-04 | 2002-05-05 | 2002-05-06 | 2002-05-07 | 2002-05-08 | Total | 1 Week | 2002-05-09 | 2002-05-10 | 2002-05-11 | 2002-05-12 | 2002-05-13 | 2002-05-14 | 2002-05-15 | Total | 2 Week | 2002-05-16 | 2002-05-17 | 2002-05-18 | 2002-05-19 | 2002-05-20 | 2002-05-21 | 2002-05-22 | Total | 3 Week | 2002-05-23 | 2002-05-24 | 2002-05-25 | 2002-05-26 | 2002-05-27 | 2002-05-28 | 2002-05-29 | 2002-05-30 | 2002-05-31 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 143104.1 | 156971.3 | 152938.9 | 158079.5 | 147989.4 | 143969.7 | 153976.8 | 1057029.7 | 1057029.7 | 144675.7 | 158542.9 | 154508.6 | 159651.1 | 149561 | 145541.3 | 155548.4 | 1068029 | 1068029 | 144390.1 | 158257.3 | 154223.2 | 159365.5 | 149275.4 | 145255.7 | 155262.8 | 1066030 | 1066030 | 115770 | 116637.2 | 117603.1 | 118745.4 | 119655.3 | 120635.6 | 121642.7 | 122759.9 | 123579.8 | 1077029 | 1077029 | 4268117.7
Coal Audited (kgs) | 22263 | 22160 | 22155 | 22164 | 22268 | 22149 | 22139 | 155298 | 155298 | 22439 | 22336 | 22334 | 22342 | 22444 | 22326 | 22315 | 156536 | 156536 | 22380 | 22277 | 22272 | 22282 | 22386 | 22267 | 22257 | 156121 | 156121 | 17562 | 17459 | 17456 | 17464 | 17567 | 17448 | 17438 | 17552 | 17412 | 157358 | 157358 | 625313
Actual Coal Consumed (Kgs) | 21595.11 | 21495.2 | 21490.35 | 21499.08 | 21599.96 | 21484.53 | 21474.83 | 150639.06 | 150639.06 | 21765.83 | 21665.92 | 21663.98 | 21671.74 | 21770.68 | 21656.22 | 21645.55 | 151839.92 | 151839.92 | 21708.6 | 21608.69 | 21603.84 | 21613.54 | 21714.42 | 21598.99 | 21589.29 | 151437.37 | 151437.37 | 17035.14 | 16935.23 | 16932.32 | 16940.08 | 17039.99 | 16924.56 | 16914.86 | 17025.44 | 16889.64 | 152637.26 | 152637.26 | 606553.61
Feed Water Temp. deg. C | 70 | 73 | 71 | 71 | 72 | 71 | 69 | 71 | 71 | 71 | 74 | 72 | 72 | 73 | 72 | 70 | 72 | 72 | 74 | 77 | 75 | 75 | 76 | 75 | 73 | 75 | 75 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.8325
Feed Water Consumed (Kg) | 147397.223 | 161680.439 | 157527.067 | 162821.885 | 152429.082 | 148288.791 | 158596.104 | 1088740.591 | 1088740.591 | 149015.971 | 163299.187 | 159143.858 | 164440.633 | 154047.83 | 149907.539 | 160214.852 | 1100069.87 | 1100069.87 | 148721.803 | 163005.019 | 158849.896 | 164146.465 | 153753.662 | 149613.371 | 159920.684 | 1098010.9 | 1098010.9 | 119243.1 | 120136.316 | 121131.193 | 122307.762 | 123244.959 | 124254.668 | 125291.981 | 126442.697 | 127287.194 | 1109339.87 | 1109339.87 | 4396161.231
MONTH -JUNE -2002
Particulars | 2002-06-01 | 2002-06-02 | 2002-06-03 | 2002-06-04 | 2002-06-05 | 2002-06-06 | 2002-06-07 | Total | 1 Week | 2002-06-08 | 2002-06-09 | 2002-06-10 | 2002-06-11 | 2002-06-12 | 2002-06-13 | 2002-06-14 | Total | 2 Week | 2002-06-15 | 2002-06-16 | 2002-06-17 | 2002-06-18 | 2002-06-19 | 2002-06-20 | 2002-06-21 | Total | 3 Week | 2002-06-22 | 2002-06-23 | 2002-06-24 | 2002-06-25 | 2002-06-26 | 2002-06-27 | 2002-06-28 | 2002-06-29 | 2002-06-30 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 125018.8 | 138886 | 134851.9 | 139994.2 | 129904.1 | 125884.4 | 135891.5 | 930430.9 | 930430.9 | 125133.2 | 139000.4 | 134966.3 | 140108.6 | 130018.5 | 125998.8 | 136005.9 | 931231.7 | 931231.7 | 125147.4 | 139014.6 | 134980.5 | 140122.8 | 130032.7 | 126013 | 136020.1 | 931331.1 | 931331.1 | 99692.4 | 100559.6 | 101525.5 | 102667.8 | 103577.7 | 104558 | 105565.1 | 106682.7 | 107502.5 | 932331.3 | 932331.3 | 3725325
Coal Audited (kgs) | 19408 | 19305 | 19300 | 19309 | 19413 | 19295 | 19285 | 135315 | 135315 | 19732 | 19629 | 19624 | 19633 | 19737 | 19619 | 19608 | 137582 | 137582 | 19673 | 19570 | 19565 | 19575 | 19678 | 19560 | 19549 | 137170 | 137170 | 15570 | 15467 | 15462 | 15474 | 15575 | 15457 | 15446 | 15561 | 15426 | 139438 | 139438 | 549505
Actual Coal Consumed (Kgs) | 18825.76 | 18725.85 | 18721 | 18729.73 | 18830.61 | 18716.15 | 18706.45 | 131255.55 | 131255.55 | 19140.04 | 19040.13 | 19035.28 | 19044.01 | 19144.89 | 19030.43 | 19019.76 | 133454.54 | 133454.54 | 19082.81 | 18982.9 | 18978.05 | 18987.75 | 19087.66 | 18973.2 | 18962.53 | 133054.9 | 133054.9 | 15102.9 | 15002.99 | 14998.14 | 15009.78 | 15107.75 | 14993.29 | 14982.62 | 15094.17 | 14963.22 | 135254.86 | 135254.86 | 533019.85
Feed Water Temp. deg. C | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 75 | 73 | 73 | 74 | 73 | 71 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 128769.364 | 143052.58 | 138897.457 | 144194.026 | 133801.223 | 129660.932 | 139968.245 | 958343.827 | 958343.827 | 128887.196 | 143170.412 | 139015.289 | 144311.858 | 133919.055 | 129778.764 | 140086.077 | 959168.651 | 959168.651 | 128901.822 | 143185.038 | 139029.915 | 144326.484 | 133933.681 | 129793.39 | 140100.703 | 959271.033 | 959271.033 | 102683.172 | 103576.388 | 104571.265 | 105747.834 | 106685.031 | 107694.74 | 108732.053 | 109883.181 | 110727.575 | 960301.239 | 960301.239 | 3837084.75
MONTH -JULY -2002
Particulars | 2002-07-01 | 2002-07-02 | 2002-07-03 | 2002-07-04 | 2002-07-05 | 2002-07-06 | 2002-07-07 | Total | 1 Week | 2002-07-08 | 2002-07-12 | 2002-07-13 | 2002-07-14 | 2002-07-15 | 2002-07-16 | 2002-07-17 | Total | 2 Week | 2002-07-18 | 2002-07-19 | 2002-07-20 | 2002-07-21 | 2002-07-22 | 2002-07-23 | 2002-07-24 | Total | 3 Week | 2002-07-25 | 2002-07-26 | 2002-07-27 | 2002-07-28 | 2002-07-29 | 2002-07-30 | 2002-07-31 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 114433.1 | 128300.3 | 124266.2 | 129408.5 | 119318.4 | 115298.7 | 125305.8 | 856331 | 856331 | 116147.4 | 130014.6 | 125980.5 | 131122.8 | 121032.7 | 117013 | 127020.1 | 868331.1 | 868331.1 | 113290.4 | 127157.6 | 123123.5 | 128265.8 | 118175.7 | 114156 | 124163.1 | 848332.1 | 848332.1 | 115004.5 | 128871.7 | 124837.6 | 129979.9 | 119889.8 | 115870.1 | 125877.2 | 860330.8 | 860330.8 | 3433325
Coal Audited (kgs) | 18055 | 17952 | 17946 | 17957 | 18058 | 17941 | 17931 | 125840 | 125840 | 18053 | 17949 | 17941 | 17952 | 18053 | 17939 | 17929 | 125816 | 125816 | 18353 | 18249 | 18244 | 18252 | 18358 | 18239 | 18229 | 127924 | 127924 | 18348 | 18245 | 18249 | 18257 | 18354 | 18235 | 18213 | 127901 | 127901 | 507481
Actual Coal Consumed (Kgs) | 17513.35 | 17413.44 | 17407.62 | 17418.29 | 17516.26 | 17402.77 | 17393.07 | 122064.8 | 122064.8 | 17511.41 | 17410.53 | 17402.77 | 17413.44 | 17511.41 | 17400.83 | 17391.13 | 122041.52 | 122041.52 | 17802.41 | 17701.53 | 17696.68 | 17704.44 | 17807.26 | 17691.83 | 17682.13 | 124086.28 | 124086.28 | 17797.56 | 17697.65 | 17701.53 | 17709.29 | 17803.38 | 17687.95 | 17666.61 | 124063.97 | 124063.97 | 492256.57
Feed Water Temp. deg. C | 71 | 74 | 72 | 72 | 73 | 72 | 70 | 72 | 72 | 75 | 76 | 73 | 76 | 75 | 74 | 76 | 75 | 75 | 72 | 75 | 73 | 73 | 74 | 73 | 71 | 73 | 73 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 73.5
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.82 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.83
Feed Water Consumed (Kg) | 117866.093 | 132149.309 | 127994.186 | 133290.755 | 122897.952 | 118757.661 | 129064.974 | 882020.93 | 882020.93 | 119631.822 | 133915.038 | 129759.915 | 135056.484 | 124663.681 | 120523.39 | 130830.703 | 894381.033 | 894381.033 | 116689.112 | 130972.328 | 126817.205 | 132113.774 | 121720.971 | 117580.68 | 127887.993 | 873782.063 | 873782.063 | 118454.635 | 132737.851 | 128582.728 | 133879.297 | 123486.494 | 119346.203 | 129653.516 | 886140.724 | 886140.724 | 3536324.75
MONTH -AUGUST -2002
Particulars | 2002-08-01 | 2002-08-02 | 2002-08-03 | 2002-08-04 | 2002-08-05 | 2002-08-06 | 2002-08-07 | Total | 1 Week | 2002-08-08 | 2002-08-09 | 2002-08-10 | 2002-08-11 | 2002-08-12 | 2002-08-13 | 2002-08-14 | Total | 2 Week | 2002-08-15 | 2002-08-16 | 2002-08-17 | 2002-08-18 | 2002-08-19 | 2002-08-20 | 2002-08-21 | Total | 3 Week | 2002-08-22 | 2002-08-23 | 2002-08-24 | 2002-08-25 | 2002-08-26 | 2002-08-27 | 2002-08-28 | 2002-08-29 | 2002-08-30 | 2002-08-31 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 98510.8 | 112378 | 108343.9 | 113486.2 | 103396.1 | 99376.4 | 109383.5 | 744874.9 | 744874.9 | 98639.5 | 112506.7 | 108472.6 | 113614.9 | 103524.8 | 99505.1 | 109512.2 | 745775.8 | 745775.8 | 98667.8 | 112535 | 108500.9 | 113643.2 | 103553.1 | 99533.4 | 109540.5 | 745973.9 | 745973.9 | 69788.1 | 70655.3 | 71621.2 | 72763.5 | 74673.4 | 76653.7 | 74655.8 | 77779.7 | 78651.2 | 79633.5 | 746875.4 | 746875.4 | 2983500
Coal Audited (kgs) | 15343 | 15240 | 15235 | 15245 | 15348 | 15232 | 15220 | 106863 | 106863 | 15461 | 15358 | 15353 | 15363 | 15469 | 15347 | 15337 | 107688 | 107688 | 15520 | 15416 | 15411 | 15424 | 15525 | 15406 | 15396 | 108098 | 108098 | 10969 | 10866 | 10861 | 10871 | 10974 | 10856 | 10845 | 10948 | 10876 | 10855 | 108921 | 108921 | 431570
Actual Coal Consumed (Kgs) | 14882.71 | 14782.8 | 14777.95 | 14787.65 | 14887.56 | 14775.04 | 14763.4 | 103657.11 | 103657.11 | 14997.17 | 14897.26 | 14892.41 | 14902.11 | 15004.93 | 14886.59 | 14876.89 | 104457.36 | 104457.36 | 15054.4 | 14953.52 | 14948.67 | 14961.28 | 15059.25 | 14943.82 | 14934.12 | 104855.06 | 104855.06 | 10639.93 | 10540.02 | 10535.17 | 10544.87 | 10644.78 | 10530.32 | 10519.65 | 10619.56 | 10549.72 | 10529.35 | 105653.37 | 105653.37 | 418622.9
Feed Water Temp. deg. C | 70 | 73 | 71 | 71 | 72 | 71 | 69 | 71 | 71 | 72 | 75 | 73 | 73 | 74 | 73 | 71 | 73 | 73 | 76 | 79 | 77 | 77 | 78 | 77 | 75 | 77 | 77 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 74
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 101466.124 | 115749.34 | 111594.217 | 116890.786 | 106497.983 | 102357.692 | 112665.005 | 767221.147 | 767221.147 | 101598.685 | 115881.901 | 111726.778 | 117023.347 | 106630.544 | 102490.253 | 112797.566 | 768149.074 | 768149.074 | 101627.834 | 115911.05 | 111755.927 | 117052.496 | 106659.693 | 102519.402 | 112826.715 | 768353.117 | 768353.117 | 71881.743 | 72774.959 | 73769.836 | 74946.405 | 76913.602 | 78953.311 | 76895.474 | 80113.091 | 81010.736 | 82022.505 | 769281.662 | 769281.662 | 3073005
MONTH -SEPTEMBER -2002
Particulars | 2002-09-01 | 2002-09-02 | 2002-09-03 | 2002-09-04 | 2002-09-05 | 2002-09-06 | 2002-09-07 | Total | 1 Week | 2002-09-08 | 2002-09-09 | 2002-09-10 | 2002-09-11 | 2002-09-12 | 2002-09-13 | 2002-09-14 | Total | 2 Week | 2002-09-15 | 2002-09-16 | 2002-09-17 | 2002-09-18 | 2002-09-19 | 2002-09-20 | 2002-09-21 | Total | 3 Week | 2002-09-22 | 2002-09-23 | 2002-09-24 | 2002-09-25 | 2002-09-26 | 2002-09-27 | 2002-09-28 | 2002-09-29 | 2002-09-30 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 109322.2 | 123189.4 | 119155.3 | 124297.6 | 114207.5 | 110187.8 | 120194.9 | 820554.7 | 820554.7 | 109449.2 | 123316.4 | 119282.3 | 124424.6 | 114334.5 | 110314.8 | 120321.9 | 821443.7 | 821443.7 | 109766.7 | 123633.9 | 119599.8 | 124742.1 | 114652 | 110632.3 | 120639.4 | 823666.2 | 823666.2 | 87717.3 | 88584.5 | 89550.4 | 90692.7 | 91602.6 | 92582.9 | 93590 | 94708.9 | 95526.1 | 824555.4 | 824555.4 | 3290220
Coal Audited (kgs) | 17072 | 16969 | 16964 | 16974 | 17077 | 16959 | 16948 | 118963 | 118963 | 17204 | 17101 | 17097 | 17108 | 17209 | 17091 | 17080 | 119890 | 119890 | 17529 | 17426 | 17421 | 17431 | 17534 | 17415 | 17405 | 122161 | 122161 | 13754 | 13651 | 13645 | 13656 | 13758 | 13640 | 13630 | 13743 | 13609 | 123086 | 123086 | 484100
Actual Coal Consumed (Kgs) | 16559.84 | 16459.93 | 16455.08 | 16464.78 | 16564.69 | 16450.23 | 16439.56 | 115394.11 | 115394.11 | 16687.88 | 16587.97 | 16584.09 | 16594.76 | 16692.73 | 16578.27 | 16567.6 | 116293.3 | 116293.3 | 17003.13 | 16903.22 | 16898.37 | 16908.07 | 17007.98 | 16892.55 | 16882.85 | 118496.17 | 118496.17 | 13341.38 | 13241.47 | 13235.65 | 13246.32 | 13345.26 | 13230.8 | 13221.1 | 13330.71 | 13200.73 | 119393.42 | 119393.42 | 469577
Feed Water Temp. deg. C | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 112601.866 | 126885.082 | 122729.959 | 128026.528 | 117633.725 | 113493.434 | 123800.747 | 845171.341 | 845171.341 | 112732.676 | 127015.892 | 122860.769 | 128157.338 | 117764.535 | 113624.244 | 123931.557 | 846087.011 | 846087.011 | 113059.701 | 127342.917 | 123187.794 | 128484.363 | 118091.56 | 113951.269 | 124258.582 | 848376.186 | 848376.186 | 90348.819 | 91242.035 | 92236.912 | 93413.481 | 94350.678 | 95360.387 | 96397.7 | 97550.167 | 98391.883 | 849292.062 | 849292.062 | 3388926.6
MONTH -OCTOBER -2002
Particulars | 2002-10-01 | 2002-10-02 | 2002-10-03 | 2002-10-04 | 2002-10-05 | 2002-10-06 | 2002-10-07 | Total | 1 Week | 2002-10-08 | 2002-10-09 | 2002-10-10 | 2002-10-11 | 2002-10-12 | 2002-10-13 | 2002-10-14 | Total | 2 Week | 2002-10-15 | 2002-10-16 | 2002-10-17 | 2002-10-18 | 2002-10-19 | 2002-10-20 | 2002-10-21 | Total | 3 Week | 2002-10-22 | 2002-10-23 | 2002-10-24 | 2002-10-25 | 2002-10-26 | 2002-10-27 | 2002-10-28 | 2002-10-29 | 2002-10-30 | 2002-10-31 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 133656.8 | 147524 | 143489.9 | 148632.2 | 138542.1 | 134522.4 | 144529.5 | 990896.9 | 990896.9 | 133771.2 | 147638.4 | 143604.3 | 148746.6 | 138656.5 | 134636.8 | 144643.9 | 991697.7 | 991697.7 | 133828.2 | 147695.4 | 143661.3 | 148803.6 | 138713.5 | 134693.8 | 144700.9 | 992096.7 | 992096.7 | 94389.9 | 95257.1 | 96223 | 97365.3 | 99275.2 | 101255.5 | 99262.6 | 102381.5 | 103253.3 | 104234.9 | 992898.3 | 992898.3 | 3967589.6
Coal Audited (kgs) | 19868 | 19765 | 19760 | 19769 | 19873 | 19755 | 19744 | 138534 | 138534 | 20309 | 20206 | 20201 | 20211 | 20314 | 20196 | 20186 | 141623 | 141623 | 19721 | 19618 | 19612 | 19623 | 19729 | 19607 | 19597 | 137507 | 137507 | 14137 | 14034 | 14029 | 14039 | 14142 | 14024 | 14012 | 14116 | 14044 | 14019 | 140596 | 140596 | 558260
Actual Coal Consumed (Kgs) | 19271.96 | 19172.05 | 19167.2 | 19175.93 | 19276.81 | 19162.35 | 19151.68 | 134377.98 | 134377.98 | 19699.73 | 19599.82 | 19594.97 | 19604.67 | 19704.58 | 19590.12 | 19580.42 | 137374.31 | 137374.31 | 19129.37 | 19029.46 | 19023.64 | 19034.31 | 19137.13 | 19018.79 | 19009.09 | 133381.79 | 133381.79 | 13712.89 | 13612.98 | 13608.13 | 13617.83 | 13717.74 | 13603.28 | 13591.64 | 13692.52 | 13622.68 | 13598.43 | 136378.12 | 136378.12 | 541512.2
Feed Water Temp. deg. C | 72 | 74 | 73 | 73 | 74 | 73 | 72 | 73 | 73 | 72 | 75 | 72 | 73 | 74 | 74 | 71 | 73 | 73 | 74 | 73 | 74 | 73 | 73 | 72 | 72 | 73 | 73 | 73 | 72 | 74 | 74 | 72 | 73 | 72 | 74 | 72 | 74 | 73 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 137666.504 | 151949.72 | 147794.597 | 153091.166 | 142698.363 | 138558.072 | 148865.385 | 1020623.807 | 1020623.807 | 137784.336 | 152067.552 | 147912.429 | 153208.998 | 142816.195 | 138675.904 | 148983.217 | 1021448.631 | 1021448.631 | 137843.046 | 152126.262 | 147971.139 | 153267.708 | 142874.905 | 138734.614 | 149041.927 | 1021859.601 | 1021859.601 | 97221.597 | 98114.813 | 99109.69 | 100286.259 | 102253.456 | 104293.165 | 102240.478 | 105452.945 | 106350.899 | 107361.947 | 1022685.249 | 1022685.249 | 4086617.288
MONTH -NOVEMBER -2002
Particulars | 2002-11-01 | 2002-11-02 | 2002-11-03 | 2002-11-04 | 2002-11-05 | 2002-11-06 | 2002-11-07 | Total | 1 Week | 2002-11-08 | 2002-11-09 | 2002-11-10 | 2002-11-11 | 2002-11-12 | 2002-11-13 | 2002-11-14 | Total | 2 Week | 2002-11-15 | 2002-11-16 | 2002-11-17 | 2002-11-18 | 2002-11-19 | 2002-11-20 | 2002-11-21 | Total | 3 Week | 2002-11-22 | 2002-11-23 | 2002-11-24 | 2002-11-25 | 2002-11-26 | 2002-11-27 | 2002-11-28 | 2002-11-29 | 2002-11-30 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 115168.3 | 129035.5 | 125001.4 | 130143.7 | 120053.6 | 116033.9 | 126041 | 861477.4 | 861477.4 | 115468.4 | 129335.6 | 125301.5 | 130443.8 | 120353.7 | 116334 | 126341.1 | 863578.1 | 863578.1 | 115153.8 | 129021 | 124986.9 | 130129.2 | 120039.1 | 116019.4 | 126026.5 | 861375.9 | 861375.9 | 92042.1 | 92909.3 | 93875.2 | 95017.5 | 95927.4 | 96907.7 | 97914.8 | 99032.5 | 99851.2 | 863477.7 | 863477.7 | 3449909.1
Coal Audited (kgs) | 17973 | 17870 | 17865 | 17875 | 17982 | 17860 | 17849 | 125274 | 125274 | 18106 | 18003 | 17998 | 18008 | 18111 | 17993 | 17982 | 126201 | 126201 | 18135 | 18032 | 18027 | 18037 | 18144 | 18022 | 18011 | 126408 | 126408 | 14226 | 14123 | 14118 | 14128 | 14221 | 14112 | 14102 | 14215 | 14087 | 127332 | 127332 | 505215
Actual Coal Consumed (Kgs) | 17433.81 | 17333.9 | 17329.05 | 17338.75 | 17442.54 | 17324.2 | 17313.53 | 121515.78 | 121515.78 | 17562.82 | 17462.91 | 17458.06 | 17467.76 | 17567.67 | 17453.21 | 17442.54 | 122414.97 | 122414.97 | 17590.95 | 17491.04 | 17486.19 | 17495.89 | 17599.68 | 17481.34 | 17470.67 | 122615.76 | 122615.76 | 13799.22 | 13699.31 | 13694.46 | 13704.16 | 13794.37 | 13688.64 | 13678.94 | 13788.55 | 13664.39 | 123512.04 | 123512.04 | 490058.55
Feed Water Temp. deg. C | 72 | 75 | 73 | 73 | 74 | 73 | 71 | 73 | 73 | 73 | 76 | 74 | 74 | 75 | 74 | 72 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 74
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.84 | 8.8325
Feed Water Consumed (Kg) | 118623.349 | 132906.565 | 128751.442 | 134048.011 | 123655.208 | 119514.917 | 129822.23 | 887321.722 | 887321.722 | 118932.452 | 133215.668 | 129060.545 | 134357.114 | 123964.311 | 119824.02 | 130131.333 | 889485.443 | 889485.443 | 118608.414 | 132891.63 | 128736.507 | 134033.076 | 123640.273 | 119499.982 | 129807.295 | 887217.177 | 887217.177 | 94803.363 | 95696.579 | 96691.456 | 97868.025 | 98805.222 | 99814.931 | 100852.244 | 102003.475 | 102846.736 | 889382.031 | 889382.031 | 3553406.373
MONTH -DECEMBER -2002
Particulars | 2002-12-01 | 2002-12-02 | 2002-12-03 | 2002-12-04 | 2002-12-05 | 2002-12-06 | 2002-12-07 | Total | 1 Week | 2002-12-08 | 2002-12-09 | 2002-12-10 | 2002-12-11 | 2002-12-12 | 2002-12-13 | 2002-12-14 | Total | 2 Week | 2002-12-15 | 2002-12-16 | 2002-12-17 | 2002-12-18 | 2002-12-19 | 2002-12-20 | 2002-12-21 | Total | 3 Week | 2002-12-22 | 2002-12-23 | 2002-12-24 | 2002-12-25 | 2002-12-26 | 2002-12-27 | 2002-12-28 | 2002-12-29 | 2002-12-30 | 2002-12-31 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 130853.7 | 144720.9 | 140686.8 | 145829.1 | 135739 | 131719.3 | 141726.4 | 971275.2 | 971275.2 | 131308 | 145175.2 | 141141.1 | 146283.4 | 136193.3 | 132173.6 | 142180.7 | 974455.3 | 974455.3 | 131028 | 144895.2 | 140861.1 | 146003.4 | 135913.3 | 131893.6 | 141900.7 | 972495.3 | 972495.3 | 92667.6 | 93534.8 | 94500.7 | 95643 | 97552.1 | 99533.2 | 97540.3 | 100659.2 | 101509.7 | 102533.6 | 975674.2 | 975674.2 | 3893900
Coal Audited (kgs) | 20169 | 20066 | 20061 | 20071 | 20176 | 20056 | 20045 | 140644 | 140644 | 20654 | 20551 | 20545 | 20558 | 20659 | 20540 | 20530 | 144037 | 144037 | 20333 | 20230 | 20225 | 20235 | 20337 | 20220 | 20209 | 141789 | 141789 | 14595 | 14492 | 14487 | 14497 | 14600 | 14476 | 14471 | 14574 | 14502 | 14486 | 145180 | 145180 | 571650
Actual Coal Consumed (Kgs) | 19563.93 | 19464.02 | 19459.17 | 19468.87 | 19570.72 | 19454.32 | 19443.65 | 136424.68 | 136424.68 | 20034.38 | 19934.47 | 19928.65 | 19941.26 | 20039.23 | 19923.8 | 19914.1 | 139715.89 | 139715.89 | 19723.01 | 19623.1 | 19618.25 | 19627.95 | 19726.89 | 19613.4 | 19602.73 | 137535.33 | 137535.33 | 14157.15 | 14057.24 | 14052.39 | 14062.09 | 14162 | 14041.72 | 14036.87 | 14136.78 | 14066.94 | 14051.42 | 140824.6 | 140824.6 | 554500.5
Feed Water Temp. deg. C | 74 | 73 | 72 | 71 | 75 | 72 | 74 | 73 | 73 | 74 | 73 | 75 | 73 | 74 | 75 | 74 | 74 | 74 | 72 | 73 | 71 | 74 | 72 | 71 | 71 | 72 | 72 | 73 | 74 | 72 | 73 | 72 | 74 | 73 | 72 | 74 | 73 | 73 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 134779.311 | 149062.527 | 144907.404 | 150203.973 | 139811.17 | 135670.879 | 145978.192 | 1000413.456 | 1000413.456 | 135247.24 | 149530.456 | 145375.333 | 150671.902 | 140279.099 | 136138.808 | 146446.121 | 1003688.959 | 1003688.959 | 134958.84 | 149242.056 | 145086.933 | 150383.502 | 139990.699 | 135850.408 | 146157.721 | 1001670.159 | 1001670.159 | 95447.628 | 96340.844 | 97335.721 | 98512.29 | 100478.663 | 102519.196 | 100466.509 | 103678.976 | 104554.991 | 105609.608 | 1004944.426 | 1004944.426 | 4010717
MONTH -JANUARY -2003
Particulars | 2003-01-01 | 2003-01-02 | 2003-01-03 | 2003-01-04 | 2003-01-05 | 2003-01-06 | 2003-01-07 | Total | 1week | 2003-01-08 | 2003-01-09 | 2003-01-10 | 2003-01-11 | 2003-01-12 | 2003-01-13 | 2003-01-14 | Total | 2 week | 2003-01-15 | 2003-01-16 | 2003-01-17 | 2003-01-18 | 2003-01-19 | 2003-01-20 | 2003-01-21 | Total | 3 week | 2003-01-22 | 2003-01-23 | 2003-01-24 | 2003-01-25 | 2003-01-26 | 2003-01-27 | 2003-01-28 | 2003-01-29 | 2003-01-30 | 2003-01-31 | Total | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 135535.8 | 149403 | 145368.9 | 150511.2 | 140421.1 | 136401.4 | 146408.5 | 1004049.9 | 1004049.9 | 136817.9 | 150685.1 | 146651 | 151793.3 | 141703.2 | 137683.5 | 147690.6 | 1013024.6 | 1013024.6 | 137682.2 | 151549.4 | 147515.3 | 152657.6 | 142567.5 | 138547.8 | 148554.9 | 1019074.7 | 1019074.7 | 97905.1 | 98772.3 | 99738.2 | 100880.5 | 102790.4 | 104770.7 | 102777.8 | 105896.7 | 106747.2 | 107771.9 | 1028050.8 | 1028050.8 | 4064200
Coal Audited (kgs) | 18635 | 18532 | 18527 | 18537 | 18636 | 18524 | 18511 | 129902 | 129902 | 20401 | 20298 | 20295 | 20305 | 20406 | 20288 | 20277 | 142270 | 142270 | 20404 | 20301 | 20296 | 20312 | 20409 | 20291 | 20280 | 142293 | 142293 | 15542 | 15439 | 15434 | 15439 | 15547 | 15424 | 15423 | 15520 | 15449 | 15436 | 154653 | 154653 | 569118
Actual Coal Consumed (Kgs) | 18075.95 | 17976.04 | 17971.19 | 17980.89 | 18076.92 | 17968.28 | 17955.67 | 126004.94 | 126004.94 | 19788.97 | 19689.06 | 19686.15 | 19695.85 | 19793.82 | 19679.36 | 19668.69 | 138001.9 | 138001.9 | 19791.88 | 19691.97 | 19687.12 | 19702.64 | 19796.73 | 19682.27 | 19671.6 | 138024.21 | 138024.21 | 15075.74 | 14975.83 | 14970.98 | 14975.83 | 15080.59 | 14961.28 | 14960.31 | 15054.4 | 14985.53 | 14972.92 | 150013.41 | 150013.41 | 552044.46
Feed Water Temp. deg. C | 73 | 72 | 74 | 71 | 74 | 74 | 73 | 73 | 73 | 71 | 73 | 70 | 72 | 70 | 70 | 71 | 71 | 71 | 72 | 73 | 74 | 71 | 70 | 71 | 73 | 72 | 72 | 73 | 74 | 70 | 72 | 71 | 73 | 71 | 73 | 72 | 71 | 72 | 72 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 139601.874 | 153885.09 | 149729.967 | 155026.536 | 144633.733 | 140493.442 | 150800.755 | 1034171.397 | 1034171.397 | 140922.437 | 155205.653 | 151050.53 | 156347.099 | 145954.296 | 141814.005 | 152121.318 | 1043415.338 | 1043415.338 | 141812.666 | 156095.882 | 151940.759 | 157237.328 | 146844.525 | 142704.234 | 153011.547 | 1049646.941 | 1049646.941 | 100842.253 | 101735.469 | 102730.346 | 103906.915 | 105874.112 | 107913.821 | 105861.134 | 109073.601 | 109949.616 | 111005.057 | 1058892.324 | 1058892.324 | 4186126
MONTH -FEBRUARY -2003
Particulars | 2003-02-01 | 2003-02-02 | 2003-02-03 | 2003-02-04 | 2003-02-05 | 2003-02-06 | 2003-02-07 | Total | 1 Week | 2003-02-08 | 2003-02-09 | 2003-02-10 | 2003-02-11 | 2003-02-12 | 2003-02-13 | 2003-02-14 | Total | 2 Week | 2003-02-15 | 2003-02-16 | 2003-02-17 | 2003-02-18 | 2003-02-19 | 2003-02-20 | 2003-02-21 | Total | 3 Week | 2003-02-22 | 2003-02-23 | 2003-02-24 | 2003-02-25 | 2003-02-26 | 2003-02-27 | 2003-02-28 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 106118 | 119985.2 | 115951.1 | 121093.4 | 111003.3 | 106983.6 | 116990.7 | 798125.3 | 798125.3 | 105989.4 | 119856.6 | 115822.5 | 120964.8 | 110874.7 | 106855 | 116862.1 | 797225.1 | 797225.1 | 106560.8 | 120428 | 116393.9 | 121536.2 | 111446.1 | 107426.4 | 117433.5 | 801224.9 | 801224.9 | 106432.2 | 120299.4 | 116265.3 | 121407.6 | 111317.5 | 107297.8 | 117304.9 | 800324.7 | 800324.7 | 3196900
Coal Audited (kgs) | 16448 | 16345 | 16340 | 16349 | 16454 | 16335 | 16325 | 114596 | 114596 | 16759 | 16656 | 16651 | 16657 | 16764 | 16645 | 16635 | 116767 | 116767 | 16464 | 16361 | 16353 | 16366 | 16469 | 16351 | 16340 | 114704 | 114704 | 16773 | 16670 | 16665 | 16679 | 16778 | 16664 | 16648 | 116877 | 116877 | 462944
Actual Coal Consumed (Kgs) | 15954.56 | 15854.65 | 15849.8 | 15858.53 | 15960.38 | 15844.95 | 15835.25 | 111158.12 | 111158.12 | 16256.23 | 16156.32 | 16151.47 | 16157.29 | 16261.08 | 16145.65 | 16135.95 | 113263.99 | 113263.99 | 15970.08 | 15870.17 | 15862.41 | 15875.02 | 15974.93 | 15860.47 | 15849.8 | 111262.88 | 111262.88 | 16269.81 | 16169.9 | 16165.05 | 16178.63 | 16274.66 | 16164.08 | 16148.56 | 113370.69 | 113370.69 | 449055.68
Feed Water Temp. deg. C | 70 | 73 | 71 | 71 | 72 | 71 | 69 | 71 | 71 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 71 | 74 | 72 | 72 | 73 | 72 | 70 | 72 | 72 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 73 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 109301.54 | 123584.756 | 119429.633 | 124726.202 | 114333.399 | 110193.108 | 120500.421 | 822069.059 | 822069.059 | 109169.082 | 123452.298 | 119297.175 | 124593.744 | 114200.941 | 110060.65 | 120367.963 | 821141.853 | 821141.853 | 109757.624 | 124040.84 | 119885.717 | 125182.286 | 114789.483 | 110649.192 | 120956.505 | 825261.647 | 825261.647 | 109625.166 | 123908.382 | 119753.259 | 125049.828 | 114657.025 | 110516.734 | 120824.047 | 824334.441 | 824334.441 | 3292807
MONTH -MARCH -2003
Particulars | 2003-03-01 | 2003-03-02 | 2003-03-03 | 2003-03-04 | 2003-03-05 | 2003-03-06 | 2003-03-07 | Total | 1 Week | 2003-03-08 | 2003-03-09 | 2003-03-10 | 2003-03-11 | 2003-03-12 | 2003-03-13 | 2003-03-14 | Total | 2 Week | 2003-03-15 | 2003-03-16 | 2003-03-17 | 2003-03-18 | 2003-03-19 | 2003-03-20 | 2003-03-21 | Total | 3 Week | 2003-03-22 | 2003-03-23 | 2003-03-24 | 2003-03-25 | 2003-03-26 | 2003-03-27 | 2003-03-28 | 2003-03-29 | 2003-03-30 | 2003-03-31 | Total | 4 Week | Monthly Total
Actual Steam Generated (Kgs) | 120509.2 | 134376.4 | 130342.3 | 135484.6 | 125394.5 | 121374.8 | 131381.9 | 898863.7 | 898863.7 | 124947.5 | 138814.7 | 134780.6 | 139922.9 | 129832.8 | 125813.1 | 135820.2 | 929931.8 | 929931.8 | 124956.7 | 138823.9 | 134789.8 | 139932.1 | 129842 | 125822.3 | 135829.4 | 929996.2 | 929996.2 | 79206.5 | 80073.7 | 81039.6 | 82181.9 | 84091.8 | 86072.1 | 84079.2 | 87198.4 | 88048.6 | 89072.5 | 841064.3 | 841064.3 | 3599856
Coal Audited (kgs) | 18194 | 18091 | 18086 | 18095 | 18199 | 18080 | 18070 | 126815 | 126815 | 18341 | 18238 | 18233 | 18243 | 18346 | 18228 | 18218 | 127847 | 127847 | 18636 | 18533 | 18528 | 18538 | 18641 | 18523 | 18512 | 129911 | 129911 | 13171 | 13068 | 13063 | 13073 | 13176 | 13058 | 13047 | 13151 | 13080 | 13060 | 130947 | 130947 | 515520
Actual Coal Consumed (Kgs) | 17648.18 | 17548.27 | 17543.42 | 17552.15 | 17653.03 | 17537.6 | 17527.9 | 123010.55 | 123010.55 | 17790.77 | 17690.86 | 17686.01 | 17695.71 | 17795.62 | 17681.16 | 17671.46 | 124011.59 | 124011.59 | 18076.92 | 17977.01 | 17972.16 | 17981.86 | 18081.77 | 17967.31 | 17956.64 | 126013.67 | 126013.67 | 12775.87 | 12675.96 | 12671.11 | 12680.81 | 12780.72 | 12666.26 | 12655.59 | 12756.47 | 12687.6 | 12668.2 | 127018.59 | 127018.59 | 500054.4
Feed Water Temp. deg. C | 73 | 72 | 74 | 73 | 71 | 75 | 73 | 73 | 73 | 71 | 74 | 72 | 72 | 73 | 72 | 70 | 72 | 72 | 74 | 72 | 76 | 75 | 73 | 73 | 75 | 74 | 74 | 75 | 74 | 73 | 72 | 75 | 75 | 74 | 73 | 74 | 75 | 74 | 74 | 73.25
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 124124.476 | 138407.692 | 134252.569 | 139549.138 | 129156.335 | 125016.044 | 135323.357 | 925829.611 | 925829.611 | 128695.925 | 142979.141 | 138824.018 | 144120.587 | 133727.784 | 129587.493 | 139894.806 | 957829.754 | 957829.754 | 128705.401 | 142988.617 | 138833.494 | 144130.063 | 133737.26 | 129596.969 | 139904.282 | 957896.086 | 957896.086 | 81582.695 | 82475.911 | 83470.788 | 84647.357 | 86614.554 | 88654.263 | 86601.576 | 89814.352 | 90690.058 | 91744.675 | 866296.229 | 866296.229 | 3707851.68

## CER Estimation_02-03
Monitored Parameters for the year 2002-2003
Months | Quantity of Coal Used | Coal-Audited | Gross Calorific Value of Coal | Heat Energy Input | Steam Load | Steam Pressure | Steam Pressure | Steam Enthalpy | Feed water Load | Feed Water Temerature | Feed Water Enthalpy | Number of Truck Trips
Units | (tons) | (tons) | (kCal/kg) | (kCal) | (tons) | (Bar) | (kg/cm2) | (kCal) | (tons) | (°C) | (kCal)
April 2002 | 661.4042 | 681.86 | 6129 | 4053746341.8 | 4436.67 | 8.8325 | 9 | 2944534036.2744 | 4569.7701 | 73 | 333400686.552 | 0 | Temperature | Feed Water Enthalpy
May 2002 | 606.5536 | 625.313 | 5783 | 3507699526.63 | 4268.1177 | 8.8325 | 9 | 2832669060.0102 | 4396.1612 | 73 | 320734553.4973 | 77 | (0C) | (kJ/kg)
June 2002 | 533.0199 | 549.505 | 5670 | 3022222549.5 | 3725.325 | 8.83 | 9 | 2472427802.5375 | 3837.0847 | 73 | 279945525.0513 | 0 | 64 | 267.79
July 2002 | 492.2566 | 507.481 | 6126 | 3015563747.82 | 3433.325 | 8.83 | 9 | 2278632920.6571 | 3536.3248 | 73.5 | 261541744.1242 | 157 | 65 | 271.97
August 2002 | 418.6229 | 431.57 | 5837 | 2443501867.3 | 2983.5 | 8.83 | 9 | 1980092568.8015 | 3073.005 | 74 | 227275248.8024 | 0 | 66 | 276.16
September 2002 | 469.577 | 484.1 | 5442 | 2555438034 | 3290.22 | 8.83 | 9 | 2183656836.5082 | 3388.9266 | 73 | 247248861.6253 | 0 | 67 | 280.34
October 2002 | 541.5122 | 558.26 | 5709 | 3091493149.8 | 3967.5896 | 8.83 | 9 | 2633214239.321 | 4086.6173 | 73 | 298150887.1736 | 0 | 68 | 284.52
November 2002 | 490.0586 | 505.215 | 5720 | 2803134906 | 3449.9091 | 8.8325 | 9 | 2289639474.4263 | 3553.4064 | 74 | 262805077.6096 | 66 | 72 | 301.27
December 2002 | 554.5005 | 571.65 | 5573 | 3090231286.5 | 3893.9 | 8.83 | 9 | 2584307844.3628 | 4010.717 | 73 | 292613363.9339 | 0 | 73 | 305.46
January 2003 | 552.0445 | 569.118 | 5905 | 3259822536.3 | 4064.2 | 8.83 | 9 | 2697332736.0896 | 4186.126 | 72 | 301221505.1656 | 53 | 74 | 309.65
February 2003 | 449.0557 | 462.944 | 5566 | 2499443914.88 | 3196.9 | 8.83 | 9 | 2121722116.0388 | 3292.807 | 72 | 236940856.7157 | 40
March 2003 | 500.0544 | 515.52 | 5654 | 2827307577.6 | 3599.856 | 8.83 | 9 | 2389156398.3093 | 3707.8517 | 73.25 | 270516955.7096 | 0
2002-2003 | 6268.6599 | 6462.536 | 5759.5 | 36169605438.13 | 44309.5124 | 8.8306 | 9 | 29407386033.3368 | 45638.7978 | 73.0625 | 3332395265.9606 | 393
Computation of Emission Reductions for the year 2002-2003
Months | Output Enthalpy | Baseline Boiler Efficiency | Baseline Technical Losses | Boiler Efficiency | Technical Losses | Reduction in Losses | Coal Reduction | Fixed Carbon Content (C%) in Coal | Emission Co-efficienct of Coal | Emission Reductions
| (kCal) | (%) | (kCal) | (%) | (kCal) | (kCal) | (kgs) | ('%) | (kgCO2/kCal) | (tons)
April 2002 | 2611133349.7225 | 53.9271 | 2230832268.8818 | 64.4128 | 1442612992.0775 | 788219276.8042 | 128604.8747 | 0.53555 | 0.00032039 | 252.5392
May 2002 | 2511934506.5129 | 53.9271 | 2146081338.6043 | 71.612 | 995765020.1171 | 1150316318.4872 | 198913.4218 | 0.5459 | 0.00034612 | 398.1517
June 2002 | 2192482277.4862 | 53.9271 | 1873156043.1747 | 72.5454 | 829740272.0138 | 1043415771.1609 | 184023.9455 | 0.5222 | 0.0003377 | 352.3568
July 2002 | 2017091176.5329 | 53.9271 | 1723309951.353 | 66.8894 | 998472571.2871 | 724837380.0659 | 118321.479 | 0.53502 | 0.00032023 | 232.1181
August 2002 | 1752817319.9991 | 53.9271 | 1497526520.1697 | 71.7338 | 690684547.3009 | 806841972.8688 | 138228.8801 | 0.55727 | 0.00035007 | 282.4488
September 2002 | 1936407974.8829 | 53.9271 | 1654377933.8378 | 75.776 | 619030059.1171 | 1035347874.7207 | 190251.3551 | 0.5421 | 0.00036525 | 378.1626
October 2002 | 2335063352.1474 | 53.9271 | 1994970757.203 | 75.5319 | 756429797.6526 | 1238540959.5504 | 216945.3424 | 0.5304 | 0.00034066 | 421.9153
November 2002 | 2026834396.8167 | 53.9271 | 1731634110.7507 | 72.306 | 776300509.1833 | 955333601.5674 | 167016.3639 | 0.5327 | 0.00034147 | 326.2219
December 2002 | 2291694480.4289 | 53.9271 | 1957918387.3939 | 74.1593 | 798536806.0711 | 1159381581.3227 | 208035.4533 | 0.50182 | 0.00033017 | 382.7904
January 2003 | 2396111230.924 | 53.9271 | 2047127257.7263 | 73.5043 | 863711305.3761 | 1183415952.3503 | 200409.1367 | 0.5443 | 0.00033798 | 399.9699
February 2003 | 1884781259.3231 | 53.9271 | 1610270441.9628 | 75.408 | 614662655.5569 | 995607786.4059 | 178873.1201 | 0.5242 | 0.00034532 | 343.8061
March 2003 | 2118639442.5996 | 53.9271 | 1810068120.4885 | 74.9349 | 708668135.0004 | 1101399985.4881 | 194800.1389 | 0.5188 | 0.00033645 | 370.5618
2002-2003 | 26074990767.3762 | 53.9271 | 22277273131.5464 | 72.4012 | 10094614670.7538 | 12182658460.7926 | 2124423.5115 | 0.53252 | 0.00033932 | 4141.0428
Reduction in Losses (in GWhe) |  | 14.1659 | < 15

## Daily Report 03-04
INDIAN RAYON AND INDUSTRIES LTD.,
UNIT : JAYA SHREE TEXTILES
RISHRA, HOOGHLY
BOILER DAILY REPORT
MONTH -APRIL -2003
Particulars | 2003-04-01 | 2003-04-02 | 2003-04-03 | 2003-04-04 | 2003-04-05 | 2003-04-06 | 2003-04-07 | 1 week | 2003-04-08 | 2003-04-09 | 2003-04-10 | 2003-04-11 | 2003-04-12 | 2003-04-13 | 2003-04-14 | 2 Week | 2003-04-15 | 2003-04-16 | 2003-04-17 | 2003-04-18 | 2003-04-19 | 2003-04-20 | 2003-04-21 | 3 week | 2003-04-22 | 2003-04-23 | 2003-04-24 | 2003-04-25 | 2003-04-26 | 2003-04-27 | 2003-04-28 | 2003-04-29 | 2003-04-30 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 143685.9 | 143585.6 | 143485.8 | 143435.7 | 143385.3 | 143285.9 | 143186 | 1004050.2 | 144968.2 | 144868.4 | 144768.1 | 144717.9 | 144667.7 | 144567.4 | 144467.6 | 1013025.3 | 145832.7 | 145732.6 | 145632.3 | 145582.1 | 145531.9 | 145431.6 | 145331.8 | 1019075 | 114253.4 | 114278.1 | 114378.2 | 114478.5 | 114227.4 | 113977.1 | 114077.4 | 114177.5 | 114202.2 | 1028049.8 | 4064200.3
Coal Audited (kgs) | 20251 | 19099 | 20624 | 20308 | 19726 | 19081 | 19266 | 138355 | 20560 | 19240 | 19284 | 19688 | 20035 | 20009 | 19679 | 138495 | 20766 | 20749 | 20727 | 20925 | 20653 | 20318 | 20710 | 144848 | 16919 | 15768 | 16055 | 15842 | 16909 | 17289 | 16345 | 16469 | 15824 | 147420 | 569118
Actual Coal Consumed (Kgs) | 19643.47 | 18526.03 | 20005.28 | 19698.76 | 19134.22 | 18508.57 | 18688.02 | 134204.35 | 19943.2 | 18662.8 | 18705.48 | 19097.36 | 19433.95 | 19408.73 | 19088.63 | 134340.15 | 20143.02 | 20126.53 | 20105.19 | 20297.25 | 20033.41 | 19708.46 | 20088.7 | 140502.56 | 16411.43 | 15294.96 | 15573.35 | 15366.74 | 16401.73 | 16770.33 | 15854.65 | 15974.93 | 15349.28 | 142997.4 | 552044.46
Feed Water Temp. deg. C | 75 | 76 | 72 | 71 | 76 | 75 | 73 | 74 | 73 | 74 | 75 | 75 | 76 | 76 | 76 | 75 | 73 | 75 | 74 | 71 | 72 | 74 | 72 | 73 | 74 | 72 | 75 | 73 | 76 | 74 | 73 | 75 | 74 | 74 | 74
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 147996.477 | 147893.168 | 147790.374 | 147738.771 | 147686.859 | 147584.477 | 147481.58 | 1034171.706 | 149317.246 | 149214.452 | 149111.143 | 149059.437 | 149007.731 | 148904.422 | 148801.628 | 1043416.059 | 150207.681 | 150104.578 | 150001.269 | 149949.563 | 149897.857 | 149794.548 | 149691.754 | 1049647.25 | 117681.002 | 117706.443 | 117809.546 | 117912.855 | 117654.222 | 117396.413 | 117499.722 | 117602.825 | 117628.266 | 1058891.294 | 4186126.309
MONTH -MAY -2003
Particulars | 2003-05-02 | 2003-05-03 | 2003-05-04 | 2003-05-05 | 2003-05-06 | 2003-05-07 | 2003-05-08 | 1 week | 2003-05-09 | 2003-05-10 | 2003-05-11 | 2003-05-12 | 2003-05-13 | 2003-05-14 | 2003-05-15 | 2 Week | 2003-05-16 | 2003-05-17 | 2003-05-18 | 2003-05-19 | 2003-05-20 | 2003-05-21 | 2003-05-22 | 3 week | 2003-05-23 | 2003-05-24 | 2003-05-25 | 2003-05-26 | 2003-05-27 | 2003-05-28 | 2003-05-29 | 2003-05-30 | 2003-05-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 114268.7 | 114168.2 | 114068.5 | 114017.9 | 113967.3 | 113867.6 | 113767.1 | 798125.3 | 114140.1 | 114039.6 | 113939.9 | 113889.3 | 113838.7 | 113739 | 113638.5 | 797225.1 | 114711.5 | 114611.1 | 114511.3 | 114460.7 | 114410.1 | 114310.4 | 114209.9 | 801225 | 90383.3 | 90282.9 | 90183.1 | 90132.5 | 90081.9 | 89982.1 | 85881.7 | 86100.1 | 87297 | 800324.6 | 3196900
Coal Audited (kgs) | 16725 | 16398 | 16480 | 16369 | 16820 | 16483 | 16359 | 115634 | 16755 | 16428 | 16509 | 16398 | 16848 | 16513 | 16389 | 115840 | 16725 | 16398 | 16480 | 16369 | 16820 | 16483 | 16359 | 115634 | 13077 | 12750 | 12935 | 12722 | 12964 | 12938 | 12711 | 12936 | 12803 | 115836 | 462944
Actual Coal Consumed (Kgs) | 16223.25 | 15906.06 | 15985.6 | 15877.93 | 16315.4 | 15988.51 | 15868.23 | 112164.98 | 16252.35 | 15935.16 | 16013.73 | 15906.06 | 16342.56 | 16017.61 | 15897.33 | 112364.8 | 16223.25 | 15906.06 | 15985.6 | 15877.93 | 16315.4 | 15988.51 | 15868.23 | 112164.98 | 12684.69 | 12367.5 | 12546.95 | 12340.34 | 12575.08 | 12549.86 | 12329.67 | 12547.92 | 12418.91 | 112360.92 | 449055.68
Feed Water Temp. deg. C | 71 | 70 | 72 | 72 | 71 | 70 | 71 | 71 | 71 | 74 | 73 | 74 | 72 | 73 | 74 | 73 | 71 | 70 | 72 | 73 | 73 | 72 | 73 | 72 | 72 | 74 | 73 | 71 | 72 | 70 | 72 | 71 | 73 | 72 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 117696.761 | 117593.246 | 117490.555 | 117438.437 | 117386.319 | 117283.628 | 117180.113 | 822069.059 | 117564.303 | 117460.788 | 117358.097 | 117305.979 | 117253.861 | 117151.17 | 117047.655 | 821141.853 | 118152.845 | 118049.433 | 117946.639 | 117894.521 | 117842.403 | 117739.712 | 117636.197 | 825261.75 | 93094.799 | 92991.387 | 92888.593 | 92836.475 | 92784.357 | 92681.563 | 88458.151 | 88683.103 | 89915.91 | 824334.338 | 3292807
MONTH -JUNE -2003
Particulars | 2003-06-01 | 2003-06-02 | 2003-06-03 | 2003-06-04 | 2003-06-05 | 2003-06-06 | 2003-06-07 | 1 week | 2003-06-08 | 2003-06-09 | 2003-06-10 | 2003-06-11 | 2003-06-12 | 2003-06-13 | 2003-06-14 | 2 Week | 2003-06-15 | 2003-06-16 | 2003-06-17 | 2003-06-18 | 2003-06-19 | 2003-06-20 | 2003-06-21 | 3 week | 2003-06-22 | 2003-06-23 | 2003-06-24 | 2003-06-25 | 2003-06-26 | 2003-06-27 | 2003-06-28 | 2003-06-29 | 2003-06-30 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 118659.9 | 128559.4 | 108459.7 | 118409.1 | 128358.5 | 118258.8 | 128158.3 | 848863.7 | 113098.2 | 123997.7 | 123898 | 132847.4 | 124796.8 | 133717.9 | 132596.6 | 884952.6 | 135107.4 | 135986.2 | 133907.8 | 132856.8 | 132806 | 132706.3 | 132605.8 | 935976.3 | 103477.2 | 103501.9 | 103602 | 103702.3 | 103451.2 | 103200.9 | 103301.2 | 98401.3 | 96426 | 919064 | 3588856.6
Coal Audited (kgs) | 18603 | 18276 | 18358 | 18247 | 18698 | 18361 | 18237 | 128780 | 18633 | 18306 | 18387 | 18276 | 18726 | 18391 | 18267 | 128986 | 18603 | 18276 | 18358 | 18247 | 18698 | 18361 | 18237 | 128780 | 14537 | 14210 | 14395 | 14182 | 14424 | 14398 | 14171 | 14396 | 14261 | 128974 | 515520
Actual Coal Consumed (Kgs) | 18044.91 | 17727.72 | 17807.26 | 17699.59 | 18137.06 | 17810.17 | 17689.89 | 124916.6 | 18074.01 | 17756.82 | 17835.39 | 17727.72 | 18164.22 | 17839.27 | 17718.99 | 125116.42 | 18044.91 | 17727.72 | 17807.26 | 17699.59 | 18137.06 | 17810.17 | 17689.89 | 124916.6 | 14100.89 | 13783.7 | 13963.15 | 13756.54 | 13991.28 | 13966.06 | 13745.87 | 13964.12 | 13833.17 | 125104.78 | 500054.4
Feed Water Temp. deg. C | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 74 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 122219.697 | 132416.182 | 111713.491 | 121961.373 | 132209.255 | 121806.564 | 132003.049 | 874329.611 | 116491.146 | 127717.631 | 127614.94 | 136832.822 | 128540.704 | 137729.437 | 136574.498 | 911501.178 | 139160.622 | 140065.786 | 137925.034 | 136842.504 | 136790.18 | 136687.489 | 136583.974 | 964055.589 | 106581.516 | 106606.957 | 106710.06 | 106813.369 | 106554.736 | 106296.927 | 106400.236 | 101353.339 | 99318.78 | 946635.92 | 3696522.298
MONTH -JULY -2003
Particulars | 2003-07-01 | 2003-07-02 | 2003-07-03 | 2003-07-04 | 2003-07-05 | 2003-07-06 | 2003-07-07 | 1 week | 2003-07-08 | 2003-07-09 | 2003-07-10 | 2003-07-11 | 2003-07-12 | 2003-07-13 | 2003-07-14 | 2 Week | 2003-07-15 | 2003-07-16 | 2003-07-17 | 2003-07-18 | 2003-07-19 | 2003-07-20 | 2003-07-21 | 3 week | 2003-07-22 | 2003-07-23 | 2003-07-24 | 2003-07-25 | 2003-07-26 | 2003-07-27 | 2003-07-28 | 2003-07-29 | 2003-07-30 | 2003-07-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 143773.7 | 143672.1 | 143581.5 | 143492.8 | 143404.1 | 143313.5 | 143211.9 | 1004449.6 | 145098.8 | 144997.2 | 144906.6 | 144817.9 | 144729.2 | 144638.6 | 144537 | 1013725.3 | 145783 | 145681.4 | 145590.8 | 145502.1 | 145413.4 | 145322.8 | 145221.2 | 1018514.7 | 103131.9 | 103030.3 | 102939.7 | 102851 | 102762.3 | 102671.7 | 102570.1 | 102884.2 | 102517.7 | 102151.7 | 1027510.6 | 4064200.2
Coal Audited (kgs) | 20283 | 19131 | 19634 | 20340 | 19758 | 19113 | 19298 | 137557 | 20592 | 19272 | 19316 | 19720 | 20067 | 20041 | 19711 | 138719 | 20798 | 20781 | 20759 | 20957 | 20685 | 20350 | 20742 | 145072 | 14844 | 14693 | 14980 | 14767 | 14834 | 14214 | 14270 | 14394 | 15752 | 15022 | 147770 | 569118
Actual Coal Consumed (Kgs) | 19674.51 | 18557.07 | 19044.98 | 19729.8 | 19165.26 | 18539.61 | 18719.06 | 133430.29 | 19974.24 | 18693.84 | 18736.52 | 19128.4 | 19464.99 | 19439.77 | 19119.67 | 134557.43 | 20174.06 | 20157.57 | 20136.23 | 20328.29 | 20064.45 | 19739.5 | 20119.74 | 140719.84 | 14398.68 | 14252.21 | 14530.6 | 14323.99 | 14388.98 | 13787.58 | 13841.9 | 13962.18 | 15279.44 | 14571.34 | 143336.9 | 552044.46
Feed Water Temp. deg. C | 74 | 73 | 75 | 72 | 74 | 76 | 74 | 74 | 73 | 75 | 72 | 73 | 71 | 74 | 73 | 73 | 75 | 75 | 74 | 73 | 76 | 77 | 75 | 75 | 74 | 75 | 73 | 72 | 76 | 74 | 75 | 73 | 75 | 73 | 74 | 74
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 148086.911 | 147982.263 | 147888.945 | 147797.584 | 147706.223 | 147612.905 | 147508.257 | 1034583.088 | 149451.764 | 149347.116 | 149253.798 | 149162.437 | 149071.076 | 148977.758 | 148873.11 | 1044137.059 | 150156.49 | 150051.842 | 149958.524 | 149867.163 | 149775.802 | 149682.484 | 149577.836 | 1049070.141 | 106225.857 | 106121.209 | 106027.891 | 105936.53 | 105845.169 | 105751.851 | 105647.203 | 105970.726 | 105593.231 | 105216.251 | 1058335.918 | 4186126.206
MONTH -AUGUST -2003
Particulars | 2003-08-01 | 2003-08-02 | 2003-08-03 | 2003-08-04 | 2003-08-05 | 2003-08-06 | 2003-08-07 | 1 week | 2003-08-08 | 2003-08-09 | 2003-08-10 | 2003-08-11 | 2003-08-12 | 2003-08-13 | 2003-08-14 | 2 Week | 2003-08-15 | 2003-08-16 | 2003-08-17 | 2003-08-18 | 2003-08-19 | 2003-08-23 | 2003-08-24 | 3 week | 2003-08-25 | 2003-08-26 | 2003-08-27 | 2003-08-28 | 2003-08-29 | 2003-08-30 | 2003-08-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 122940.2 | 122838.6 | 122748 | 122659.3 | 122570.6 | 122480 | 122378.4 | 858615.1 | 122702.8 | 122601.2 | 122510.6 | 122421.9 | 122333.2 | 122242.6 | 122141 | 856953.3 | 123131.6 | 123030 | 122939.4 | 122850.7 | 122762 | 122671.4 | 122569.8 | 859954.9 | 90131.4 | 88767 | 88676.4 | 88587.7 | 88499 | 88408.4 | 88306.8 | 621376.7 | 3196900
Coal Audited (kgs) | 17957 | 17640 | 17719 | 17612 | 18045 | 17722 | 17602 | 124297 | 17985 | 17668 | 17747 | 17640 | 18075 | 17750 | 17630 | 124495 | 17957 | 17640 | 17719 | 17612 | 18045 | 17722 | 17602 | 124297 | 12922 | 12905 | 12684 | 12877 | 12812 | 12788 | 12867 | 89855 | 462944
Actual Coal Consumed (Kgs) | 17418.29 | 17110.8 | 17187.43 | 17083.64 | 17503.65 | 17190.34 | 17073.94 | 120568.09 | 17445.45 | 17137.96 | 17214.59 | 17110.8 | 17532.75 | 17217.5 | 17101.1 | 120760.15 | 17418.29 | 17110.8 | 17187.43 | 17083.64 | 17503.65 | 17190.34 | 17073.94 | 120568.09 | 12534.34 | 12517.85 | 12303.48 | 12490.69 | 12427.64 | 12404.36 | 12480.99 | 87159.35 | 449055.68
Feed Water Temp. deg. C | 72 | 71 | 73 | 73 | 74 | 71 | 70 | 72 | 71 | 75 | 72 | 73 | 73 | 74 | 73 | 73 | 72 | 74 | 73 | 74 | 75 | 75 | 75 | 74 | 73 | 71 | 74 | 74 | 72 | 73 | 74 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 126628.406 | 126523.758 | 126430.44 | 126339.079 | 126247.718 | 126154.4 | 126049.752 | 884373.553 | 126383.884 | 126279.236 | 126185.918 | 126094.557 | 126003.196 | 125909.878 | 125805.23 | 882661.899 | 126825.548 | 126720.9 | 126627.582 | 126536.221 | 126444.86 | 126351.542 | 126246.894 | 885753.547 | 92835.342 | 91430.01 | 91336.692 | 91245.331 | 91153.97 | 91060.652 | 90956.004 | 640018.001 | 3292807
MONTH -SEPTEMBER -2003
Particulars | 2003-09-01 | 2003-09-02 | 2003-09-03 | 2003-09-04 | 2003-09-05 | 2003-09-06 | 2003-09-07 | 1 week | 2003-09-08 | 2003-09-09 | 2003-09-10 | 2003-09-11 | 2003-09-12 | 2003-09-13 | 2003-09-14 | 2 Week | 2003-09-15 | 2003-09-16 | 2003-09-17 | 2003-09-18 | 2003-09-19 | 2003-09-20 | 2003-09-21 | 3 week | 2003-09-22 | 2003-09-23 | 2003-09-24 | 2003-09-25 | 2003-09-26 | 2003-09-27 | 2003-09-28 | 2003-09-29 | 2003-09-30 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 128813.5 | 128711.9 | 128621.3 | 128532.6 | 128443.9 | 128353.3 | 128251.7 | 899728.2 | 133261.5 | 133159.9 | 133069.3 | 132980.6 | 132891.9 | 132801.3 | 132699.7 | 930864.2 | 132890 | 132788.4 | 132697.8 | 132609.1 | 132520.4 | 132429.8 | 132328.2 | 928263.7 | 93470 | 93494.7 | 93594.8 | 93695.4 | 93444.4 | 93193.7 | 93294 | 93394.1 | 93418.8 | 840999.9 | 3599856
Coal Audited (kgs) | 18594 | 18280 | 18359 | 18252 | 18690 | 18362 | 18242 | 128779 | 18626 | 18309 | 18388 | 18281 | 18716 | 18391 | 18271 | 128982 | 18597 | 18280 | 18359 | 18252 | 18687 | 18362 | 18242 | 128779 | 14530 | 14213 | 14392 | 14185 | 14423 | 14395 | 14175 | 14393 | 14274 | 128980 | 515520
Actual Coal Consumed (Kgs) | 18036.18 | 17731.6 | 17808.23 | 17704.44 | 18129.3 | 17811.14 | 17694.74 | 124915.63 | 18067.22 | 17759.73 | 17836.36 | 17732.57 | 18154.52 | 17839.27 | 17722.87 | 125112.54 | 18039.09 | 17731.6 | 17808.23 | 17704.44 | 18126.39 | 17811.14 | 17694.74 | 124915.63 | 14094.1 | 13786.61 | 13960.24 | 13759.45 | 13990.31 | 13963.15 | 13749.75 | 13961.21 | 13845.78 | 125110.6 | 500054.4
Feed Water Temp. deg. C | 71 | 72 | 74 | 74 | 72 | 71 | 70 | 72 | 71 | 75 | 74 | 73 | 73 | 73 | 72 | 73 | 75 | 72 | 75 | 73 | 75 | 74 | 74 | 74 | 71 | 72 | 73 | 75 | 73 | 74 | 72 | 73 | 74 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 132677.905 | 132573.257 | 132479.939 | 132388.578 | 132297.217 | 132203.899 | 132099.251 | 926720.046 | 137259.345 | 137154.697 | 137061.379 | 136970.018 | 136878.657 | 136785.339 | 136680.691 | 958790.126 | 136876.7 | 136772.052 | 136678.734 | 136587.373 | 136496.012 | 136402.694 | 136298.046 | 956111.611 | 96274.1 | 96299.541 | 96402.644 | 96506.262 | 96247.732 | 95989.511 | 96092.82 | 96195.923 | 96221.364 | 866229.897 | 3707851.68
MONTH -OCTOBER -2003
Particulars | 2003-10-01 | 2003-10-02 | 2003-10-03 | 2003-10-04 | 2003-10-05 | 2003-10-06 | 2003-10-07 | 1 week | 2003-10-08 | 2003-10-09 | 2003-10-10 | 2003-10-11 | 2003-10-12 | 2003-10-13 | 2003-10-14 | 2 Week | 2003-10-15 | 2003-10-16 | 2003-10-17 | 2003-10-18 | 2003-10-19 | 2003-10-20 | 2003-10-21 | 3 week | 2003-10-22 | 2003-10-23 | 2003-10-24 | 2003-10-25 | 2003-10-26 | 2003-10-27 | 2003-10-28 | 2003-10-29 | 2003-10-30 | 2003-10-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 143813.8 | 143712.2 | 143621.6 | 143532.9 | 143444.2 | 143353.6 | 143252 | 1004730.3 | 145126.2 | 145024.6 | 144934 | 144845.3 | 144756.6 | 144666 | 144564.4 | 1013917.1 | 145781.6 | 145680 | 145589.4 | 145500.7 | 145412 | 145321.4 | 145219.8 | 1018504.9 | 103085.7 | 102984.1 | 102893.5 | 102804.8 | 102716.1 | 102625.5 | 102523.9 | 102838 | 102471.5 | 102105 | 1027048.1 | 4064200.4
Coal Audited (kgs) | 20511 | 20194 | 20273 | 20166 | 20604 | 20276 | 20156 | 142180 | 20440 | 20240 | 20340 | 20240 | 20540 | 20340 | 20240 | 142380 | 20511 | 20194 | 20273 | 20169 | 20601 | 20276 | 20156 | 142180 | 14338 | 14321 | 14100 | 14293 | 14228 | 14200 | 14289 | 14101 | 14366 | 14142 | 142378 | 569118
Actual Coal Consumed (Kgs) | 19895.67 | 19588.18 | 19664.81 | 19561.02 | 19985.88 | 19667.72 | 19551.32 | 137914.6 | 19826.8 | 19632.8 | 19729.8 | 19632.8 | 19923.8 | 19729.8 | 19632.8 | 138108.6 | 19895.67 | 19588.18 | 19664.81 | 19563.93 | 19982.97 | 19667.72 | 19551.32 | 137914.6 | 13907.86 | 13891.37 | 13677 | 13864.21 | 13801.16 | 13774 | 13860.33 | 13677.97 | 13935.02 | 13717.74 | 138106.66 | 552044.46
Feed Water Temp. deg. C | 70 | 72 | 73 | 73 | 71 | 73 | 72 | 72 | 71 | 70 | 70 | 73 | 72 | 71 | 70 | 71 | 73 | 74 | 73 | 71 | 72 | 75 | 73 | 73 | 70 | 72 | 73 | 74 | 72 | 71 | 70 | 73 | 73 | 72 | 72 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 148128.214 | 148023.566 | 147930.248 | 147838.887 | 147747.526 | 147654.208 | 147549.56 | 1034872.209 | 149479.986 | 149375.338 | 149282.02 | 149190.659 | 149099.298 | 149005.98 | 148901.332 | 1044334.613 | 150155.048 | 150050.4 | 149957.082 | 149865.721 | 149774.36 | 149681.042 | 149576.394 | 1049060.047 | 106178.271 | 106073.623 | 105980.305 | 105888.944 | 105797.583 | 105704.265 | 105599.617 | 105923.14 | 105545.645 | 105168.15 | 1057859.543 | 4186126.412
MONTH -NOVEMBER -2003
Particulars | 2003-11-01 | 2003-11-02 | 2003-11-03 | 2003-11-04 | 2003-11-05 | 2003-11-06 | 2003-11-07 | 1 week | 2003-11-08 | 2003-11-09 | 2003-11-10 | 2003-11-11 | 2003-11-12 | 2003-11-13 | 2003-11-14 | 2 Week | 2003-11-15 | 2003-11-16 | 2003-11-17 | 2003-11-18 | 2003-11-19 | 2003-11-20 | 2003-11-21 | 3 week | 2003-11-22 | 2003-11-23 | 2003-11-24 | 2003-11-25 | 2003-11-26 | 2003-11-27 | 2003-11-28 | 2003-11-29 | 2003-11-30 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 114396.2 | 114294.6 | 114204 | 114115.3 | 114026.6 | 113936 | 113834.4 | 798807.1 | 114211.2 | 114109.6 | 114019 | 113930.3 | 113841.6 | 113751 | 113649.4 | 797512.1 | 114709.5 | 114607.9 | 114517.3 | 114428.6 | 114339.9 | 114249.3 | 114147.7 | 801000.2 | 88867.9 | 88892.6 | 88992.7 | 89093 | 88842.3 | 88591.6 | 88691.9 | 88792 | 88816.7 | 799580.7 | 3196900.1
Coal Audited (kgs) | 16713 | 16406 | 16482 | 16378 | 16800 | 16485 | 16369 | 115633 | 16741 | 16434 | 16510 | 16407 | 16828 | 16513 | 16397 | 115830 | 16713 | 16406 | 16482 | 16378 | 16803 | 16485 | 16369 | 115636 | 13064 | 12757 | 12930 | 12729 | 12956 | 12933 | 12720 | 12932 | 12824 | 115845 | 462944
Actual Coal Consumed (Kgs) | 16211.61 | 15913.82 | 15987.54 | 15886.66 | 16296 | 15990.45 | 15877.93 | 112164.01 | 16238.77 | 15940.98 | 16014.7 | 15914.79 | 16323.16 | 16017.61 | 15905.09 | 112355.1 | 16211.61 | 15913.82 | 15987.54 | 15886.66 | 16298.91 | 15990.45 | 15877.93 | 112166.92 | 12672.08 | 12374.29 | 12542.1 | 12347.13 | 12567.32 | 12545.01 | 12338.4 | 12544.04 | 12439.28 | 112369.65 | 449055.68
Feed Water Temp. deg. C | 74 | 75 | 73 | 72 | 75 | 75 | 74 | 74 | 73 | 74 | 72 | 71 | 74 | 73 | 74 | 73 | 74 | 76 | 76 | 75 | 74 | 73 | 76 | 76 | 74 | 73 | 72 | 75 | 71 | 74 | 75 | 71 | 72 | 73 | 74
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 117828.086 | 117723.438 | 117630.12 | 117538.759 | 117447.398 | 117354.08 | 117249.432 | 822771.313 | 117637.536 | 117532.888 | 117439.57 | 117348.209 | 117256.848 | 117163.53 | 117058.882 | 821437.463 | 118150.785 | 118046.137 | 117952.819 | 117861.458 | 117770.097 | 117676.779 | 117572.131 | 825030.206 | 91533.937 | 91559.378 | 91662.481 | 91765.79 | 91507.569 | 91249.348 | 91352.657 | 91455.76 | 91481.201 | 823568.121 | 3292807.103
MONTH -DECEMBER -2003
Particulars | 2003-12-01 | 2003-12-02 | 2003-12-03 | 2003-12-04 | 2003-12-05 | 2003-12-06 | 2003-12-07 | 1 week | 2003-12-08 | 2003-12-09 | 2003-12-10 | 2003-12-11 | 2003-12-12 | 2003-12-13 | 2003-12-14 | 2 Week | 2003-12-15 | 2003-12-16 | 2003-12-17 | 2003-12-18 | 2003-12-19 | 2003-12-20 | 2003-12-21 | 3 week | 2003-12-22 | 2003-12-23 | 2003-12-24 | 2003-12-25 | 2003-12-26 | 2003-12-27 | 2003-12-28 | 2003-12-29 | 2003-12-30 | 2003-12-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 128813.5 | 128711.9 | 128621.3 | 128532.6 | 128443.9 | 128353.3 | 128251.7 | 899728.2 | 133261.5 | 133159.9 | 133069.3 | 132980.6 | 132891.9 | 132801.3 | 132699.7 | 930864.2 | 132994.6 | 132893 | 132802.4 | 132713.7 | 132625 | 132534.4 | 132432.8 | 928995.9 | 84407.7 | 84306.1 | 84215.5 | 84126.8 | 84038.1 | 83947.5 | 83845.9 | 84160 | 83793.5 | 83427 | 840268.1 | 3599856.4
Coal Audited (kgs) | 18591 | 18283 | 18360 | 18256 | 18680 | 18363 | 18246 | 128779 | 18619 | 18311 | 18388 | 18284 | 18705 | 18391 | 18275 | 128973 | 18591 | 18283 | 18360 | 18258 | 18678 | 18363 | 18246 | 128779 | 12995 | 12979 | 12764 | 12952 | 12889 | 12863 | 12942 | 12764 | 13031 | 12810 | 128989 | 515520
Actual Coal Consumed (Kgs) | 18033.27 | 17734.51 | 17809.2 | 17708.32 | 18119.6 | 17812.11 | 17698.62 | 124915.63 | 18060.43 | 17761.67 | 17836.36 | 17735.48 | 18143.85 | 17839.27 | 17726.75 | 125103.81 | 18033.27 | 17734.51 | 17809.2 | 17710.26 | 18117.66 | 17812.11 | 17698.62 | 124915.63 | 12605.15 | 12589.63 | 12381.08 | 12563.44 | 12502.33 | 12477.11 | 12553.74 | 12381.08 | 12640.07 | 12425.7 | 125119.33 | 500054.4
Feed Water Temp. deg. C | 72 | 70 | 71 | 73 | 73 | 74 | 71 | 72 | 71 | 72 | 70 | 72 | 74 | 72 | 73 | 72 | 72 | 71 | 71 | 71 | 74 | 72 | 73 | 72 | 72 | 72 | 70 | 73 | 71 | 74 | 72 | 70 | 73 | 73 | 72 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 132677.905 | 132573.257 | 132479.939 | 132388.578 | 132297.217 | 132203.899 | 132099.251 | 926720.046 | 137259.345 | 137154.697 | 137061.379 | 136970.018 | 136878.657 | 136785.339 | 136680.691 | 958790.126 | 136984.438 | 136879.79 | 136786.472 | 136695.111 | 136603.75 | 136510.432 | 136405.784 | 956865.777 | 86939.931 | 86835.283 | 86741.965 | 86650.604 | 86559.243 | 86465.925 | 86361.277 | 86684.8 | 86307.305 | 85929.81 | 865476.143 | 3707852.092
MONTH -JANUARY -2004
Particulars | 2004-01-01 | 2004-01-02 | 2004-01-03 | 2004-01-04 | 2004-01-05 | 2004-01-06 | 2004-01-07 | 1 week | 2004-01-08 | 2004-01-09 | 2004-01-10 | 2004-01-11 | 2004-01-12 | 2004-01-13 | 2004-01-14 | 2 Week | 2004-01-15 | 2004-01-16 | 2004-01-17 | 2004-01-18 | 2004-01-19 | 2004-01-20 | 2004-01-21 | 3 week | 2004-01-22 | 2004-01-23 | 2004-01-24 | 2004-01-25 | 2004-01-26 | 2004-01-27 | 2004-01-28 | 2004-01-29 | 2004-01-30 | 2004-01-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 156707.1 | 155282.6 | 155919.2 | 155264.7 | 157346.9 | 155918.5 | 155252.5 | 1091691.5 | 154480.6 | 155468.3 | 151300.6 | 153058.2 | 157532.4 | 151299.9 | 155438.2 | 1078578.2 | 156707.1 | 150504 | 153519.9 | 155264.5 | 154927.4 | 151119.9 | 155252.5 | 1077295.3 | 106037.3 | 109925.8 | 108612.4 | 108216.4 | 105396.9 | 107580.2 | 109895.7 | 108685.9 | 106529.3 | 108649.1 | 1079529 | 4327094
Coal Audited (kgs) | 24935 | 24612 | 24699 | 24594 | 25027 | 24698 | 24582 | 173147 | 24964 | 24641 | 24728 | 24622 | 25054 | 24727 | 24611 | 173347 | 24935 | 24612 | 24699 | 24596 | 25025 | 24698 | 24582 | 173147 | 17435 | 17412 | 17199 | 17394 | 17325 | 17301 | 17382 | 17273 | 17397 | 17241 | 173359 | 693000
Actual Coal Consumed (Kgs) | 24186.95 | 23873.64 | 23958.03 | 23856.18 | 24276.19 | 23957.06 | 23844.54 | 167952.59 | 24215.08 | 23901.77 | 23986.16 | 23883.34 | 24302.38 | 23985.19 | 23872.67 | 168146.59 | 24186.95 | 23873.64 | 23958.03 | 23858.12 | 24274.25 | 23957.06 | 23844.54 | 167952.59 | 16911.95 | 16889.64 | 16683.03 | 16872.18 | 16805.25 | 16781.97 | 16860.54 | 16754.81 | 16875.09 | 16723.77 | 168158.23 | 672210
Feed Water Temp. deg. C | 72 | 71 | 73 | 73 | 74 | 71 | 70 | 72 | 71 | 75 | 72 | 73 | 73 | 74 | 73 | 73 | 72 | 74 | 73 | 74 | 75 | 75 | 75 | 74 | 73 | 71 | 74 | 74 | 72 | 75 | 73 | 73 | 72 | 73 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 161408.313 | 159941.078 | 160596.776 | 159922.641 | 162067.307 | 160596.055 | 159910.075 | 1124442.245 | 159115.018 | 160132.349 | 155839.618 | 157649.946 | 162258.372 | 155838.897 | 160101.346 | 1110935.546 | 161408.313 | 155019.12 | 158125.497 | 159922.435 | 159575.222 | 155653.497 | 159910.075 | 1109614.159 | 109218.419 | 113223.574 | 111870.772 | 111462.892 | 108558.807 | 110807.606 | 113192.571 | 111946.477 | 109725.179 | 111908.573 | 1111914.87 | 4456906.82
MONTH -FEBRUARY -2004
Particulars | 2004-02-01 | 2004-02-02 | 2004-02-03 | 2004-02-04 | 2004-02-05 | 2004-02-06 | 2004-02-07 | 1 week | 2004-02-08 | 2004-02-09 | 2004-02-10 | 2004-02-11 | 2004-02-12 | 2004-02-13 | 2004-02-14 | 2 Week | 2004-02-15 | 2004-02-16 | 2004-02-17 | 2004-02-18 | 2004-02-19 | 2004-02-20 | 2004-02-21 | 3 week | 2004-02-22 | 2004-02-23 | 2004-02-24 | 2004-02-25 | 2004-02-26 | 2004-02-27 | 2004-02-28 | 2004-02-29 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 170216.7 | 168799.9 | 169428.2 | 168774.2 | 170855.8 | 169430.6 | 168760.8 | 1186266.2 | 167782.4 | 168985.6 | 164393.9 | 166359.9 | 171041.5 | 164396.3 | 168946.5 | 1171906.1 | 170216.7 | 163605.6 | 166821 | 168774.2 | 168228.6 | 164216.3 | 168760.8 | 1170623.2 | 144608.2 | 147778.7 | 148407.8 | 146757 | 143375.2 | 146127 | 149040.8 | 147758.8 | 1173853.5 | 4702649
Coal Audited (kgs) | 27079 | 26762 | 26841 | 26734 | 27168 | 26844 | 26723 | 188151 | 27107 | 26790 | 26869 | 26765 | 27197 | 26872 | 26752 | 188352 | 27079 | 26762 | 26841 | 26734 | 27167 | 26844 | 26724 | 188151 | 23744 | 23427 | 23506 | 23599 | 23570 | 23509 | 23584 | 23407 | 188346 | 753000
Actual Coal Consumed (Kgs) | 26266.63 | 25959.14 | 26035.77 | 25931.98 | 26352.96 | 26038.68 | 25921.31 | 182506.47 | 26293.79 | 25986.3 | 26062.93 | 25962.05 | 26381.09 | 26065.84 | 25949.44 | 182701.44 | 26266.63 | 25959.14 | 26035.77 | 25931.98 | 26351.99 | 26038.68 | 25922.28 | 182506.47 | 23031.68 | 22724.19 | 22800.82 | 22891.03 | 22862.9 | 22803.73 | 22876.48 | 22704.79 | 182695.62 | 730410
Feed Water Temp. deg. C | 74 | 74 | 73 | 72 | 73 | 72 | 73 | 73 | 71 | 72 | 70 | 73 | 74 | 73 | 71 | 72 | 74 | 75 | 76 | 73 | 72 | 73 | 75 | 74 | 73 | 71 | 72 | 74 | 74 | 73 | 74 | 73 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 175323.201 | 173863.897 | 174511.046 | 173837.426 | 175981.474 | 174513.518 | 173823.624 | 1221854.186 | 172815.872 | 174055.168 | 169325.717 | 171350.697 | 176172.745 | 169328.189 | 174014.895 | 1207063.283 | 175323.201 | 168513.768 | 171825.63 | 173837.426 | 173275.458 | 169142.789 | 173823.624 | 1205741.896 | 148946.446 | 152212.061 | 152860.034 | 151159.71 | 147676.456 | 150510.81 | 153512.024 | 152191.564 | 1209069.105 | 4843728.47
MONTH -MARCH -2004
Particulars | 2004-03-01 | 2004-03-02 | 2004-03-03 | 2004-03-04 | 2004-03-05 | 2004-03-06 | 2004-03-07 | 1 week | 2004-03-08 | 2004-03-09 | 2004-03-10 | 2004-03-11 | 2004-03-12 | 2004-03-13 | 2004-03-14 | 2 Week | 2004-03-15 | 2004-03-16 | 2004-03-17 | 2004-03-18 | 2004-03-19 | 2004-03-20 | 2004-03-21 | 3 week | 2004-03-22 | 2004-03-23 | 2004-03-24 | 2004-03-25 | 2004-03-26 | 2004-03-27 | 2004-03-28 | 2004-03-29 | 2004-03-30 | 2004-03-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 176544.2 | 175127.4 | 175755.7 | 175101.7 | 177183.3 | 175758.1 | 175088.3 | 1230558.7 | 174012.6 | 175313.1 | 170526.7 | 172590.1 | 177369 | 170529.1 | 175274 | 1215614.6 | 176544.2 | 169738.4 | 173051.2 | 175101.7 | 174458.8 | 170349.1 | 175088.3 | 1214331.7 | 119495.7 | 123819.2 | 122497.5 | 121888.3 | 118854.8 | 121254.7 | 123780.1 | 122499.4 | 120062.1 | 122535.9 | 1216687.7 | 4877192.7
Coal Audited (kgs) | 28087 | 27761 | 27842 | 27734 | 28181 | 27845 | 27721 | 195171 | 28117 | 27791 | 27872 | 27762 | 28211 | 27875 | 27751 | 195379 | 28087 | 27761 | 27842 | 27734 | 28181 | 27845 | 27721 | 195171 | 19641 | 19624 | 19396 | 19595 | 19525 | 19502 | 19586 | 19397 | 19676 | 19437 | 195379 | 781100
Actual Coal Consumed (Kgs) | 27244.39 | 26928.17 | 27006.74 | 26901.98 | 27335.57 | 27009.65 | 26889.37 | 189315.87 | 27273.49 | 26957.27 | 27035.84 | 26929.14 | 27364.67 | 27038.75 | 26918.47 | 189517.63 | 27244.39 | 26928.17 | 27006.74 | 26901.98 | 27335.57 | 27009.65 | 26889.37 | 189315.87 | 19051.77 | 19035.28 | 18814.12 | 19007.15 | 18939.25 | 18916.94 | 18998.42 | 18815.09 | 19085.72 | 18853.89 | 189517.63 | 757667
Feed Water Temp. deg. C | 70 | 71 | 72 | 74 | 74 | 72 | 71 | 72 | 70 | 71 | 72 | 70 | 75 | 74 | 72 | 72 | 73 | 73 | 72 | 71 | 75 | 74 | 73 | 73 | 73 | 72 | 70 | 70 | 71 | 70 | 72 | 71 | 70 | 71 | 71 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 181840.526 | 180381.222 | 181028.371 | 180354.751 | 182498.799 | 181030.843 | 180340.949 | 1267475.461 | 179232.978 | 180572.493 | 175642.501 | 177767.803 | 182690.07 | 175644.973 | 180532.22 | 1252083.038 | 181840.526 | 174830.552 | 178242.736 | 180354.751 | 179692.564 | 175459.573 | 180340.949 | 1250761.651 | 123080.571 | 127533.776 | 126172.425 | 125544.949 | 122420.444 | 124892.341 | 127493.503 | 126174.382 | 123663.963 | 126211.977 | 1253188.331 | 5023508.481

## CER Estimation_03-04
Monitored Parameters for the year 2003-2004
Months | Quantity of Coal Used | Coal-Audited | Gross Calorific Value of Coal | Heat Energy Input | Steam Load | Steam Pressure | Steam Pressure | Steam Enthalpy | Feed water Load | Feed Water Temerature | Feed Water Enthalpy | Number of Truck Trips
Units | (tons) | (tons) | (kCal/kg) | (kCal) | (tons) | (Bar) | (kg/cm2) | (kCal) | (tons) | (°C) | (kCal)
April 2003 | 552.0445 | 569.118 | 5905 | 3259822536.3 | 4064.2003 | 8.83 | 9 | 2697332935.1939 | 4186.1263 | 74 | 309600179.1069 | 78 | Temperature | Feed Water Enthalpy
May 2003 | 449.0557 | 462.944 | 5566 | 2499443914.88 | 3196.9 | 8.83 | 9 | 2121722116.0388 | 3292.807 | 72 | 236940856.7157 | 0 | (0C) | (kJ/kg)
June 2003 | 500.0544 | 515.52 | 5654 | 2827307577.6 | 3588.8566 | 8.83 | 9 | 2381856304.3923 | 3696.5223 | 73 | 269690388.1462 | 3 | 64 | 267.79
July 2003 | 552.0445 | 569.118 | 5905 | 3259822536.3 | 4064.2002 | 8.83 | 9 | 2697332868.8258 | 4186.1262 | 74 | 309600171.4891 | 138 | 65 | 271.97
August 2003 | 449.0557 | 462.944 | 5566 | 2499443914.88 | 3196.9 | 8.83 | 9 | 2121722116.0388 | 3292.807 | 73 | 240236180.4773 | 79 | 66 | 276.16
September 2003 | 500.0544 | 515.52 | 5654 | 2827307577.6 | 3599.856 | 8.83 | 9 | 2389156398.3093 | 3707.8517 | 73 | 270516955.7096 | 0 | 67 | 280.34
October 2003 | 552.0445 | 569.118 | 5905 | 3259822536.3 | 4064.2004 | 8.83 | 9 | 2697333001.562 | 4186.1264 | 72 | 301221534.812 | 0 | 68 | 284.52
November 2003 | 449.0557 | 462.944 | 5566 | 2499443914.88 | 3196.9001 | 8.83 | 9 | 2121722182.4069 | 3292.8071 | 74 | 243531511.8565 | 0 | 72 | 301.27
December 2003 | 500.0544 | 515.52 | 5654 | 2827307577.6 | 3599.8564 | 8.83 | 9 | 2389156663.7817 | 3707.8521 | 72 | 266806299.6871 | 84 | 73 | 305.46
January 2004 | 672.21 | 693 | 5565 | 3740848650 | 4327.094 | 8.83 | 9 | 2871810515.8055 | 4456.9068 | 73 | 325166422.1984 | 4 | 74 | 309.65
February 2004 | 730.41 | 753 | 5565 | 4064731650 | 4702.649 | 8.83 | 9 | 3121059272.1911 | 4843.7285 | 73 | 353388105.3162 | 80
March 2004 | 757.667 | 781.1 | 5565 | 4216416855 | 4877.1927 | 8.83 | 9 | 3236900627.4118 | 5023.5085 | 72 | 371531819.7921 | 36
2003-2004 | 6663.7506 | 6869.846 | 5672.5 | 37781719241.34 | 46478.8057 | 8.83 | 9 | 30847105001.9579 | 47873.1699 | 72.9167 | 3498230425.3071 | 502
Computation of Emission Reductions for the year 2003-2004
Months | Output Enthalpy | Baseline Boiler Efficiency | Baseline Technical Losses | Boiler Efficiency | Technical Losses | Reduction in Losses | Coal Reduction | Fixed Carbon Content (C%) in Coal | Emission Co-efficienct of Coal | Emission Reductions
| (kCal) | (%) | (kCal) | (%) | (kCal) | (kCal) | (kgs) | ('%) | (kgCO2/kCal) | (tons)
April 2003 | 2387732756.087 | 53.9271 | 2039969074.0847 | 73.2473 | 872089780.213 | 1167879293.8717 | 197778.0345 | 0.5443 | 0.00033798 | 394.7188
May 2003 | 1884781259.3231 | 53.9271 | 1610270441.9628 | 75.408 | 614662655.5569 | 995607786.4059 | 178873.1201 | 0.52417 | 0.00034531 | 343.7897
June 2003 | 2112165916.2461 | 53.9271 | 1804537437.2377 | 74.7059 | 715141661.3539 | 1089395775.8838 | 192677.0032 | 0.51882 | 0.00033646 | 366.5407
July 2003 | 2387732697.3367 | 53.9271 | 2039969023.8911 | 73.2473 | 872089838.9633 | 1167879184.9277 | 197778.0161 | 0.54425 | 0.00033795 | 394.6825
August 2003 | 1881485935.5615 | 53.9271 | 1607455068.8665 | 75.2762 | 617957979.3185 | 989497089.5481 | 177775.2586 | 0.5242 | 0.00034532 | 341.6959
September 2003 | 2118639442.5996 | 53.9271 | 1810068120.4885 | 74.9349 | 708668135.0004 | 1101399985.4881 | 194800.1389 | 0.51882 | 0.00033646 | 370.5797
October 2003 | 2396111466.7501 | 53.9271 | 2047127459.2053 | 73.5044 | 863711069.5499 | 1183416389.6554 | 200409.2108 | 0.5442 | 0.00033792 | 399.8965
November 2003 | 1878190670.5503 | 53.9271 | 1604639745.9639 | 75.1443 | 621253244.3297 | 983386501.6342 | 176677.4168 | 0.5242 | 0.00034532 | 339.5858
December 2003 | 2122350364.0946 | 53.9271 | 1813238561.1783 | 75.0661 | 704957213.5054 | 1108281347.6729 | 196017.2175 | 0.5435 | 0.00035246 | 390.6296
January 2004 | 2546644093.6071 | 53.9271 | 2175735613.8015 | 68.0766 | 1194204556.3929 | 981531057.4086 | 176375.7516 | 0.524 | 0.00034525 | -
February 2004 | 2767671166.8749 | 53.9271 | 2364570981.9357 | 68.0899 | 1297060483.1251 | 1067510498.8106 | 191825.7859 | 0.5335 | 0.00035151 | -
March 2004 | 2865368807.6197 | 53.9271 | 2448039353.8555 | 67.9574 | 1351048047.3803 | 1064215088.6931 | 191233.6188 | 0.53827 | 0.00035466 | -
2003-2004 | 27348874576.6508 | 53.9271 | 23365620882.4714 | 72.8882 | 10432844664.6892 | 12900000000 | 2272220.5727 | 0.53185 | 0.00034388 | 3342.1192
Reduction in Losses (in GWhe) |  | 15 | = 15

## Daily Report 04-05
INDIAN RAYON AND INDUSTRIES LTD.,
UNIT : JAYA SHREE TEXTILES
RISHRA, HOOGHLY
BOILER DAILY REPORT
MONTH -APRIL -2004
Particulars | 2004-04-01 | 2004-04-02 | 2004-04-03 | 2004-04-04 | 2004-04-05 | 2004-04-06 | 2004-04-07 | 1 week | 2008-04-08 | 2008-04-09 | 2008-04-10 | 2008-04-11 | 2008-04-12 | 2008-04-13 | 2008-04-14 | 2 Week | 2008-04-15 | 2008-04-16 | 2008-04-17 | 2008-04-18 | 2008-04-19 | 2008-04-20 | 2008-04-21 | 3 week | 2008-04-22 | 2008-04-23 | 2008-04-24 | 2008-04-25 | 2008-04-26 | 2008-04-27 | 2008-04-28 | 2008-04-29 | 2008-04-30 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 174492.8 | 173076 | 173704.3 | 173050.3 | 175131.9 | 173706.7 | 173036.9 | 1216198.9 | 171992.7 | 173261.8 | 168538.7 | 170570.2 | 175317.8 | 168540.8 | 173222.7 | 1201444.7 | 174492.8 | 167750.1 | 171031.4 | 173050.3 | 172439 | 168360.8 | 173036.9 | 1200161.3 | 131845.4 | 134611 | 135889.3 | 132514.1 | 131204.5 | 133800.5 | 134571.9 | 135891.2 | 130521.8 | 1200849.7 | 4818654.6
Coal Audited (kgs) | 27763 | 27436 | 27518 | 27407 | 27856 | 27522 | 27397 | 192899 | 27792 | 27465 | 27546 | 27436 | 27885 | 27549 | 27426 | 193099 | 27763 | 27436 | 27518 | 27407 | 27856 | 27522 | 27397 | 192899 | 21662 | 21335 | 21520 | 21306 | 21548 | 21523 | 21296 | 21521 | 21382 | 193093 | 771990
Actual Coal Consumed (Kgs) | 26930.11 | 26612.92 | 26692.46 | 26584.79 | 27020.32 | 26696.34 | 26575.09 | 187112.03 | 26958.24 | 26641.05 | 26719.62 | 26612.92 | 27048.45 | 26722.53 | 26603.22 | 187306.03 | 26930.11 | 26612.92 | 26692.46 | 26584.79 | 27020.32 | 26696.34 | 26575.09 | 187112.03 | 21012.14 | 20694.95 | 20874.4 | 20666.82 | 20901.56 | 20877.31 | 20657.12 | 20875.37 | 20740.54 | 187300.21 | 748830.3
Feed Water Temp. deg. C | 70 | 71 | 72 | 71 | 70 | 72 | 71 | 71 | 72 | 73 | 74 | 72 | 72 | 70 | 71 | 72 | 73 | 74 | 72 | 71 | 75 | 73 | 73 | 73 | 71 | 70 | 72 | 73 | 72 | 73 | 72 | 73 | 72 | 72 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 179727.584 | 178268.28 | 178915.429 | 178241.809 | 180385.857 | 178917.901 | 178228.007 | 1252684.867 | 177152.481 | 178459.654 | 173594.861 | 175687.306 | 180577.334 | 173597.024 | 178419.381 | 1237488.041 | 179727.584 | 172782.603 | 176162.342 | 178241.809 | 177612.17 | 173411.624 | 178228.007 | 1236166.139 | 135800.762 | 138649.33 | 139965.979 | 136489.523 | 135140.635 | 137814.515 | 138609.057 | 139967.936 | 134437.454 | 1236875.191 | 4963214.238
MONTH -MAY -2004
Particulars | 2008-05-02 | 2008-05-03 | 2008-05-04 | 2008-05-05 | 2008-05-06 | 2008-05-07 | 2008-05-08 | 1 week | 2008-05-09 | 2008-05-10 | 2008-05-11 | 2008-05-12 | 2008-05-13 | 2008-05-14 | 2008-05-15 | 2 Week | 2008-05-16 | 2008-05-17 | 2008-05-18 | 2008-05-19 | 2008-05-20 | 2008-05-21 | 2008-05-22 | 3 week | 2008-05-23 | 2008-05-24 | 2008-05-25 | 2008-05-26 | 2008-05-27 | 2008-05-28 | 2008-05-29 | 2008-05-30 | 2008-05-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 168577.4 | 167160.6 | 167788.9 | 167134.9 | 169216.5 | 167791.3 | 167121.5 | 1174791.1 | 166168.3 | 167346.3 | 162805 | 164745.8 | 169402.2 | 162807.4 | 167307.2 | 1160582.2 | 168577.4 | 162016.7 | 165206.9 | 167134.9 | 166614.5 | 162627.4 | 167121.5 | 1159299.3 | 127086 | 131237.9 | 129916.2 | 129392.8 | 126445.1 | 128759.2 | 131198.8 | 129918.1 | 127652.2 | 1161606.3 | 4656278.9
Coal Audited (kgs) | 26825 | 26498 | 26579 | 26469 | 26918 | 26582 | 26459 | 186330 | 26854 | 26527 | 26608 | 26498 | 26946 | 26611 | 26488 | 186532 | 26591 | 26498 | 26579 | 26469 | 26918 | 26582 | 26459 | 186096 | 20843 | 20825 | 20597 | 20796 | 20729 | 20704 | 20786 | 20598 | 20884 | 186762 | 745720
Actual Coal Consumed (Kgs) | 26020.25 | 25703.06 | 25781.63 | 25674.93 | 26110.46 | 25784.54 | 25665.23 | 180740.1 | 26048.38 | 25731.19 | 25809.76 | 25703.06 | 26137.62 | 25812.67 | 25693.36 | 180936.04 | 25793.27 | 25703.06 | 25781.63 | 25674.93 | 26110.46 | 25784.54 | 25665.23 | 180513.12 | 20217.71 | 20200.25 | 19979.09 | 20172.12 | 20107.13 | 20082.88 | 20162.42 | 19980.06 | 20257.48 | 181159.14 | 723348.4
Feed Water Temp. deg. C | 71 | 70 | 73 | 72 | 74 | 72 | 72 | 72 | 71 | 70 | 72 | 72 | 71 | 70 | 71 | 71 | 71 | 74 | 73 | 74 | 72 | 73 | 74 | 73 | 70 | 72 | 74 | 72 | 72 | 73 | 72 | 71 | 72 | 72 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 173634.722 | 172175.418 | 172822.567 | 172148.947 | 174292.995 | 172825.039 | 172135.145 | 1210034.833 | 171153.349 | 172366.689 | 167689.15 | 169688.174 | 174484.266 | 167691.622 | 172326.416 | 1195399.666 | 173634.722 | 166877.201 | 170163.107 | 172148.947 | 171612.935 | 167506.222 | 172135.145 | 1194078.279 | 130898.58 | 135175.037 | 133813.686 | 133274.584 | 130238.453 | 132621.976 | 135134.764 | 133815.643 | 131481.766 | 1196454.489 | 4795967.267
MONTH -JUNE -2004
Particulars | 2008-06-01 | 2008-06-02 | 2008-06-03 | 2008-06-04 | 2008-06-05 | 2008-06-06 | 2008-06-07 | 1 week | 2008-06-08 | 2008-06-09 | 2008-06-10 | 2008-06-11 | 2008-06-12 | 2008-06-13 | 2008-06-14 | 2 Week | 2008-06-15 | 2008-06-16 | 2008-06-17 | 2008-06-18 | 2008-06-19 | 2008-06-20 | 2008-06-21 | 3 week | 2008-06-22 | 2008-06-23 | 2008-06-24 | 2008-06-25 | 2008-06-26 | 2008-06-27 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 186904.7 | 185487.9 | 186116.2 | 185462.2 | 187543.8 | 186118.6 | 185448.8 | 1303082.2 | 184439.1 | 185673.6 | 181019.4 | 183016.6 | 187729.5 | 181021.8 | 185634.5 | 1288534.5 | 186904.7 | 180231.1 | 183477.8 | 185462.2 | 184885.4 | 180841.8 | 185448.8 | 1287251.8 | 144810.4 | 147522.2 | 148800.5 | 145452.2 | 144169.5 | 146737.4 | 877492.2 | 4756360.7
Coal Audited (kgs) | 29753 | 29426 | 29508 | 29398 | 29846 | 29511 | 29387 | 206829 | 29782 | 29455 | 29537 | 29426 | 29875 | 29540 | 29416 | 207031 | 29753 | 29426 | 29508 | 29398 | 29846 | 29511 | 29387 | 206829 | 23732 | 23409 | 23589 | 23376 | 23618 | 23597 | 141321 | 762010
Actual Coal Consumed (Kgs) | 28860.41 | 28543.22 | 28622.76 | 28516.06 | 28950.62 | 28625.67 | 28505.39 | 200624.13 | 28888.54 | 28571.35 | 28650.89 | 28543.22 | 28978.75 | 28653.8 | 28533.52 | 200820.07 | 28860.41 | 28543.22 | 28622.76 | 28516.06 | 28950.62 | 28625.67 | 28505.39 | 200624.13 | 23020.04 | 22706.73 | 22881.33 | 22674.72 | 22909.46 | 22889.09 | 137081.37 | 739149.7
Feed Water Temp. deg. C | 75 | 76 | 72 | 71 | 76 | 75 | 73 | 74 | 73 | 75 | 74 | 71 | 72 | 74 | 72 | 73 | 73 | 74 | 75 | 75 | 76 | 76 | 76 | 75 | 74 | 72 | 75 | 73 | 76 | 74 | 74 | 74
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 192511.841 | 191052.537 | 191699.686 | 191026.066 | 193170.114 | 191702.158 | 191012.264 | 1342174.666 | 189972.273 | 191243.808 | 186449.982 | 188507.098 | 193361.385 | 186452.454 | 191203.535 | 1327190.535 | 192511.841 | 185638.033 | 188982.134 | 191026.066 | 190431.962 | 186267.054 | 191012.264 | 1325869.354 | 149154.712 | 151947.866 | 153264.515 | 149815.766 | 148494.585 | 151139.522 | 903816.966 | 4899051.521
MONTH -JULY -2004
Particulars | 2008-07-01 | 2008-07-02 | 2008-07-03 | 2008-07-04 | 2008-07-05 | 2008-07-06 | 2008-07-07 | 1 week | 2008-07-08 | 2008-07-09 | 2008-07-10 | 2008-07-11 | 2008-07-12 | 2008-07-13 | 2008-07-14 | 2 Week | 2008-07-15 | 2008-07-16 | 2008-07-17 | 2008-07-18 | 2008-07-19 | 2008-07-20 | 2008-07-21 | 3 week | 2008-07-22 | 2008-07-23 | 2008-07-24 | 2008-07-25 | 2008-07-26 | 2008-07-27 | 2008-07-28 | 2008-07-29 | 2008-07-30 | 2008-07-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 163605.5 | 162188.7 | 162817 | 162163 | 164244.6 | 162819.4 | 162149.6 | 1139987.8 | 161272.9 | 162374.4 | 157986 | 159850.4 | 164430.3 | 157988.4 | 162335.3 | 1126237.7 | 163605.5 | 157197.7 | 160311.5 | 162163 | 161719.1 | 157808.4 | 162149.6 | 1124954.8 | 110717.2 | 114762.1 | 113440.4 | 112970.5 | 110076.3 | 112336.3 | 114723 | 113442.3 | 111283.6 | 113478.8 | 1127230.5 | 4518410.8
Coal Audited (kgs) | 26036 | 25709 | 25791 | 25680 | 26129 | 25794 | 25670 | 180809 | 26065 | 25738 | 25820 | 25710 | 26158 | 25823 | 25699 | 181013 | 25932 | 26036 | 25709 | 25791 | 25680 | 26129 | 25794 | 181071 | 18204 | 18187 | 17959 | 18158 | 18091 | 18065 | 18147 | 17960 | 18240 | 17736 | 180747 | 723640
Actual Coal Consumed (Kgs) | 25254.92 | 24937.73 | 25017.27 | 24909.6 | 25345.13 | 25020.18 | 24899.9 | 175384.73 | 25283.05 | 24965.86 | 25045.4 | 24938.7 | 25373.26 | 25048.31 | 24928.03 | 175582.61 | 25154.04 | 25254.92 | 24937.73 | 25017.27 | 24909.6 | 25345.13 | 25020.18 | 175638.87 | 17657.88 | 17641.39 | 17420.23 | 17613.26 | 17548.27 | 17523.05 | 17602.59 | 17421.2 | 17692.8 | 17203.92 | 175324.59 | 701930.8
Feed Water Temp. deg. C | 72 | 73 | 71 | 74 | 74 | 73 | 74 | 73 | 72 | 73 | 71 | 74 | 74 | 73 | 74 | 73 | 73 | 71 | 72 | 74 | 74 | 73 | 74 | 73 | 73 | 71 | 74 | 72 | 74 | 73 | 74 | 73 | 74 | 72 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 168513.665 | 167054.361 | 167701.51 | 167027.89 | 169171.938 | 167703.982 | 167014.088 | 1174187.434 | 166111.087 | 167245.632 | 162725.58 | 164645.912 | 169363.209 | 162728.052 | 167205.359 | 1160024.831 | 168513.665 | 161913.631 | 165120.845 | 167027.89 | 166570.673 | 162542.652 | 167014.088 | 1158703.444 | 114038.716 | 118204.963 | 116843.612 | 116359.615 | 113378.589 | 115706.389 | 118164.69 | 116845.569 | 114622.108 | 116883.164 | 1161047.415 | 4653963.124
MONTH -AUGUST -2004
Particulars | 2008-08-01 | 2008-08-02 | 2008-08-03 | 2008-08-04 | 2008-08-05 | 2008-08-06 | 2008-08-07 | 1 week | 2008-08-08 | 2008-08-09 | 2008-08-10 | 2008-08-11 | 2008-08-12 | 2008-08-13 | 2008-08-14 | 2 Week | 2008-08-15 | 2008-08-16 | 2008-08-17 | 2008-08-18 | 2008-08-19 | 2008-08-20 | 2008-08-21 | 3 week | 2008-08-22 | 2008-08-23 | 2008-08-24 | 2008-08-25 | 2008-08-26 | 2008-08-27 | 2008-08-28 | 2008-08-29 | 2008-08-30 | 2008-08-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 162083.3 | 160666.5 | 161294.8 | 160640.8 | 162722.4 | 161297.2 | 160627.4 | 1129332.4 | 159774.1 | 160852.2 | 156510.7 | 158351.6 | 162908.1 | 156513.1 | 160813.1 | 1115722.9 | 162083.3 | 155722.4 | 158812.7 | 160640.8 | 160220.3 | 156333.1 | 160627.4 | 1114440 | 109684.3 | 113696.2 | 112375.2 | 111918.5 | 109044.3 | 111288.5 | 113658.2 | 112376.2 | 110251.3 | 112413.2 | 1116705.9 | 4476201.2
Coal Audited (kgs) | 25794 | 25467 | 25548 | 25438 | 25887 | 25552 | 25428 | 179114 | 25824 | 25497 | 25578 | 25468 | 25915 | 25581 | 25458 | 179321 | 25794 | 25467 | 25548 | 25438 | 25886 | 25552 | 25428 | 179113 | 18035 | 18018 | 17790 | 17989 | 17922 | 17896 | 17978 | 17791 | 18085 | 17828 | 179332 | 716880
Actual Coal Consumed (Kgs) | 25020.18 | 24702.99 | 24781.56 | 24674.86 | 25110.39 | 24785.44 | 24665.16 | 173740.58 | 25049.28 | 24732.09 | 24810.66 | 24703.96 | 25137.55 | 24813.57 | 24694.26 | 173941.37 | 25020.18 | 24702.99 | 24781.56 | 24674.86 | 25109.42 | 24785.44 | 24665.16 | 173739.61 | 17493.95 | 17477.46 | 17256.3 | 17449.33 | 17384.34 | 17359.12 | 17438.66 | 17257.27 | 17542.45 | 17293.16 | 173952.04 | 695373.6
Feed Water Temp. deg. C | 71 | 70 | 72 | 72 | 71 | 70 | 71 | 71 | 71 | 70 | 72 | 73 | 73 | 72 | 73 | 72 | 71 | 74 | 73 | 74 | 72 | 73 | 74 | 73 | 72 | 74 | 73 | 71 | 72 | 70 | 72 | 71 | 72 | 73 | 72 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 166945.799 | 165486.495 | 166133.644 | 165460.024 | 167604.072 | 166136.116 | 165446.222 | 1163212.372 | 164567.323 | 165677.766 | 161206.021 | 163102.148 | 167795.343 | 161208.493 | 165637.493 | 1149194.587 | 166945.799 | 160394.072 | 163577.081 | 165460.024 | 165026.909 | 161023.093 | 165446.222 | 1147873.2 | 112974.829 | 117107.086 | 115746.456 | 115276.055 | 112315.629 | 114627.155 | 117067.946 | 115747.486 | 113558.839 | 115785.596 | 1150207.077 | 4610487.236
MONTH -SEPTEMBER -2004
Particulars | 2008-09-01 | 2008-09-02 | 2008-09-03 | 2008-09-04 | 2008-09-05 | 2008-09-06 | 2008-09-07 | 1 week | 2008-09-08 | 2008-09-09 | 2008-09-10 | 2008-09-11 | 2008-09-12 | 2008-09-13 | 2008-09-14 | 2 Week | 2008-09-15 | 2008-09-16 | 2008-09-17 | 2008-09-18 | 2008-09-19 | 2008-09-20 | 2008-09-21 | 3 week | 2008-09-22 | 2008-09-23 | 2008-09-24 | 2008-09-25 | 2008-09-26 | 2008-09-27 | 2008-09-28 | 2008-09-29 | 2008-09-30 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 171029.8 | 169728.1 | 170377.9 | 169729.4 | 171678.3 | 170378.4 | 169728.3 | 1192650.2 | 168581.4 | 169913.8 | 165315.5 | 167301 | 171864 | 165316 | 169914 | 1178205.7 | 171029.8 | 164505.7 | 167756.7 | 169729.4 | 169037.1 | 165136 | 169728.3 | 1176923 | 129210.4 | 132010.6 | 133310.4 | 129981 | 128578.9 | 131260 | 132010.8 | 133311.8 | 127948.2 | 1177622.1 | 4725401
Coal Audited (kgs) | 27229 | 26902 | 26984 | 26873 | 27321 | 26987 | 26863 | 189159 | 27259 | 26932 | 27013 | 26903 | 27352 | 27016 | 26893 | 189368 | 27229 | 26902 | 26984 | 26873 | 27322 | 26987 | 26863 | 189160 | 21246 | 20920 | 21104 | 20891 | 21133 | 21107 | 20884 | 21105 | 20973 | 189363 | 757050
Actual Coal Consumed (Kgs) | 26412.13 | 26094.94 | 26174.48 | 26066.81 | 26501.37 | 26177.39 | 26057.11 | 183484.23 | 26441.23 | 26124.04 | 26202.61 | 26095.91 | 26531.44 | 26205.52 | 26086.21 | 183686.96 | 26412.13 | 26094.94 | 26174.48 | 26066.81 | 26502.34 | 26177.39 | 26057.11 | 183485.2 | 20608.62 | 20292.4 | 20470.88 | 20264.27 | 20499.01 | 20473.79 | 20257.48 | 20471.85 | 20343.81 | 183682.11 | 734338.5
Feed Water Temp. deg. C | 71 | 71 | 72 | 73 | 74 | 71 | 72 | 72 | 72 | 70 | 70 | 71 | 71 | 72 | 71 | 71 | 74 | 75 | 73 | 72 | 72 | 72 | 73 | 73 | 71 | 72 | 70 | 73 | 73 | 72 | 73 | 72 | 72 | 72 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 176160.694 | 174819.943 | 175489.237 | 174821.282 | 176828.649 | 175489.752 | 174820.149 | 1228429.706 | 173638.842 | 175011.214 | 170274.965 | 172320.03 | 177019.92 | 170275.48 | 175011.42 | 1213551.871 | 176160.694 | 169440.871 | 172789.401 | 174821.282 | 174108.213 | 170090.08 | 174820.149 | 1212230.69 | 133086.712 | 135970.918 | 137309.712 | 133880.43 | 132436.267 | 135197.8 | 135971.124 | 137311.154 | 131786.646 | 1212950.763 | 4867163.03
MONTH -OCTOBER -2004
Particulars | 2008-10-01 | 2008-10-02 | 2008-10-03 | 2008-10-04 | 2008-10-05 | 2008-10-06 | 2008-10-07 | 1 week | 2008-10-08 | 2008-10-09 | 2008-10-10 | 2008-10-11 | 2008-10-12 | 2008-10-13 | 2008-10-14 | 2 Week | 2008-10-15 | 2008-10-16 | 2008-10-17 | 2008-10-18 | 2008-10-19 | 2008-10-20 | 2008-10-21 | 3 week | 2008-10-22 | 2008-10-23 | 2008-10-24 | 2008-10-25 | 2008-10-26 | 2008-10-27 | 2008-10-28 | 2008-10-29 | 2008-10-30 | 2008-10-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 161951.3 | 160417.5 | 161024.8 | 160363.8 | 162580.4 | 161030.2 | 160340.4 | 1127708.4 | 159545.7 | 160620.2 | 156285.9 | 158123.2 | 162676.1 | 156288.3 | 160581.1 | 1114120.5 | 161851.3 | 155497.6 | 158584.3 | 160408.8 | 159991.9 | 156108.3 | 160395.4 | 1112837.6 | 109527.1 | 113534.2 | 112212.5 | 111761.5 | 108886.2 | 111127.9 | 113495.1 | 112214.4 | 110093.5 | 112250.9 | 1115103.3 | 4469769.8
Coal Audited (kgs) | 25758 | 25431 | 25512 | 25402 | 25851 | 25515 | 25392 | 178861 | 25787 | 25460 | 25541 | 25431 | 25879 | 25544 | 25421 | 179063 | 25758 | 25431 | 25512 | 25402 | 25851 | 25515 | 25392 | 178861 | 18009 | 17992 | 17764 | 17963 | 17896 | 17870 | 17953 | 17769 | 18046 | 17803 | 179065 | 715850
Actual Coal Consumed (Kgs) | 24985.26 | 24668.07 | 24746.64 | 24639.94 | 25075.47 | 24749.55 | 24630.24 | 173495.17 | 25013.39 | 24696.2 | 24774.77 | 24668.07 | 25102.63 | 24777.68 | 24658.37 | 173691.11 | 24985.26 | 24668.07 | 24746.64 | 24639.94 | 25075.47 | 24749.55 | 24630.24 | 173495.17 | 17468.73 | 17452.24 | 17231.08 | 17424.11 | 17359.12 | 17333.9 | 17414.41 | 17235.93 | 17504.62 | 17268.91 | 173693.05 | 694374.5
Feed Water Temp. deg. C | 74 | 75 | 74 | 73 | 72 | 75 | 75 | 74 | 73 | 72 | 71 | 75 | 74 | 73 | 73 | 73 | 73 | 74 | 71 | 72 | 74 | 74 | 73 | 73 | 72 | 71 | 70 | 72 | 73 | 74 | 71 | 73 | 72 | 72 | 72 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 166809.839 | 165230.025 | 165855.544 | 165174.714 | 167457.812 | 165861.106 | 165150.612 | 1161539.652 | 164332.071 | 165438.806 | 160974.477 | 162866.896 | 167556.383 | 160976.949 | 165398.533 | 1147544.115 | 166706.839 | 160162.528 | 163341.829 | 165221.064 | 164791.657 | 160791.549 | 165207.262 | 1146222.728 | 112812.913 | 116940.226 | 115578.875 | 115114.345 | 112152.786 | 114461.737 | 116899.953 | 115580.832 | 113396.305 | 115618.427 | 1148556.399 | 4603862.894
MONTH -NOVEMBER -2004
Particulars | 2008-11-01 | 2008-11-02 | 2008-11-03 | 2008-11-04 | 2008-11-05 | 2008-11-06 | 2008-11-07 | 1 week | 2008-11-08 | 2008-11-09 | 2008-11-10 | 2008-11-11 | 2008-11-12 | 2008-11-13 | 2008-11-14 | 2 Week | 2008-11-15 | 2008-11-16 | 2008-11-17 | 2008-11-18 | 2008-11-19 | 2008-11-20 | 2008-11-21 | 3 week | 2008-11-22 | 2008-11-23 | 2008-11-24 | 2008-11-25 | 2008-11-26 | 2008-11-27 | 2008-11-28 | 2008-11-29 | 2008-11-30 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 167881.6 | 166464.8 | 167093.1 | 166439.1 | 168520.7 | 167095.5 | 166425.7 | 1169920.5 | 165483.2 | 166650.5 | 162130.6 | 164060.7 | 168706.4 | 162133 | 166611.4 | 1155775.8 | 167881.6 | 161342.3 | 164521.9 | 166439.1 | 165929.5 | 161953 | 166425.7 | 1154493.1 | 126861.5 | 129468.9 | 130747.2 | 127451.1 | 126220.6 | 128737.5 | 129429.8 | 130749.3 | 125537.9 | 1155203.8 | 4635393.2
Coal Audited (kgs) | 26714 | 26388 | 26469 | 26359 | 26806 | 26472 | 26348 | 185556 | 26743 | 26416 | 26498 | 26388 | 26838 | 26500 | 26377 | 185760 | 26714 | 26388 | 26469 | 26359 | 26808 | 26472 | 26348 | 185558 | 20846 | 20520 | 20704 | 20492 | 20726 | 20707 | 20480 | 20706 | 20575 | 185756 | 742630
Actual Coal Consumed (Kgs) | 25912.58 | 25596.36 | 25674.93 | 25568.23 | 26001.82 | 25677.84 | 25557.56 | 179989.32 | 25940.71 | 25623.52 | 25703.06 | 25596.36 | 26032.86 | 25705 | 25585.69 | 180187.2 | 25912.58 | 25596.36 | 25674.93 | 25568.23 | 26003.76 | 25677.84 | 25557.56 | 179991.26 | 20220.62 | 19904.4 | 20082.88 | 19877.24 | 20104.22 | 20085.79 | 19865.6 | 20084.82 | 19957.75 | 180183.32 | 720351.1
Feed Water Temp. deg. C | 73 | 72 | 74 | 71 | 74 | 74 | 73 | 73 | 72 | 71 | 74 | 74 | 73 | 74 | 73 | 73 | 73 | 74 | 71 | 72 | 74 | 73 | 74 | 73 | 71 | 73 | 72 | 74 | 74 | 73 | 74 | 74 | 72 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 172918.048 | 171458.744 | 172105.893 | 171432.273 | 173576.321 | 172108.365 | 171418.471 | 1205018.115 | 170447.696 | 171650.015 | 166994.518 | 168982.521 | 173767.592 | 166996.99 | 171609.742 | 1190449.074 | 172918.048 | 166182.569 | 169457.557 | 171432.273 | 170907.385 | 166811.59 | 171418.471 | 1189127.893 | 130667.345 | 133352.967 | 134669.616 | 131274.633 | 130007.218 | 132599.625 | 133312.694 | 134671.779 | 129304.037 | 1189859.914 | 4774454.996
MONTH -DECEMBER -2004
Particulars | 2008-12-01 | 2008-12-02 | 2008-12-03 | 2008-12-04 | 2008-12-05 | 2008-12-06 | 2008-12-07 | 1 week | 2008-12-08 | 2008-12-09 | 2008-12-10 | 2008-12-11 | 2008-12-12 | 2008-12-13 | 2008-12-14 | 2 Week | 2008-12-15 | 2008-12-16 | 2008-12-17 | 2008-12-18 | 2008-12-19 | 2008-12-20 | 2008-12-21 | 3 week | 2008-12-22 | 2008-12-23 | 2008-12-24 | 2008-12-25 | 2008-12-26 | 2008-12-27 | 2008-12-28 | 2008-12-29 | 2008-12-30 | 2008-12-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 167517.7 | 165983.9 | 166591.2 | 165930.2 | 168146.8 | 166596.6 | 165906.8 | 1166673.2 | 165026.5 | 166186.7 | 161681 | 163604 | 168242.6 | 161683.4 | 166147.6 | 1152571.8 | 167417.7 | 160892.7 | 164065.1 | 165975.2 | 165472.7 | 161503.4 | 165961.8 | 1151288.6 | 113303.7 | 117430.6 | 116108.9 | 115598.1 | 112662.8 | 114964.5 | 117391.5 | 116110.8 | 113870.4 | 116147.3 | 1153588.6 | 4624122.2
Coal Audited (kgs) | 26640 | 26313 | 26395 | 26285 | 26733 | 26398 | 26274 | 185038 | 26670 | 26343 | 26425 | 26314 | 26763 | 26428 | 26304 | 185247 | 26640 | 26313 | 26395 | 26285 | 26733 | 26398 | 26274 | 185038 | 18628 | 18610 | 18382 | 18581 | 18514 | 18489 | 18571 | 18384 | 18666 | 18422 | 185247 | 740570
Actual Coal Consumed (Kgs) | 25840.8 | 25523.61 | 25603.15 | 25496.45 | 25931.01 | 25606.06 | 25485.78 | 179486.86 | 25869.9 | 25552.71 | 25632.25 | 25524.58 | 25960.11 | 25635.16 | 25514.88 | 179689.59 | 25840.8 | 25523.61 | 25603.15 | 25496.45 | 25931.01 | 25606.06 | 25485.78 | 179486.86 | 18069.16 | 18051.7 | 17830.54 | 18023.57 | 17958.58 | 17934.33 | 18013.87 | 17832.48 | 18106.02 | 17869.34 | 179689.59 | 718352.9
Feed Water Temp. deg. C | 70 | 72 | 73 | 73 | 71 | 73 | 72 | 72 | 73 | 74 | 73 | 71 | 72 | 75 | 73 | 73 | 71 | 70 | 70 | 73 | 72 | 71 | 70 | 71 | 70 | 72 | 73 | 74 | 72 | 71 | 70 | 73 | 73 | 72 | 72 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 172543.231 | 170963.417 | 171588.936 | 170908.106 | 173191.204 | 171594.498 | 170884.004 | 1201673.396 | 169977.295 | 171172.301 | 166531.43 | 168512.12 | 173289.878 | 166533.902 | 171132.028 | 1187148.954 | 172440.231 | 165719.481 | 168987.053 | 170954.456 | 170436.881 | 166348.502 | 170940.654 | 1185827.258 | 116702.811 | 120953.518 | 119592.167 | 119066.043 | 116042.684 | 118413.435 | 120913.245 | 119594.124 | 117286.512 | 119631.719 | 1188196.258 | 4762845.866
MONTH -JANUARY -2004
Particulars | 2008-01-01 | 2008-01-02 | 2008-01-03 | 2008-01-04 | 2008-01-05 | 2008-01-06 | 2008-01-07 | 1 week | 2008-01-08 | 2008-01-09 | 2008-01-10 | 2008-01-11 | 2008-01-12 | 2008-01-13 | 2008-01-14 | 2 Week | 2008-01-15 | 2008-01-16 | 2008-01-17 | 2008-01-18 | 2008-01-19 | 2008-01-20 | 2008-01-21 | 3 week | 2008-01-22 | 2008-01-23 | 2008-01-24 | 2008-01-25 | 2008-01-26 | 2008-01-27 | 2008-01-28 | 2008-01-29 | 2008-01-30 | 2008-01-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 175738.1 | 174321.3 | 174949.6 | 174295.6 | 176377.2 | 174952 | 174282.2 | 1224916 | 173218.8 | 174507 | 169745.3 | 171796.3 | 176562.9 | 169747.7 | 174467.9 | 1210045.9 | 175738.1 | 168957 | 172257.5 | 174295.6 | 173665.1 | 169567.7 | 174282.2 | 1208763.2 | 118948.7 | 123254.9 | 121933.2 | 121332.7 | 118307.8 | 120699.1 | 123215.8 | 121935.1 | 119515.1 | 121971.5 | 1211113.9 | 4854839
Coal Audited (kgs) | 27960 | 27633 | 27714 | 27604 | 28053 | 27717 | 27594 | 194275 | 27990 | 27663 | 27744 | 27634 | 28083 | 27747 | 27624 | 194485 | 27960 | 27633 | 27714 | 27604 | 28052 | 27718 | 27594 | 194275 | 19552 | 19534 | 19306 | 19505 | 19438 | 19411 | 19495 | 19307 | 19590 | 19347 | 194485 | 777520
Actual Coal Consumed (Kgs) | 27121.2 | 26804.01 | 26882.58 | 26775.88 | 27211.41 | 26885.49 | 26766.18 | 188446.75 | 27150.3 | 26833.11 | 26911.68 | 26804.98 | 27240.51 | 26914.59 | 26795.28 | 188650.45 | 27121.2 | 26804.01 | 26882.58 | 26775.88 | 27210.44 | 26886.46 | 26766.18 | 188446.75 | 18965.44 | 18947.98 | 18726.82 | 18919.85 | 18854.86 | 18828.67 | 18910.15 | 18727.79 | 19002.3 | 18766.59 | 188650.45 | 754194.4
Feed Water Temp. deg. C | 71 | 72 | 75 | 75 | 76 | 75 | 74 | 74 | 73 | 72 | 74 | 75 | 75 | 75 | 74 | 74 | 75 | 76 | 74 | 74 | 75 | 76 | 75 | 75 | 73 | 74 | 74 | 72 | 72 | 74 | 71 | 75 | 72 | 73 | 73 | 74
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 181010.243 | 179550.939 | 180198.088 | 179524.468 | 181668.516 | 180200.56 | 179510.666 | 1261663.48 | 178415.364 | 179742.21 | 174837.659 | 176950.189 | 181859.787 | 174840.131 | 179701.937 | 1246347.277 | 181010.243 | 174025.71 | 177425.225 | 179524.468 | 178875.053 | 174654.731 | 179510.666 | 1245026.096 | 122517.161 | 126952.547 | 125591.196 | 124972.681 | 121857.034 | 124320.073 | 126912.274 | 125593.153 | 123100.553 | 125630.645 | 1247447.317 | 5000484.17
MONTH -FEBRUARY -2004
Particulars | 2008-02-01 | 2008-02-02 | 2008-02-03 | 2008-02-04 | 2008-02-05 | 2008-02-06 | 2008-02-07 | 1 week | 2008-02-08 | 2008-02-09 | 2008-02-10 | 2008-02-11 | 2008-02-12 | 2008-02-13 | 2008-02-14 | 2 Week | 2008-02-15 | 2008-02-16 | 2008-02-17 | 2008-02-18 | 2008-02-19 | 2008-02-20 | 2008-02-21 | 3 week | 2008-02-22 | 2008-02-23 | 2008-02-24 | 2008-02-25 | 2008-02-26 | 2008-02-27 | 2008-02-28 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 161155.5 | 167112 | 162834.8 | 159713 | 161794.6 | 162837.2 | 159699.6 | 1135146.7 | 158860.6 | 172227.6 | 175376.5 | 179583.8 | 161980.3 | 155613.9 | 159885.3 | 1163528 | 161155.5 | 162196.5 | 170238.1 | 159713 | 161794.6 | 160369.4 | 159699.6 | 1135166.7 | 161341.2 | 159924.4 | 163023.4 | 159898.7 | 164471 | 167967 | 159885.7 | 1136511.4 | 4570352.8
Coal Audited (kgs) | 25647 | 25321 | 25402 | 25292 | 25740 | 25405 | 25281 | 178088 | 25676 | 25349 | 25431 | 25321 | 25769 | 25434 | 25310 | 178290 | 25647 | 25321 | 25402 | 25292 | 25740 | 25405 | 25281 | 178088 | 25676 | 25349 | 25431 | 25321 | 25769 | 25435 | 25313 | 178294 | 712760
Actual Coal Consumed (Kgs) | 24877.59 | 24561.37 | 24639.94 | 24533.24 | 24967.8 | 24642.85 | 24522.57 | 172745.36 | 24905.72 | 24588.53 | 24668.07 | 24561.37 | 24995.93 | 24670.98 | 24550.7 | 172941.3 | 24877.59 | 24561.37 | 24639.94 | 24533.24 | 24967.8 | 24642.85 | 24522.57 | 172745.36 | 24905.72 | 24588.53 | 24668.07 | 24561.37 | 24995.93 | 24671.95 | 24553.61 | 172945.18 | 691377.2
Feed Water Temp. deg. C | 71 | 72 | 70 | 73 | 74 | 73 | 71 | 72 | 74 | 74 | 73 | 72 | 73 | 72 | 73 | 73 | 74 | 75 | 76 | 73 | 72 | 73 | 75 | 74 | 73 | 71 | 72 | 73 | 74 | 75 | 73 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 165990.165 | 172125.36 | 167719.844 | 164504.39 | 166648.438 | 167722.316 | 164490.588 | 1169201.101 | 163626.418 | 177394.428 | 180637.795 | 184971.314 | 166839.709 | 160282.317 | 164681.859 | 1198433.84 | 165990.165 | 167062.395 | 175345.243 | 164504.39 | 166648.438 | 165180.482 | 164490.588 | 1169221.701 | 166181.436 | 164722.132 | 167914.102 | 164695.661 | 169405.13 | 173006.01 | 164682.271 | 1170606.742 | 4707463.384
MONTH -MARCH -2004
Particulars | 2008-03-01 | 2008-03-02 | 2008-03-03 | 2008-03-04 | 2008-03-05 | 2008-03-06 | 2008-03-07 | 1 week | 2008-03-08 | 2008-03-09 | 2008-03-10 | 2008-03-11 | 2008-03-12 | 2008-03-13 | 2008-03-14 | 2 Week | 2008-03-15 | 2008-03-16 | 2008-03-17 | 2008-03-18 | 2008-03-19 | 2008-03-20 | 2008-03-21 | 3 week | 2008-03-22 | 2008-03-23 | 2008-03-24 | 2008-03-25 | 2008-03-26 | 2008-03-27 | 2008-03-28 | 2008-03-29 | 2008-03-30 | 2008-03-31 | 4 week | Monthly Total
Actual Steam Generated (Kgs) | 219844.5 | 208733.1 | 209361.4 | 218342 | 217272 | 209363.8 | 211905.5 | 1494822.3 | 207101.2 | 212133.2 | 203098.3 | 205678.7 | 223952.3 | 212773.9 | 208879.7 | 1473617.3 | 210149.9 | 202310 | 206139.8 | 218342 | 214030.5 | 219028.4 | 208694 | 1478694.6 | 142295.7 | 147342.8 | 146021.8 | 145047.8 | 141655.7 | 144417.8 | 147304.8 | 146022.8 | 142862.6 | 146059.8 | 1449031.6 | 5896165.8
Coal Audited (kgs) | 33418 | 33091 | 33172 | 33062 | 33509 | 33175 | 33052 | 232479 | 33447 | 33121 | 33202 | 33092 | 33540 | 33205 | 33081 | 232688 | 33418 | 33091 | 33172 | 33062 | 33509 | 33175 | 33052 | 232479 | 23372 | 23355 | 23127 | 23326 | 23259 | 23233 | 23315 | 23128 | 23412 | 23167 | 232694 | 930340
Actual Coal Consumed (Kgs) | 32415.46 | 32098.27 | 32176.84 | 32070.14 | 32503.73 | 32179.75 | 32060.44 | 225504.63 | 32443.59 | 32127.37 | 32205.94 | 32099.24 | 32533.8 | 32208.85 | 32088.57 | 225707.36 | 32415.46 | 32098.27 | 32176.84 | 32070.14 | 32503.73 | 32179.75 | 32060.44 | 225504.63 | 22670.84 | 22654.35 | 22433.19 | 22626.22 | 22561.23 | 22536.01 | 22615.55 | 22434.16 | 22709.64 | 22471.99 | 225713.18 | 902429.8
Feed Water Temp. deg. C | 72 | 70 | 71 | 73 | 73 | 74 | 71 | 72 | 72 | 71 | 71 | 71 | 74 | 72 | 73 | 72 | 71 | 72 | 70 | 72 | 74 | 72 | 73 | 72 | 72 | 72 | 70 | 73 | 71 | 74 | 72 | 70 | 73 | 73 | 72 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 226439.835 | 214995.093 | 215642.242 | 224892.26 | 223790.16 | 215644.714 | 218262.665 | 1539666.969 | 213314.236 | 218497.196 | 209191.249 | 211849.061 | 230670.869 | 219157.117 | 215146.091 | 1517825.819 | 216454.397 | 208379.3 | 212323.994 | 224892.26 | 220451.415 | 225599.252 | 214954.82 | 1523055.438 | 146564.571 | 151763.084 | 150402.454 | 149399.234 | 145905.371 | 148750.334 | 151723.944 | 150403.484 | 147148.478 | 150441.594 | 1492502.548 | 6073050.774

## CER Estimation_04-05
Monitored Parameters for the year 2004-2005
Months | Quantity of Coal Used | Coal-Audited | Gross Calorific Value of Coal | Heat Energy Input | Steam Load | Steam Pressure | Steam Pressure | Steam Enthalpy | Feed water Load | Feed Water Temerature | Feed Water Enthalpy | Number of Truck Trips
Units | (tons) | (tons) | (kCal/kg) | (kCal) | (tons) | (Bar) | (kg/cm2) | (kCal) | (tons) | (°C) | (kCal)
April '04 | 748.8303 | 771.99 | 5565 | 4167240619.5 | 4818.6546 | 8.83 | 9 | 3198049996.6755 | 4963.2142 | 72 | 357138524.5523 | 78 | Temperature | Feed Water Enthalpy
May '04 | 723.3484 | 745.72 | 5565 | 4025433846 | 4656.2789 | 8.83 | 9 | 3090284313.1079 | 4795.9673 | 72 | 345103916.8173 | 38 | (0C) | (kJ/kg)
June'04 | 739.1497 | 762.01 | 5546 | 4099324236.2 | 4756.3607 | 8.83 | 9 | 3156706712.4551 | 4899.0515 | 74 | 362327153.1713 | 4 | 64 | 267.79
July'04 | 701.9308 | 723.64 | 5600 | 3930812480 | 4518.4108 | 8.83 | 9 | 2998783860.5238 | 4653.9631 | 73 | 339543230.1352 | 21 | 65 | 271.97
August'04 | 695.3736 | 716.88 | 5716 | 3974755497.6 | 4476.2012 | 8.83 | 9 | 2970770146.6669 | 4610.4872 | 72 | 331757310.8824 | 64 | 66 | 276.16
September'04 | 734.3385 | 757.05 | 5575 | 4093937137.5 | 4725.401 | 8.83 | 9 | 3136159344.6313 | 4867.163 | 72 | 350226957.7607 | 59 | 67 | 280.34
October'04 | 694.3745 | 715.85 | 5655 | 3926687797.5 | 4469.7698 | 8.83 | 9 | 2966501748.0253 | 4603.8629 | 73 | 335888024.1373 | 42 | 68 | 284.52
November'04 | 720.3511 | 742.63 | 5578 | 4018118435.8 | 4635.3932 | 8.83 | 9 | 3076422868.709 | 4774.455 | 73 | 348334060.3016 | 118 | 72 | 301.27
December'04 | 718.3529 | 740.57 | 5602 | 4024212945.8 | 4624.1222 | 8.83 | 9 | 3068942519.0046 | 4762.8459 | 72 | 342720596.7112 | 42 | 73 | 305.46
January'05 | 754.1944 | 777.52 | 5634 | 4249131249.6 | 4854.839 | 8.83 | 9 | 3222064899.1547 | 5000.4842 | 74 | 369828973.2263 | 76 | 74 | 309.65
Febraury'05 | 691.3772 | 712.76 | 5602 | 3873095074.4 | 4570.3528 | 8.83 | 9 | 3033256784.341 | 4707.4634 | 73 | 343446495.0751 | 67
March'05 | 902.4298 | 930.34 | 5672 | 5118581825.6 | 5896.1658 | 8.83 | 9 | 3913173817.6645 | 6073.0508 | 72 | 436999147.9214 | 28
2004-2005 | 8824.0512 | 9096.96 | 5609.1667 | 49501331145.5 | 57001.95 | 8.83 | 9 | 37831117010.9595 | 58712.0085 | 72.6667 | 4263314390.6922 | 637
Computation of Emission Reductions for the year 2004-2005
Months | Output Enthalpy | Baseline Boiler Efficiency | Baseline Technical Losses | Boiler Efficiency | Technical Losses | Reduction in Losses | Coal Reduction | Fixed Carbon Content (C%) in Coal | Emission Co-efficienct of Coal | Emission Reductions
| (kCal) | (%) | (kCal) | (%) | (kCal) | (kCal) | (kgs) | ('%) | (kgCO2/kCal) | (tons)
April '04 | 2840911472.1233 | 53.9271 | 2427144131.0045 | 68.1725 | 1326329147.3767 | 1100814983.6277 | 197810.4193 | 0.52987 | 0.00034912 | -
March '04 | 2745180396.2906 | 53.9271 | 2345355901.7189 | 68.1959 | 1280253449.7094 | 1065102452.0095 | 191393.0731 | 0.5358 | 0.00035303 | -
June'04 | 2794379559.2838 | 53.9271 | 2387389404.3046 | 68.1668 | 1304944676.9162 | 1082444727.3884 | 195175.7532 | 0.54912 | 0.00036305 | -
July'04 | 2659240630.3886 | 53.9271 | 2271932917.4142 | 67.6512 | 1271571849.6114 | 1000361067.8027 | 178635.905 | 0.53073 | 0.0003475 | -
August'04 | 2639012835.7845 | 53.9271 | 2254651219.8187 | 66.3943 | 1335742661.8155 | 918908558.0032 | 160760.7694 | 0.54405 | 0.00034899 | -
September'04 | 2785932386.8705 | 53.9271 | 2380172528.6126 | 68.0502 | 1308004750.6295 | 1072167777.9831 | 192317.0902 | 0.54087 | 0.00035573 | -
October'04 | 2630613723.888 | 53.9271 | 2247475404.8224 | 66.9932 | 1296074073.612 | 951401331.2104 | 168240.7305 | 0.53473 | 0.00034671 | -
November'04 | 2728088808.4074 | 53.9271 | 2330753634.9368 | 67.8947 | 1290029627.3926 | 1040724007.5442 | 186576.5521 | 0.54273 | 0.00035676 | -
December'04 | 2726221922.2934 | 53.9271 | 2329158653.2842 | 67.7455 | 1297991023.5066 | 1031167629.7775 | 184071.337 | 0.54068 | 0.00035389 | -
January'05 | 2852235925.9284 | 53.9271 | 2436819223.6146 | 67.1252 | 1396895323.6716 | 1039923899.943 | 184580.0319 | 0.5263 | 0.00034252 | -
Febraury'05 | 2689810289.2659 | 53.9271 | 2298050228.305 | 69.4486 | 1183284785.1341 | 1114765443.1709 | 198994.1884 | 0.5188 | 0.00033957 | -
March'05 | 3476174669.743 | 53.9271 | 2969883796.3815 | 67.9128 | 1642407155.857 | 1327476640.5246 | 234040.3104 | 0.54297 | 0.00035101 | -
2004-2005 | 33567802620.2673 | 53.9271 | 28678787044.218 | 67.8126 | 15933528525.2327 | 12745258518.9853 | 2272596.1606 | 0.53639 | 0.00035066 | 0
Reduction in Losses (in GWhe) |  | 14.8201 | < 15

## Daily Report 05-06
INDIAN RAYON AND INDUSTRIES LTD.,
UNIT : JAYA SHREE TEXTILES
RISHRA, HOOGHLY
BOILER DAILY REPORT
MONTH -APRIL -2005
Particulars | 2005-04-01 | 2005-04-02 | 2005-04-03 | 2005-04-04 | 2005-04-05 | 2005-04-06 | 2005-04-07 | 1 week | 2005-04-08 | 2005-04-09 | 2005-04-10 | 2005-04-11 | 2005-04-12 | 2005-04-13 | 2005-04-14 | 2 week | 2005-04-15 | 2005-04-16 | 2005-04-17 | 2005-04-18 | 2005-04-19 | 2005-04-20 | 2005-04-21 | 3 week | 2005-04-22 | 2005-04-23 | 2005-04-24 | 2005-04-25 | 2005-04-26 | 2005-04-27 | 2005-04-28 | 2005-04-29 | 2005-04-30 | 4 week | Total
Actual Steam Generated (Kgs) | 235970.1 | 234670.1 | 235320.1 | 234670.1 | 236620.1 | 235320.1 | 234670.1 | 1647240.7 | 232522.6 | 234855.8 | 228259.5 | 231242.6 | 236805.8 | 228259.5 | 234855.1 | 1626800.9 | 235970.1 | 227449.5 | 231699.8 | 234670.1 | 232979.8 | 228079.5 | 234670.1 | 1625518.9 | 178165.1 | 182521.2 | 183821.2 | 179713.2 | 177535.1 | 180993.2 | 182521.2 | 183821.2 | 176905.1 | 1625996.5 | 6525557
Coal Audited (Kgs) | 37426 | 37220 | 37323 | 37218 | 37529 | 37324 | 37220 | 261260 | 37456 | 37249 | 37353 | 37249 | 37559 | 37353 | 37249 | 261468 | 37426 | 37220 | 37323 | 37220 | 37527 | 37323 | 37220 | 261259 | 29155 | 28949 | 29155 | 28949 | 29052 | 29155 | 28949 | 29155 | 28944 | 261463 | 1045450
Actual Coal Consumed (Kgs) | 36303.22 | 36103.4 | 36203.31 | 36101.46 | 36403.13 | 36204.28 | 36103.4 | 253422.2 | 36332.32 | 36131.53 | 36232.41 | 36131.53 | 36432.23 | 36232.41 | 36131.53 | 253623.96 | 36303.22 | 36103.4 | 36203.31 | 36103.4 | 36401.19 | 36203.31 | 36103.4 | 253421.23 | 28280.35 | 28080.53 | 28280.35 | 28080.53 | 28180.44 | 28280.35 | 28080.53 | 28280.35 | 28075.68 | 253619.11 | 1014086.5
Feed Water Temp. deg. C | 71 | 73 | 72 | 70 | 71 | 73 | 74 | 72 | 71 | 72 | 74 | 74 | 73 | 74 | 73 | 73 | 71 | 70 | 71 | 71 | 72 | 70 | 72 | 71 | 74 | 70 | 73 | 71 | 72 | 73 | 71 | 72 | 72 | 72 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 243049.203 | 241710.203 | 242379.703 | 241710.203 | 243718.703 | 242379.703 | 241710.203 | 1696657.921 | 239498.278 | 241901.474 | 235107.285 | 238179.878 | 243909.974 | 235107.285 | 241900.753 | 1675604.927 | 243049.203 | 234272.985 | 238650.794 | 241710.203 | 239969.194 | 234921.885 | 241710.203 | 1674284.467 | 183510.053 | 187996.836 | 189335.836 | 185104.596 | 182861.153 | 186422.996 | 187996.836 | 189335.836 | 182212.253 | 1674776.395 | 6721323.71
MONTH -MAY -2005
Particulars | 2005-05-02 | 2005-05-03 | 2005-05-04 | 2005-05-05 | 2005-05-06 | 2005-05-07 | 2005-05-08 | 1 week | 2005-05-09 | 2005-05-10 | 2005-05-11 | 2005-05-12 | 2005-05-13 | 2005-05-14 | 2005-05-15 | 2 week | 2005-05-16 | 2005-05-17 | 2005-05-18 | 2005-05-19 | 2005-05-20 | 2005-05-21 | 2005-05-22 | 3 week | 2005-05-23 | 2005-05-24 | 2005-05-25 | 2005-05-26 | 2005-05-27 | 2005-05-28 | 2005-05-29 | 2005-05-30 | 2005-05-31 | 4 week | Total
Actual Steam Generated (Kgs) | 203668.3 | 203668.4 | 203668.4 | 203668.3 | 203668.4 | 203668.3 | 203668.4 | 1425678.5 | 203705.9 | 203565.9 | 203665.9 | 203685.9 | 203565.9 | 203745.9 | 203711.7 | 1425647.1 | 203691.7 | 203551.7 | 203651.7 | 203671.7 | 203551.7 | 203731.7 | 203658.8 | 1425509 | 203758.8 | 203738.8 | 203718.8 | 203698.8 | 203658.8 | 203618.8 | 203598.8 | 203578.8 | 203558.8 | 1832929.2 | 6109763.8
Coal Audited (Kgs) | 32748 | 32542 | 32584 | 32625 | 32573 | 32645 | 32656 | 228373 | 32651 | 32506 | 32609 | 32630 | 32506 | 32692 | 32686 | 228280 | 32665 | 32521 | 32624 | 32645 | 32521 | 32707 | 32617 | 228300 | 32720 | 32699 | 32679 | 32658 | 32617 | 32575 | 32555 | 32534 | 32510 | 293547 | 978500
Actual Coal Consumed (Kgs) | 31765.56 | 31565.74 | 31606.48 | 31646.25 | 31595.81 | 31665.65 | 31676.32 | 221521.81 | 31671.47 | 31530.82 | 31630.73 | 31651.1 | 31530.82 | 31711.24 | 31705.42 | 221431.6 | 31685.05 | 31545.37 | 31645.28 | 31665.65 | 31545.37 | 31725.79 | 31638.49 | 221451 | 31738.4 | 31718.03 | 31698.63 | 31678.26 | 31638.49 | 31597.75 | 31578.35 | 31557.98 | 31534.7 | 284740.59 | 949145
Feed Water Temp. deg. C | 73 | 75 | 72 | 71 | 73 | 74 | 73 | 73 | 72 | 71 | 70 | 73 | 74 | 71 | 73 | 72 | 73 | 74 | 72 | 75 | 74 | 75 | 75 | 74 | 74 | 73 | 72 | 74 | 71 | 74 | 73 | 72 | 74 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 209778.349 | 209778.452 | 209778.452 | 209778.349 | 209778.452 | 209778.349 | 209778.452 | 1468448.855 | 209817.077 | 209672.877 | 209775.877 | 209796.477 | 209672.877 | 209858.277 | 209823.051 | 1468416.513 | 209802.451 | 209658.251 | 209761.251 | 209781.851 | 209658.251 | 209843.651 | 209768.564 | 1468274.27 | 209871.564 | 209850.964 | 209830.364 | 209809.764 | 209768.564 | 209727.364 | 209706.764 | 209686.164 | 209665.564 | 1887917.076 | 6293056.714
MONTH -JUNE -2005
Particulars | 2005-06-01 | 2005-06-02 | 2005-06-03 | 2005-06-04 | 2005-06-05 | 2005-06-06 | 2005-06-07 | 1 week | 2005-06-08 | 2005-06-09 | 2005-06-10 | 2005-06-11 | 2005-06-12 | 2005-06-13 | 2005-06-14 | 2 week | 2005-06-15 | 2005-06-16 | 2005-06-17 | 2005-06-18 | 2005-06-19 | 2005-06-20 | 2005-06-21 | 3 week | 2005-06-22 | 2005-06-23 | 2005-06-24 | 2005-06-25 | 2005-06-26 | 2005-06-27 | 2005-06-28 | 2005-06-29 | 2005-06-30 | 4 week | Total
Actual Steam Generated (Kgs) | 222054 | 220754 | 221404 | 220754 | 222704 | 221404 | 221404 | 1550478 | 218820.7 | 220939.8 | 214771.6 | 217540.7 | 222889.8 | 214771.6 | 220290.8 | 1530025 | 222054 | 213961.6 | 217997.8 | 220754 | 219277.8 | 214591.6 | 220754 | 1529390.8 | 167674.6 | 171697.7 | 172997.5 | 169056.1 | 167044.5 | 170336.3 | 171697.4 | 172997.5 | 166414.1 | 1529915.7 | 6139809.5
Coal Audited (Kgs) | 35219 | 35012 | 35115 | 35012 | 35322 | 35115 | 35012 | 245807 | 35248 | 35042 | 35145 | 35042 | 35352 | 35145 | 35042 | 246016 | 35219 | 35012 | 35115 | 35012 | 35322 | 35114 | 35012 | 245806 | 27438 | 27232 | 27438 | 27232 | 27335 | 27438 | 27232 | 27438 | 27238 | 246021 | 983650
Actual Coal Consumed (Kgs) | 34162.43 | 33961.64 | 34061.55 | 33961.64 | 34262.34 | 34061.55 | 33961.64 | 238432.79 | 34190.56 | 33990.74 | 34090.65 | 33990.74 | 34291.44 | 34090.65 | 33990.74 | 238635.52 | 34162.43 | 33961.64 | 34061.55 | 33961.64 | 34262.34 | 34060.58 | 33961.64 | 238431.82 | 26614.86 | 26415.04 | 26614.86 | 26415.04 | 26514.95 | 26614.86 | 26415.04 | 26614.86 | 26420.86 | 238640.37 | 954140.5
Feed Water Temp. deg. C | 73 | 74 | 72 | 71 | 74 | 73 | 74 | 73 | 74 | 75 | 73 | 72 | 75 | 75 | 74 | 74 | 74 | 73 | 72 | 75 | 75 | 74 | 75 | 74 | 74 | 76 | 76 | 75 | 74 | 73 | 76 | 76 | 75 | 75 | 74
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 228715.62 | 227376.62 | 228046.12 | 227376.62 | 229385.12 | 228046.12 | 228046.12 | 1596992.34 | 225385.321 | 227567.994 | 221214.748 | 224066.921 | 229576.494 | 221214.748 | 226899.524 | 1575925.75 | 228715.62 | 220380.448 | 224537.734 | 227376.62 | 225856.134 | 221029.348 | 227376.62 | 1575272.524 | 172704.838 | 176848.631 | 178187.425 | 174127.783 | 172055.835 | 175446.389 | 176848.322 | 178187.425 | 171406.523 | 1575813.171 | 6324003.785
MONTH -JULY -2005
Particulars | 2005-07-01 | 2005-07-02 | 2005-07-03 | 2005-07-04 | 2005-07-05 | 2005-07-06 | 2005-07-07 | 1 week | 2005-07-08 | 2005-07-09 | 2005-07-13 | 2005-07-14 | 2005-07-15 | 2005-07-16 | 2005-07-17 | 2 week | 2005-07-18 | 2005-07-19 | 2005-07-20 | 2005-07-21 | 2005-07-22 | 2005-07-23 | 2005-07-24 | 3 week | 2005-07-25 | 2005-07-26 | 2005-07-27 | 2005-07-28 | 2005-07-29 | 2005-07-30 | 2005-07-31 | 4 week | Total
Actual Steam Generated (Kgs) | 223413.3 | 223062.9 | 223163.1 | 223213.1 | 223012.9 | 223363.3 | 223263.1 | 1562491.7 | 222413.5 | 222063 | 222162.8 | 222213.1 | 222013.5 | 222363 | 222256 | 1555484.9 | 223113.9 | 222763.9 | 222863.9 | 222913.9 | 222713.9 | 223063.9 | 222963.9 | 1560397.3 | 222713.3 | 222362.9 | 222463.1 | 222513.1 | 222312.9 | 222663.2 | 222563.1 | 1557591.6 | 6235965.5
Coal Audited (Kgs) | 36404 | 36043 | 36146 | 36198 | 35991 | 36352 | 36249 | 253383 | 35373 | 35012 | 35115 | 35167 | 34961 | 35321 | 35218 | 246167 | 36094 | 35733 | 35836 | 35888 | 35682 | 36043 | 35940 | 251216 | 35682 | 35321 | 35425 | 35476 | 35271 | 35630 | 35529 | 248334 | 999100
Actual Coal Consumed (Kgs) | 35311.88 | 34961.71 | 35061.62 | 35112.06 | 34911.27 | 35261.44 | 35161.53 | 245781.51 | 34311.81 | 33961.64 | 34061.55 | 34111.99 | 33912.17 | 34261.37 | 34161.46 | 238781.99 | 35011.18 | 34661.01 | 34760.92 | 34811.36 | 34611.54 | 34961.71 | 34861.8 | 243679.52 | 34611.54 | 34261.37 | 34362.25 | 34411.72 | 34212.87 | 34561.1 | 34463.13 | 240883.98 | 969127
Feed Water Temp. deg. C | 72 | 71 | 73 | 73 | 74 | 71 | 70 | 72 | 72 | 74 | 73 | 74 | 75 | 75 | 75 | 74 | 71 | 75 | 72 | 73 | 73 | 74 | 73 | 73 | 73 | 71 | 74 | 74 | 72 | 75 | 72 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 230115.699 | 229754.787 | 229857.993 | 229909.493 | 229703.287 | 230064.199 | 229960.993 | 1609366.451 | 229085.905 | 228724.89 | 228827.684 | 228879.493 | 228673.905 | 229033.89 | 228923.68 | 1602149.447 | 229807.317 | 229446.817 | 229549.817 | 229601.317 | 229395.317 | 229755.817 | 229652.817 | 1607209.219 | 229394.699 | 229033.787 | 229136.993 | 229188.493 | 228982.287 | 229343.096 | 229239.993 | 1604319.348 | 6423044.465
MONTH -AUGUST -2005
Particulars | 2005-08-01 | 2005-08-02 | 2005-08-03 | 2005-08-04 | 2005-08-05 | 2005-08-06 | 2005-08-07 | 1 week | 2005-08-08 | 2005-08-09 | 2005-08-10 | 2005-08-11 | 2005-08-12 | 2005-08-13 | 2005-08-14 | 2 week | 2005-08-15 | 2005-08-16 | 2005-08-17 | 2005-08-18 | 2005-08-19 | 2005-08-20 | 2005-08-21 | 3 week | 2005-08-22 | 2005-08-23 | 2005-08-24 | 2005-08-25 | 2005-08-26 | 2005-08-27 | 2005-08-28 | 2005-08-29 | 2005-08-30 | 2005-08-31 | 4 week | Total
Actual Steam Generated (Kgs) | 215150 | 214500 | 217750 | 221000 | 227500 | 208000 | 214500 | 1518400 | 215040 | 195000 | 201600 | 212480 | 213200 | 205380 | 217750 | 1460450 | 218400 | 207900 | 213760 | 208000 | 200960 | 189000 | 208000 | 1446020 | 220500 | 228800 | 231400 | 214227.2 | 207900 | 217600 | 217750 | 222300 | 211680 | 226200 | 2198357.2 | 6623227.2
Coal Audited (Kgs) | 34124 | 34021 | 34536 | 35051 | 36082 | 32990 | 34021 | 240825 | 34639 | 30928 | 32990 | 34227 | 33814 | 33608 | 34536 | 234742 | 34639 | 34021 | 34433 | 32990 | 32371 | 30928 | 32990 | 232372 | 36082 | 36289 | 36701 | 34508 | 34021 | 35052 | 34536 | 35258 | 34639 | 35875 | 352961 | 1060900
Actual Coal Consumed (Kgs) | 33100.28 | 33000.37 | 33499.92 | 33999.47 | 34999.54 | 32000.3 | 33000.37 | 233600.25 | 33599.83 | 30000.16 | 32000.3 | 33200.19 | 32799.58 | 32599.76 | 33499.92 | 227699.74 | 33599.83 | 33000.37 | 33400.01 | 32000.3 | 31399.87 | 30000.16 | 32000.3 | 225400.84 | 34999.54 | 35200.33 | 35599.97 | 33472.76 | 33000.37 | 34000.44 | 33499.92 | 34200.26 | 33599.83 | 34798.75 | 342372.17 | 1029073
Feed Water Temp. deg. C | 74 | 73 | 75 | 72 | 75 | 74 | 75 | 74 | 73 | 72 | 74 | 73 | 74 | 71 | 74 | 73 | 74 | 75 | 76 | 73 | 76 | 75 | 76 | 75 | 75 | 75 | 74 | 73 | 72 | 74 | 75 | 74 | 73 | 75 | 74 | 74
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 221604.5 | 220935 | 224282.5 | 227630 | 234325 | 214240 | 220935 | 1563952 | 221491.2 | 200850 | 207648 | 218854.4 | 219596 | 211541.4 | 224282.5 | 1504263.5 | 224952 | 214137 | 220172.8 | 214240 | 206988.8 | 194670 | 214240 | 1489400.6 | 227115 | 235664 | 238342 | 220654.016 | 214137 | 224128 | 224282.5 | 228969 | 218030.4 | 232986 | 2264307.916 | 6821924.016
MONTH -SEPTEMBER -2005
Particulars | 2005-09-01 | 2005-09-02 | 2005-09-03 | 2005-09-04 | 2005-09-05 | 2005-09-06 | 2005-09-07 | 1 week | 2005-09-08 | 2005-09-09 | 2005-09-10 | 2005-09-11 | 2005-09-12 | 2005-09-13 | 2005-09-14 | 2 week | 2005-09-15 | 2005-09-16 | 2005-09-17 | 2005-09-18 | 2005-09-19 | 2005-09-20 | 2005-09-21 | 3 week | 2005-09-22 | 2005-09-23 | 2005-09-24 | 2005-09-25 | 2005-09-26 | 2005-09-27 | 2005-09-28 | 2005-09-29 | 2005-09-30 | 4 week | Total
Actual Steam Generated (Kgs) | 188500 | 198250 | 185250 | 188500 | 182000 | 188500 | 179400 | 1310400 | 169600 | 175500 | 166950 | 179200 | 195000 | 176400 | 190846.5 | 1253496.5 | 195000 | 204750 | 204800 | 206700 | 204800 | 214200 | 227500 | 1457750 | 211050 | 222300 | 224900 | 220800 | 214200 | 224000 | 223600 | 217750 | 217350 | 1975950 | 5997596.5
Coal Audited (Kgs) | 29897 | 31443 | 29381 | 29897 | 28866 | 29897 | 28454 | 207835 | 27320 | 27835 | 27320 | 28866 | 30928 | 28866 | 30269 | 201404 | 30928 | 33505 | 32990 | 32784 | 32988 | 35052 | 36082 | 234329 | 34536 | 35258 | 35670 | 35567 | 35052 | 36082 | 35464 | 34536 | 35567 | 317732 | 961300
Actual Coal Consumed (Kgs) | 29000.09 | 30499.71 | 28499.57 | 29000.09 | 28000.02 | 29000.09 | 27600.38 | 201599.95 | 26500.4 | 26999.95 | 26500.4 | 28000.02 | 30000.16 | 28000.02 | 29360.93 | 195361.88 | 30000.16 | 32499.85 | 32000.3 | 31800.48 | 31998.36 | 34000.44 | 34999.54 | 227299.13 | 33499.92 | 34200.26 | 34599.9 | 34499.99 | 34000.44 | 34999.54 | 34400.08 | 33499.92 | 34499.99 | 308200.04 | 932461
Feed Water Temp. deg. C | 71 | 73 | 72 | 73 | 75 | 73 | 74 | 73 | 72 | 71 | 70 | 74 | 75 | 70 | 72 | 72 | 71 | 70 | 72 | 73 | 70 | 71 | 70 | 71 | 72 | 73 | 74 | 72 | 70 | 71 | 72 | 71 | 73 | 72 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 194155 | 204197.5 | 190807.5 | 194155 | 187460 | 194155 | 184782 | 1349712 | 174688 | 180765 | 171958.5 | 184576 | 200850 | 181692 | 196571.895 | 1291101.395 | 200850 | 210892.5 | 210944 | 212901 | 210944 | 220626 | 234325 | 1501482.5 | 217381.5 | 228969 | 231647 | 227424 | 220626 | 230720 | 230308 | 224282.5 | 223870.5 | 2035228.5 | 6177524.395
MONTH -OCTOBER -2005
Particulars | 2005-10-01 | 2005-10-02 | 2005-10-03 | 2005-10-04 | 2005-10-05 | 2005-10-06 | 2005-10-07 | 1 week | 2005-10-08 | 2005-10-09 | 2005-10-10 | 2005-10-11 | 2005-10-12 | 2005-10-13 | 2005-10-14 | 2 week | 2005-10-15 | 2005-10-16 | 2005-10-17 | 2005-10-18 | 2005-10-19 | 2005-10-20 | 2005-10-21 | 3 week | 2005-10-22 | 2005-10-23 | 2005-10-24 | 2005-10-25 | 2005-10-26 | 2005-10-27 | 2005-10-28 | 2005-10-29 | 2005-10-30 | 2005-10-31 | 4 week | Total
Actual Steam Generated (Kgs) | 208000 | 201500 | 195000 | 201500 | 195000 | 201500 | 183841.1 | 1386341.1 | 204800 | 221000 | 207900 | 204800 | 211250 | 211050 | 214500 | 1475300 | 218400 | 214200 | 220800 | 226200 | 225280 | 207900 | 208000 | 1520780 | 209160 | 201500 | 218400 | 217600 | 217350 | 208640 | 226200 | 221000 | 220500 | 224900 | 2165250 | 6547671.1
Coal Audited (Kgs) | 32990 | 31959 | 30928 | 31959 | 30928 | 31959 | 29158 | 219881 | 32990 | 35052 | 34021 | 32990 | 33505 | 34536 | 34021 | 237115 | 34639 | 35052 | 35567 | 35876 | 36289 | 34022 | 32990 | 244435 | 34227 | 31959 | 34639 | 35052 | 35567 | 33608 | 35876 | 35052 | 36082 | 35665 | 347727 | 1049158
Actual Coal Consumed (Kgs) | 32000.3 | 31000.23 | 30000.16 | 31000.23 | 30000.16 | 31000.23 | 28283.26 | 213284.57 | 32000.3 | 34000.44 | 33000.37 | 32000.3 | 32499.85 | 33499.92 | 33000.37 | 230001.55 | 33599.83 | 34000.44 | 34499.99 | 34799.72 | 35200.33 | 33001.34 | 32000.3 | 237101.95 | 33200.19 | 31000.23 | 33599.83 | 34000.44 | 34499.99 | 32599.76 | 34799.72 | 34000.44 | 34999.54 | 34595.05 | 337295.19 | 1017683.26
Feed Water Temp. deg. C | 70 | 71 | 72 | 74 | 74 | 72 | 71 | 72 | 73 | 73 | 72 | 71 | 75 | 74 | 73 | 73 | 70 | 71 | 72 | 70 | 75 | 74 | 72 | 72 | 73 | 72 | 70 | 70 | 71 | 70 | 72 | 71 | 70 | 71 | 71 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 214240 | 207545 | 200850 | 207545 | 200850 | 207545 | 189356.333 | 1427931.333 | 210944 | 227630 | 214137 | 210944 | 217587.5 | 217381.5 | 220935 | 1519559 | 224952 | 220626 | 227424 | 232986 | 232038.4 | 214137 | 214240 | 1566403.4 | 215434.8 | 207545 | 224952 | 224128 | 223870.5 | 214899.2 | 232986 | 227630 | 227115 | 231647 | 2230207.5 | 6744101.233
MONTH -NOVEMBER -2005
Particulars | 2005-11-01 | 2005-11-02 | 2005-11-03 | 2005-11-04 | 2005-11-05 | 2005-11-06 | 2005-11-07 | 1 week | 2005-11-08 | 2005-11-09 | 2005-11-10 | 2005-11-11 | 2005-11-12 | 2005-11-13 | 2005-11-14 | 2 week | 2005-11-15 | 2005-11-16 | 2005-11-17 | 2005-11-18 | 2005-11-19 | 2005-11-20 | 2005-11-21 | 3 week | 2005-11-22 | 2005-11-23 | 2005-11-24 | 2005-11-25 | 2005-11-26 | 2005-11-27 | 2005-11-28 | 2005-11-29 | 2005-11-30 | 4 week | Total
Actual Steam Generated (Kgs) | 182000 | 175500 | 178750 | 179400 | 182000 | 183300 | 179004.9 | 1259954.9 | 188800 | 195000 | 204750 | 211200 | 227500 | 204750 | 218400 | 1450400 | 208000 | 207900 | 204800 | 221000 | 217600 | 217980 | 222300 | 1499580 | 192150 | 195000 | 201500 | 211200 | 204750 | 192000 | 201500 | 195000 | 199206 | 1792306 | 6002240.9
Coal Audited (Kgs) | 28866 | 27835 | 28351 | 28454 | 28866 | 29073 | 28391 | 199836 | 30412 | 30928 | 33505 | 34022 | 36082 | 33505 | 34639 | 233093 | 32990 | 34021 | 32988 | 35052 | 35052 | 35670 | 35258 | 241031 | 31443 | 30928 | 31959 | 34021 | 33504 | 30928 | 31957 | 30928 | 32598 | 288266 | 962226
Actual Coal Consumed (Kgs) | 28000.02 | 26999.95 | 27500.47 | 27600.38 | 28000.02 | 28200.81 | 27539.27 | 193840.92 | 29499.64 | 30000.16 | 32499.85 | 33001.34 | 34999.54 | 32499.85 | 33599.83 | 226100.21 | 32000.3 | 33000.37 | 31998.36 | 34000.44 | 34000.44 | 34599.9 | 34200.26 | 233800.07 | 30499.71 | 30000.16 | 31000.23 | 33000.37 | 32498.88 | 30000.16 | 30998.29 | 30000.16 | 31620.06 | 279618.02 | 933359.22
Feed Water Temp. deg. C | 71 | 75 | 74 | 73 | 73 | 73 | 72 | 73 | 71 | 72 | 74 | 74 | 72 | 71 | 70 | 72 | 75 | 72 | 75 | 73 | 75 | 74 | 74 | 74 | 71 | 72 | 73 | 75 | 73 | 74 | 72 | 73 | 74 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 187460 | 180765 | 184112.5 | 184782 | 187460 | 188799 | 184375.047 | 1297753.547 | 194464 | 200850 | 210892.5 | 217536 | 234325 | 210892.5 | 224952 | 1493912 | 214240 | 214137 | 210944 | 227630 | 224128 | 224519.4 | 228969 | 1544567.4 | 197914.5 | 200850 | 207545 | 217536 | 210892.5 | 197760 | 207545 | 200850 | 205182.18 | 1846075.18 | 6182308.127
MONTH -DECEMBER -2005
Particulars | 2005-12-01 | 2005-12-02 | 2005-12-03 | 2005-12-04 | 2005-12-05 | 2005-12-06 | 2005-12-07 | 1 week | 2005-12-08 | 2005-12-09 | 2005-12-10 | 2005-12-11 | 2005-12-12 | 2005-12-13 | 2005-12-14 | 2 week | 2005-12-15 | 2005-12-16 | 2005-12-17 | 2005-12-18 | 2005-12-19 | 2005-12-20 | 2005-12-21 | 3 week | 2005-12-22 | 2005-12-23 | 2005-12-24 | 2005-12-25 | 2005-12-26 | 2005-12-27 | 2005-12-28 | 2005-12-29 | 2005-12-30 | 2005-12-31 | 4 week | Total
Actual Steam Generated (Kgs) | 230100 | 229450 | 229450 | 226200 | 232700 | 227500 | 234000 | 1609400 | 192000 | 182000 | 179550 | 185600 | 191750 | 157500 | 162500 | 1250900 | 182000 | 166950 | 179200 | 182000 | 188800 | 182700 | 195000 | 1276650 | 201600 | 217750 | 221000 | 229120 | 224280 | 227200 | 234000 | 227500 | 221186.7 | 227500 | 2231136.7 | 6368086.7
Coal Audited (Kgs) | 36495 | 36392 | 36392 | 35876 | 36908 | 36082 | 37113 | 255258 | 30928 | 28866 | 29382 | 29897 | 30412 | 25773 | 25773 | 201031 | 28866 | 27320 | 28866 | 28866 | 30412 | 29897 | 30928 | 205155 | 32990 | 34536 | 35052 | 36907 | 36701 | 36598 | 37113 | 36082 | 36195 | 36082 | 358256 | 1019700
Actual Coal Consumed (Kgs) | 35400.15 | 35300.24 | 35300.24 | 34799.72 | 35800.76 | 34999.54 | 35999.61 | 247600.26 | 30000.16 | 28000.02 | 28500.54 | 29000.09 | 29499.64 | 24999.81 | 24999.81 | 195000.07 | 28000.02 | 26500.4 | 28000.02 | 28000.02 | 29499.64 | 29000.09 | 30000.16 | 199000.35 | 32000.3 | 33499.92 | 34000.44 | 35799.79 | 35599.97 | 35500.06 | 35999.61 | 34999.54 | 35109.15 | 34999.54 | 347508.32 | 989109
Feed Water Temp. deg. C | 75 | 73 | 74 | 71 | 73 | 72 | 73 | 73 | 75 | 75 | 74 | 72 | 73 | 74 | 75 | 74 | 72 | 75 | 74 | 73 | 75 | 74 | 75 | 74 | 76 | 76 | 75 | 74 | 75 | 74 | 73 | 76 | 76 | 75 | 75 | 74
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg./ Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumed (Kg) | 237003 | 236333.5 | 236333.5 | 232986 | 239681 | 234325 | 241020 | 1657682 | 197760 | 187460 | 184936.5 | 191168 | 197502.5 | 162225 | 167375 | 1288427 | 187460 | 171958.5 | 184576 | 187460 | 194464 | 188181 | 200850 | 1314949.5 | 207648 | 224282.5 | 227630 | 235993.6 | 231008.4 | 234016 | 241020 | 234325 | 227822.301 | 234325 | 2298070.801 | 6559129.301
MONTH -JANUARY -2006
Particulars | 2006-01-01 | 2006-01-02 | 2006-01-03 | 2006-01-04 | 2006-01-05 | 2006-01-06 | 2006-01-07 | 1 week | 2006-01-08 | 2006-01-09 | 2006-01-10 | 2006-01-11 | 2006-01-12 | 2006-01-13 | 2006-01-14 | 2 week | 2006-01-15 | 2006-01-16 | 2006-01-17 | 2006-01-18 | 2006-01-19 | 2006-01-20 | 2006-01-21 | 3 week | 2006-01-22 | 2006-01-23 | 2006-01-24 | 2006-01-25 | 2006-01-26 | 2006-01-27 | 2006-01-28 | 2006-01-29 | 2006-01-30 | 2006-01-31 | 4 week | Total
Actual Steam Generated (Kgs) | 220000 | 215000 | 216000 | 220000 | 222000 | 225000 | 226000 | 1544000 | 223000 | 231000 | 223000 | 232000 | 216000 | 221000 | 222000 | 1568000 | 222500 | 224500 | 225500 | 231500 | 230500 | 229500 | 228500 | 1592500 | 227500 | 226510 | 223600 | 224615 | 235400 | 221300 | 222500 | 226000 | 234000 | 226100 | 2267525 | 6972025
Coal Audited (Kgs) | 33505 | 35052 | 35155 | 35052 | 36082 | 36701 | 36082 | 247629 | 36495 | 36804 | 36701 | 36495 | 36700 | 36289 | 36289 | 255773 | 36031 | 36701 | 36753 | 36959 | 37010 | 36907 | 35979 | 256340 | 36082 | 35670 | 36701 | 36701 | 35876 | 35979 | 35876 | 35979 | 35930 | 36928 | 361722 | 1121464
Actual Coal Consumed | 32499.85 | 34000.44 | 34100.35 | 34000.44 | 34999.54 | 35599.97 | 34999.54 | 240200.13 | 35400.15 | 35699.88 | 35599.97 | 35400.15 | 35599 | 35200.33 | 35200.33 | 248099.81 | 34950.07 | 35599.97 | 35650.41 | 35850.23 | 35899.7 | 35799.79 | 34899.63 | 248649.8 | 34999.54 | 34599.9 | 35599.97 | 35599.97 | 34799.72 | 34899.63 | 34799.72 | 34899.63 | 34852.1 | 35820.16 | 350870.34 | 1087820.08
Feed Water Temp. deg. C | 72 | 71 | 72 | 74 | 74 | 70 | 71 | 72 | 71 | 73 | 74 | 75 | 73 | 72 | 73 | 73 | 74 | 72 | 74 | 75 | 73 | 75 | 75 | 74 | 72 | 71 | 73 | 75 | 74 | 73 | 74 | 72 | 74 | 72 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg. / Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumption (Kg. ) | 226600 | 221450 | 222480 | 226600 | 228660 | 231750 | 232780 | 1590320 | 229690 | 237930 | 229690 | 238960 | 222480 | 227630 | 228660 | 1615040 | 229175 | 231235 | 232265 | 238445 | 237415 | 236385 | 235355 | 1640275 | 234325 | 233305.3 | 230308 | 231353.45 | 242462 | 227939 | 229175 | 232780 | 241020 | 232883 | 2335550.75 | 7181185.75
MONTH -FEBRUARY -2006
Particulars | 2006-02-01 | 2006-02-02 | 2006-02-03 | 2006-02-04 | 2006-02-05 | 2006-02-06 | 2006-02-07 | 1 week | 2006-02-08 | 2006-02-09 | 2006-02-10 | 2006-02-11 | 2006-02-12 | 2006-02-13 | 2006-02-14 | 2 week | 2006-02-15 | 2006-02-16 | 2006-02-17 | 2006-02-18 | 2006-02-19 | 2006-02-20 | 2006-02-21 | 3 week | 2006-02-22 | 2006-02-23 | 2006-02-24 | 2006-02-25 | 2006-02-26 | 2006-02-27 | 2006-02-28 | 4 week | Total
Actual Steam Generated (Kgs) | 218000 | 219000 | 218000 | 217500 | 190000 | 218000 | 217600 | 1498100 | 215000 | 218000 | 220000 | 219000 | 200000 | 215000 | 230000 | 1517000 | 225000 | 219500 | 218000 | 220000 | 195000 | 208000 | 218000 | 1503500 | 230000 | 220000 | 227000 | 231000 | 226000 | 220000 | 190000 | 1544000 | 6062600
Coal Audited (Kgs) | 34536 | 37113 | 35052 | 35052 | 29897 | 36082 | 36289 | 244021 | 34639 | 36082 | 36598 | 36907 | 30928 | 34537 | 37526 | 247217 | 35052 | 35052 | 32990 | 35052 | 30928 | 32475 | 35052 | 236601 | 39175 | 37113 | 38144 | 39175 | 37321 | 36082 | 30861 | 257871 | 985710
Actual Coal Consumed | 33499.92 | 35999.61 | 34000.44 | 34000.44 | 29000.09 | 34999.54 | 35200.33 | 236700.37 | 33599.83 | 34999.54 | 35500.06 | 35799.79 | 30000.16 | 33500.89 | 36400.22 | 239800.49 | 34000.44 | 34000.44 | 32000.3 | 34000.44 | 30000.16 | 31500.75 | 34000.44 | 229502.97 | 37999.75 | 35999.61 | 36999.68 | 37999.75 | 36201.37 | 34999.54 | 29935.17 | 250134.87 | 956138.7
Feed Water Temp. deg. C | 72 | 71 | 71 | 74 | 72 | 73 | 71 | 72 | 74 | 72 | 73 | 74 | 73 | 73 | 72 | 73 | 72 | 71 | 73 | 70 | 70 | 71 | 70 | 71 | 71 | 72 | 72 | 73 | 72 | 71 | 73 | 72 | 72
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg. / Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumption (Kg. ) | 224540 | 225570 | 224540 | 224025 | 195700 | 224540 | 224128 | 1543043 | 221450 | 224540 | 226600 | 225570 | 206000 | 221450 | 236900 | 1562510 | 231750 | 226085 | 224540 | 226600 | 200850 | 214240 | 224540 | 1548605 | 236900 | 226600 | 233810 | 237930 | 232780 | 226600 | 195700 | 1590320 | 6244478
MONTH -MARCH -2006
Particulars | 2006-03-01 | 2006-03-02 | 2006-03-03 | 2006-03-04 | 2006-03-05 | 2006-03-06 | 2006-03-07 | 1 week | 2006-03-08 | 2006-03-09 | 2006-03-10 | 2006-03-11 | 2006-03-12 | 2006-03-13 | 2006-03-14 | 2 week | 2006-03-15 | 2006-03-16 | 2006-03-17 | 2006-03-18 | 2006-03-19 | 2006-03-20 | 2006-03-21 | 3 week | 2006-03-22 | 2006-03-23 | 2006-03-24 | 2006-03-25 | 2006-03-26 | 2006-03-27 | 2006-03-28 | 2006-03-29 | 2006-03-30 | 2006-03-31 | 4 week | Total
Actual Steam Generated (Kgs) | 154798.3 | 157561.2 | 160848.8 | 158425.1 | 157708.2 | 164349.6 | 160973.8 | 1114665 | 161248.8 | 154342.3 | 154606.3 | 158026.7 | 154462.2 | 161123.8 | 154486.4 | 1098296.5 | 154798.3 | 156556.7 | 161148.8 | 158051.2 | 154558.3 | 161048.8 | 144675.8 | 1090837.9 | 154630.3 | 148347.9 | 146135.3 | 144765.7 | 151294.2 | 147979.9 | 144923.3 | 154606.3 | 150768.1 | 160936.3 | 1504387.3 | 4808186.7
Coal Audited (Kgs) | 24742 | 25258 | 25773 | 25361 | 25258 | 26289 | 25773 | 178454 | 25773 | 24742 | 24742 | 25258 | 24742 | 25773 | 24742 | 175772 | 24742 | 25258 | 25773 | 25258 | 24742 | 25773 | 23196 | 174742 | 24742 | 23711 | 23430 | 23196 | 24227 | 23711 | 23196 | 24742 | 24124 | 25775 | 240854 | 769822
Actual Coal Consumed | 23999.74 | 24500.26 | 24999.81 | 24600.17 | 24500.26 | 25500.33 | 24999.81 | 173100.38 | 24999.81 | 23999.74 | 23999.74 | 24500.26 | 23999.74 | 24999.81 | 23999.74 | 170498.84 | 23999.74 | 24500.26 | 24999.81 | 24500.26 | 23999.74 | 24999.81 | 22500.12 | 169499.74 | 23999.74 | 22999.67 | 22727.1 | 22500.12 | 23500.19 | 22999.67 | 22500.12 | 23999.74 | 23400.28 | 25001.75 | 233628.38 | 746727.34
Feed Water Temp. deg. C | 72 | 71 | 72 | 75 | 73 | 71 | 70 | 72 | 73 | 72 | 73 | 74 | 73 | 71 | 75 | 73 | 72 | 74 | 75 | 76 | 73 | 74 | 74 | 74 | 73 | 72 | 72 | 73 | 74 | 75 | 72 | 71 | 75 | 73 | 73 | 73
Blowdown Loss (%) | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
Steam Pressure ( Kg. / Cm2 ) | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83 | 8.83
Feed Water Consumption (Kg. ) | 159442.249 | 162288.036 | 165674.264 | 163177.853 | 162439.446 | 169280.088 | 165803.014 | 1148104.95 | 166086.264 | 158972.569 | 159244.489 | 162767.501 | 159096.066 | 165957.514 | 159120.992 | 1131245.395 | 159442.249 | 161253.401 | 165983.264 | 162792.736 | 159195.049 | 165880.264 | 149016.074 | 1123563.037 | 159269.209 | 152798.337 | 150519.359 | 149108.671 | 155833.026 | 152419.297 | 149270.999 | 159244.489 | 155291.143 | 165764.389 | 1549518.919 | 4952432.301

## CER Estimation_05-06
Monitored Parameters for the year 2005-2006
Months | Quantity of Coal Used | Coal-Audited | Gross Calorific Value of Coal | Heat Energy Input | Steam Load | Steam Pressure | Steam Pressure | Steam Enthalpy | Feed water Load | Feed Water Temerature | Feed Water Enthalpy | Number of Truck Trips
Units | (tons) | (tons) | (kCal/kg) | (kCal) | (tons) | (Bar) | (kg/cm2) | (kCal) | (tons) | (°C) | (kCal)
April '05 | 1014.0865 | 1045.45 | 5565 | 5643391372.5 | 6525.557 | 8.83 | 9 | 4330888863.0772 | 6721.3237 | 72 | 483646991.1875 | 91 | Temperature | Feed Water Enthalpy
May '05 | 949.145 | 978.5 | 5565 | 5281991925 | 6109.7638 | 8.83 | 9 | 4054934773.7599 | 6293.0567 | 73 | 459128004.9205 | 52 | (0C) | (kJ/kg)
June'05 | 954.1405 | 983.65 | 5565 | 5309791882.5 | 6139.8095 | 8.83 | 9 | 4074875537.0562 | 6324.0038 | 74 | 467714674.6144 | 14 | 64 | 267.79
July'05 | 969.127 | 999.1 | 5565 | 5393191755 | 6235.9655 | 8.83 | 9 | 4138692457.1318 | 6423.0445 | 73 | 468611634.1794 | 150 | 65 | 271.97
August'05 | 1029.073 | 1060.9 | 5565 | 5726791245 | 6623.2272 | 8.83 | 9 | 4395710729.078 | 6821.924 | 74 | 504540174.2098 | 85 | 66 | 276.16
September'05 | 932.461 | 961.3 | 5565 | 5189145465 | 5997.5965 | 8.83 | 9 | 3980491456.4506 | 6177.5244 | 72 | 444516767.1636 | 38 | 67 | 280.34
October'05 | 1017.6833 | 1049.158 | 5565 | 5663407341.9 | 6547.6711 | 8.83 | 9 | 4345565573.3423 | 6744.1012 | 72 | 485285995.7855 | 48 | 68 | 284.52
November'05 | 933.3592 | 962.226 | 5565 | 5194144059.3 | 6002.2409 | 8.83 | 9 | 3983573856.9622 | 6182.3081 | 73 | 451048024.0609 | 102 | 72 | 301.27
December'05 | 989.109 | 1019.7 | 5565 | 5504391585 | 6368.0867 | 8.83 | 9 | 4226378800.789 | 6559.1293 | 74 | 485104236.3459 | 67 | 73 | 305.46
January'06 | 1087.8201 | 1121.464 | 5565 | 6053718745.2 | 6972.025 | 8.83 | 9 | 4627201237.4723 | 7181.1857 | 73 | 523924006.4412 | 47 | 74 | 309.65
Febraury'06 | 956.1387 | 985.71 | 5400 | 5163148980 | 6062.6 | 8.83 | 9 | 4023633050.9859 | 6244.478 | 72 | 449334554.7013 | 49
March'06 | 746.7273 | 769.822 | 5565 | 4155537647.1 | 4808.1867 | 8.83 | 9 | 3191102649.2645 | 4952.4323 | 73 | 361318905.1361 | 41
2005-2006 | 11578.8706 | 11936.98 | 5551.25 | 64278652003.5 | 74392.7299 | 8.83 | 9 | 49373048985.37 | 76624.5118 | 72.9167 | 5584173968.746 | 784
Computation of Emission Reductions for the year 2005-2006
Months | Output Enthalpy | Baseline Boiler Efficiency | Baseline Technical Losses | Boiler Efficiency | Technical Losses | Reduction in Losses | Coal Reduction | Fixed Carbon Content (C%) in Coal | Emission Co-efficienct of Coal | Emission Reductions
| (kCal) | (%) | (kCal) | (%) | (kCal) | (kCal) | (kgs) | ('%) | (kgCO2/kCal) | (tons)
April '05 | 3847241871.8898 | 53.9271 | 3286906551.4854 | 68.1725 | 1796149500.6102 | 1490757050.8752 | 267880.8717 | 0.43228 | 0.00028482 | -
March '05 | 3595806768.8395 | 53.9271 | 3072091960.9269 | 68.0767 | 1686185156.1605 | 1385906804.7664 | 249039.8571 | 0.49345 | 0.00032512 | -
June'05 | 3607160862.4418 | 53.9271 | 3081792376.4169 | 67.9341 | 1702631020.0582 | 1379161356.3588 | 247827.737 | 0.48137 | 0.00031717 | -
July'05 | 3670080822.9525 | 53.9271 | 3135548297.4919 | 68.0503 | 1723110932.0475 | 1412437365.4444 | 253807.2534 | 0.46165 | 0.00030417 | -
August'05 | 3891170554.8682 | 53.9271 | 3324437198.2937 | 67.9468 | 1835620690.1318 | 1488816508.1619 | 267532.1668 | 0.4681 | 0.00030842 | -
September'05 | 3535974689.287 | 53.9271 | 3020974183.3557 | 68.1418 | 1653170775.713 | 1367803407.6426 | 245786.7759 | 0.48452 | 0.00031924 | -
October'05 | 3860279577.5567 | 53.9271 | 3298045367.7076 | 68.1618 | 1803127764.3433 | 1494917603.3643 | 268628.5002 | 0.44577 | 0.00029371 | -
November'05 | 3532525832.9013 | 53.9271 | 3018027639.045 | 68.0098 | 1661618226.3987 | 1356409412.6463 | 243739.3374 | 0.52112 | 0.00034336 | -
December'05 | 3741274564.4432 | 53.9271 | 3196372956.5912 | 67.9689 | 1763117020.5568 | 1433255936.0344 | 257548.2365 | 0.47732 | 0.0003145 | -
January'06 | 4103277231.0311 | 53.9271 | 3505651389.3191 | 67.7811 | 1950441514.1689 | 90534554.7057 | 16268.5633 | 0.43145 | 0.00028427 | -
Febraury'06 | 3574298496.2845 | 53.9271 | 3053716281.8492 | 69.2271 | 1588850483.7155 | - | - | 0.39205 | 0.00026621 | -
March'06 | 2829783744.1284 | 53.9271 | 2417637111.8808 | 68.0967 | 1325753902.9716 | - | - | 0.48252 | 0.00031793 | -
2005-2006 | 43788875016.6239 | 53.9271 | 37411201314.3634 | 68.1306 | 20489776986.8761 | 12900000000 | 2318059.2992 | 0.4643 | 0.00030658 | 0
Reduction in Losses (in GWhe) |  | 15 | = 15

## Weekly Fixed Carbon-GCV
Gross Calorific Value, Fixed Carbon and Emission Factor of Coal Consumed
2001-2002
Month | Week 1 |  | Week 2 |  | Week 3 |  | Week 4 |  | Mothly Average GCV | Mothly Average Fixed Carbon
| GCV | Fixed Carbon | GCV | Fixed Carbon | GCV | Fixed Carbon | GCV | Fixed Carbon
April 2001 | 5772 | 0.5436 | 5992 | 0.535 | 5800 | 0.5495 | 5964 | 0.5297 | 5882 | 0.53945
May 2001 | 5511 | 0.4888 | 5951 | 0.5812 | 5700 | 0.5285 | 5762 | 0.5415 | 5731 | 0.535
June 2001 | 5800 | 0.5495 | 5856 | 0.5613 | 5804 | 0.5503 | 5852 | 0.5604 | 5828 | 0.55537
July 2001 | 5900 | 0.5433 | 5954 | 0.5541 | 5925 | 0.5483 | 5929 | 0.5491 | 5927 | 0.5487
August 2001 | 5700 | 0.5285 | 5746 | 0.5382 | 5600 | 0.5075 | 5846 | 0.5592 | 5723 | 0.53335
September 2001 | 5900 | 0.5433 | 5910 | 0.5453 | 5902 | 0.5437 | 5908 | 0.5449 | 5905 | 0.5443
October 2001 | 5475 | 0.4813 | 5697 | 0.5279 | 5575 | 0.5023 | 5597 | 0.5069 | 5586 | 0.5046
November 2001 | 5766 | 0.5424 | 5788 | 0.547 | 5776 | 0.5445 | 5778 | 0.5449 | 5777 | 0.5447
December 2001 | 5629 | 0.5136 | 5809 | 0.5514 | 5729 | 0.5346 | 5709 | 0.5304 | 5719 | 0.5325
January 2002 | 5800 | 0.5495 | 5990 | 0.5613 | 5820 | 0.5537 | 5748 | 0.5129 | 5840 | 0.54435
February 2002 | 5588 | 0.505 | 5810 | 0.5516 | 5699 | 0.5283 | 5699 | 0.5283 | 5699 | 0.5283
March 2002 | 5601 | 0.5077 | 5632 | 0.5142 | 5720 | 0.5327 | 5530 | 0.4928 | 5621 | 0.51185
2002-2003
Month | Week 1 |  | Week 2 |  | Week 3 |  | Week 4 |  | Mothly Average GCV | Mothly Average Fixed Carbon
| GCV | Fixed Carbon | GCV | Fixed Carbon | GCV | Fixed Carbon | GCV | Fixed Carbon
April 2002 | 6120 | 0.5339 | 6138 | 0.5372 | 6149 | 0.5392 | 6109 | 0.5319 | 6129 | 0.53555
May 2002 | 5673 | 0.5228 | 5703 | 0.5291 | 5863 | 0.5627 | 5893 | 0.569 | 5783 | 0.5459
June 2002 | 5660 | 0.5201 | 5680 | 0.5243 | 5560 | 0.4991 | 5780 | 0.5453 | 5670 | 0.5222
July 2002 | 6115 | 0.533 | 6129 | 0.5356 | 6123 | 0.5345 | 6137 | 0.537 | 6126 | 0.53502
August 2002 | 5848 | 0.5596 | 5826 | 0.555 | 5800 | 0.5495 | 5874 | 0.565 | 5837 | 0.55727
September 2002 | 5322 | 0.5133 | 5422 | 0.5373 | 5482 | 0.5517 | 5542 | 0.5661 | 5442 | 0.5421
October 2002 | 5608 | 0.5092 | 5700 | 0.5285 | 5718 | 0.5323 | 5810 | 0.5516 | 5709 | 0.5304
November 2002 | 5700 | 0.5285 | 5740 | 0.5369 | 5710 | 0.5306 | 5730 | 0.5348 | 5720 | 0.5327
December 2002 | 5552 | 0.4974 | 5594 | 0.5062 | 5471 | 0.4804 | 5675 | 0.5233 | 5573 | 0.50182
January 2003 | 5905 | 0.5443 | 5900 | 0.5433 | 5910 | 0.5453 | 5905 | 0.5443 | 5905 | 0.5443
February 2003 | 5465 | 0.502 | 5667 | 0.5464 | 5575 | 0.5262 | 5557 | 0.5222 | 5566 | 0.5242
March 2003 | 5604 | 0.5083 | 5704 | 0.5293 | 5644 | 0.5167 | 5664 | 0.5209 | 5654 | 0.5188
2003-2004
Month | Week 1 |  | Week 2 |  | Week 3 |  | Week 4 |  | Mothly Average GCV | Mothly Average Fixed Carbon
| GCV | Fixed Carbon | GCV | Fixed Carbon | GCV | Fixed Carbon | GCV | Fixed Carbon
April 2003 | 5905 | 0.5443 | 5925 | 0.5483 | 5900 | 0.5433 | 5890 | 0.5413 | 5905 | 0.5443
May 2003 | 5528 | 0.5158 | 5700 | 0.5537 | 5447 | 0.498 | 5589 | 0.5292 | 5566 | 0.52417
June 2003 | 5654 | 0.5188 | 5674 | 0.523 | 5649 | 0.5178 | 5639 | 0.5157 | 5654 | 0.51882
July 2003 | 5908 | 0.5449 | 5925 | 0.5483 | 5900 | 0.5433 | 5886 | 0.5405 | 5905 | 0.54425
August 2003 | 5565 | 0.524 | 5589 | 0.5292 | 5560 | 0.5229 | 5550 | 0.5207 | 5566 | 0.5242
September 2003 | 5654 | 0.5188 | 5674 | 0.523 | 5649 | 0.5178 | 5639 | 0.5157 | 5654 | 0.51882
October 2003 | 5905 | 0.5443 | 5935 | 0.5503 | 5910 | 0.5453 | 5868 | 0.5369 | 5905 | 0.5442
November 2003 | 5566 | 0.5242 | 5586 | 0.5286 | 5561 | 0.5231 | 5551 | 0.5209 | 5566 | 0.5242
December 2003 | 5654 | 0.5435 | 5674 | 0.5479 | 5649 | 0.5424 | 5639 | 0.5402 | 5654 | 0.5435
January 2004 | 5565 | 0.524 | 5585 | 0.5284 | 5560 | 0.5229 | 5550 | 0.5207 | 5565 | 0.524
February 2004 | 5565 | 0.5335 | 5585 | 0.538 | 5560 | 0.5324 | 5550 | 0.5301 | 5565 | 0.5335
March 2004 | 5581 | 0.5419 | 5569 | 0.5392 | 5576 | 0.5407 | 5534 | 0.5313 | 5565 | 0.53827
2004-2005
Month | Week 1 |  | Week 2 |  | Week 3 |  | Week 4 |  | Mothly Average GCV | Mothly Average Fixed Carbon
| GCV | Fixed Carbon | GCV | Fixed Carbon | GCV | Fixed Carbon | GCV | Fixed Carbon
April 2004 | 5560 | 0.5229 | 5570 | 0.5251 | 5590 | 0.5295 | 5540 | 0.542 | 5565 | 0.52987
May 2004 | 5575 | 0.5262 | 5562 | 0.5233 | 5535 | 0.5409 | 5587 | 0.5528 | 5565 | 0.5358
June 2004 | 5572 | 0.5494 | 5596 | 0.5549 | 5528 | 0.5393 | 5487 | 0.5529 | 5546 | 0.54912
July 2004 | 5467 | 0.5252 | 5678 | 0.5239 | 5564 | 0.5476 | 5689 | 0.5262 | 5600 | 0.53073
August 2004 | 5534 | 0.4936 | 5789 | 0.5472 | 5643 | 0.5657 | 5896 | 0.5697 | 5716 | 0.54405
September 2004 | 5567 | 0.5482 | 5892 | 0.5417 | 5386 | 0.5286 | 5454 | 0.545 | 5575 | 0.54087
October 2004 | 5676 | 0.5235 | 5278 | 0.5027 | 5788 | 0.547 | 5877 | 0.5657 | 5655 | 0.53473
November 2004 | 5482 | 0.5517 | 5644 | 0.5413 | 5784 | 0.5461 | 5399 | 0.5318 | 5578 | 0.54273
December 2004 | 5288 | 0.5051 | 5467 | 0.5481 | 5788 | 0.547 | 5862 | 0.5625 | 5602 | 0.54068
January 2005 | 5552 | 0.5211 | 5498 | 0.5092 | 5786 | 0.5466 | 5699 | 0.5283 | 5634 | 0.5263
February 2005 | 5356 | 0.4997 | 5588 | 0.505 | 5676 | 0.5235 | 5788 | 0.547 | 5602 | 0.5188
March 2005 | 5688 | 0.526 | 5795 | 0.5485 | 5982 | 0.5877 | 5222 | 0.5097 | 5672 | 0.54297
2005-2006
Month | Week 1 |  | Week 2 |  | Week 3 |  | Week 4 |  | Mothly Average GCV | Mothly Average Fixed Carbon
| GCV | Fixed Carbon | GCV | Fixed Carbon | GCV | Fixed Carbon | GCV | Fixed Carbon
April 2005 | 5815 | 0.4289 | 5450 | 0.4609 | 5745 | 0.3967 | 5250 | 0.4426 | 5565 | 0.43228
May 2005 | 5684 | 0.5838 | 5445 | 0.4616 | 5766 | 0.397 | 5365 | 0.5314 | 5565 | 0.49345
June 2005 | 5790 | 0.4303 | 5385 | 0.5312 | 5620 | 0.5113 | 5465 | 0.4527 | 5565 | 0.48137
July 2005 | 5834 | 0.428 | 5415 | 0.4552 | 5606 | 0.5107 | 5405 | 0.4527 | 5565 | 0.46165
August 2005 | 5866 | 0.4257 | 5495 | 0.4618 | 5634 | 0.5281 | 5265 | 0.4568 | 5565 | 0.4681
September 2005 | 5787 | 0.4293 | 5365 | 0.5313 | 5643 | 0.5238 | 5465 | 0.4537 | 5565 | 0.48452
October 2005 | 5744 | 0.394 | 5315 | 0.5177 | 5786 | 0.3998 | 5415 | 0.4716 | 5565 | 0.44577
November 2005 | 5847 | 0.4338 | 5383 | 0.5294 | 5687 | 0.5912 | 5343 | 0.5301 | 5565 | 0.52112
December 2005 | 5790 | 0.4234 | 5465 | 0.4388 | 5620 | 0.5136 | 5385 | 0.5335 | 5565 | 0.47732
January 2006 | 5450 | 0.4521 | 5815 | 0.4297 | 5745 | 0.3938 | 5250 | 0.4502 | 5565 | 0.43145
February 2006 | 5400 | 0.3915 | 5400 | 0.3927 | 5400 | 0.3937 | 5400 | 0.3903 | 5400 | 0.39205
March 2006 | 5365 | 0.5334 | 5787 | 0.4223 | 5465 | 0.4514 | 5643 | 0.523 | 5565 | 0.48252

## Total CER
Summary of Emission Reduction
Year | Emission Reductions
April 2001 – March 2002 | 3233.4847
April 2002 – March 2003 | 4141.0428
April 2003 – March 2004 | 3342.1192
April 2004 – March 2005 | 0
Aril 2005 – March 2006 | 0
Total | 10716.6467