## Sheet1
Calculation of achieved PLF with respect to 7 MW WHRB, 10 MW WHRB and 11 MW AFBC for
registered Project activity UNFCCC 0264 and 0772, based on Monitoring Report for the Period 01/01/2006 to 31/12006
http://cdm.unfccc.int/UserManagement/FileStorage/QYNFFJF39ZNDWJ47G6ACFKDZQ4OZF3
1 | Total power generation recorded in year Jan-2006 to Dec.2006 | 172730.636
2 | Total Steam provided by AFBC | 499568
3 | Total Steam provided by WHRB1 | 154231
4 | Total Steam Provided by WHRb2 | 231555
| Total Steam consumed by all TGs | 870275.6
| Power Generation because of 11 MW AFBC | 99153.3008
| Power Generation because of WHRB1 | 30611.4738
| Power Generation because of WHRB2 | 45958.5934
AFBC GENERATION
1 | Capacity | 11 | MW
2 | Days | 365 | days
3 | Hours | 24 | hours
4 | Generation at 100% PLF | 96360 | MWh/Year
5 | Generation achieved in given period | 99153.3008 | MWh/Year
6 | Effective PLF achieved during the year | 102.9%
7 | Operating PLF based on 350 days | 107.3%
WHRB-1
1 | Capacity | 7 | MW
2 | Days | 365 | days
3 | Hours | 24 | hours
4 | Generation at 100% PLF | 61320 | MWh/Year
5 | Generation achieved in given period | 30611.4738 | MWh/Year
6 | Effective PLF achieved during the year | 49.92%
7 | Assuming operating PLF @ | 80%
8 | Actual calculated days of production based on operating PLF | 227.7639 | days
9 | Calculated Operating PLF based on 300 days | 60.74%
WHRB-2
1 | Capacity | 10 | MW
2 | Days | 365 | days
3 | Hours | 24 | hours
4 | Generation at 100% PLF | 87600 | MWh/Year
5 | Generation achieved in given period | 45958.5934 | MWh/Year
6 | Effective PLF achieved during the year | 52.46%
7 | Assuming operating PLF @ | 80%
8 | Actual calculated days of production based on operating PLF | 239.3677 | days
9 | Calculated Operating PLF based on 300 days | 63.83%
Comments : It is evident with the above that the
1. The AFBC can easily operate for more than 100% PLF
2. The WHRB can not easily be operate for more than 64% PLF
3. The WHRB annual average PLF is just around 52%
4. The AFBC can operate for more than 350 days also
Note on E44: Lalit Singhania: As against the actual OPLF of 64% we have considered 80% OPLF