## Jan-07
CDM EXCLUSIVE REPORT FOR THE MONTH OF JANUARY-2007
DATE | POWER GENERATION
| GROSS POWER GENERATION (kWh) | AUXILIARY POWER CONSUMPTION (kWh) | NET POWER GENERATED FROM TURBINE (kWh)
1st Jan,07 | 120000 | 21560 | 98440
2nd Jan,07 | 130000 | 21910 | 108090
3rd Jan,07 | 95000 | 20210 | 74790
4th Jan,07 | 138000 | 22010 | 115990
5th Jan,07 | 164000 | 19950 | 144050
6th Jan,07 | 250000 | 28400 | 221600
7th Jan,07 | 319000 | 30630 | 288370
8th Jan,07 | 0 | 0 | 0 | Net generation for this day has been considered zero, On this day TG tripped at 11 AM and plant was shut, hence closing auxiliary meter reading for the day could not be taken
9th Jan,07 | 0 | 0 | 0 | Plant remained shut down from 09.01.07 to 17.01.07
10th Jan,07 | 0 | 0 | 0
11th Jan,07 | 0 | 0 | 0
12th Jan,07 | 0 | 0 | 0
13th Jan,07 | 0 | 0 | 0
14th Jan,07 | 0 | 0 | 0
15th Jan,07 | 0 | 0 | 0
16th Jan,07 | 0 | 0 | 0
17th Jan,07 | 0 | 0 | 0
18th Jan,07 | 105000 | 21800 | 83200
19th Jan,07 | 240000 | 27460 | 212540
20th Jan,07 | 256000 | 31870 | 224130
21st Jan,07 | 208000 | 30720 | 177280
22nd Jan,07 | 239000 | 30490 | 208510
23rd Jan,07 | 268000 | 31400 | 236600
24th Jan,07 | 248000 | 32600 | 215400
25th Jan,07 | 196000 | 30320 | 165680
26th Jan,07 | 243000 | 32320 | 210680
27th Jan,07 | 237000 | 30520 | 206480
28th Jan,07 | 223000 | 31270 | 191730
29th Jan,07 | 0 | 0 | 0 | Closing auxiliary meter reading for two consecutive days and intial meter reading for the last day could not be taken hence the net generation for all the three days has been taken as zero. Although for cumulative three days net power generation was 213.33 MWh
30th Jan,07 | 0 | 0 | 0
31st Jan,07 | 0 | 0 | 0
TOTAL | 3679000 | 495440 | 3183560
(A.M.SAHAY) |  |  | (V.K.BAKSHI)
DGM (Power) |  |  | President (Power)
29th Jan,07 | 27000 | 20050 | 6950
30th Jan,07 | 7000 | 33600 | -26600 | 840
26th feb,07 | 7000 | 22110 | -15110 | 840

## Feb-07
CDM EXCLUSIVE REPORT FOR THE MONTH OF FEBRUARY-2007
DATE | POWER GENERATION
| GROSS POWER GENERATION (kWh) | AUXILIARY POWER CONSUMPTION (kWh) | NET POWER GENERATED FROM TURBINE (kWh)
1st feb,07 | 267000 | 32040 | 234960
2nd feb,07 | 265000 | 32500 | 232500
3rd feb,07 | 220000 | 32440 | 187560
4th feb,07 | 27000 | 10000 | 17000
5th feb,07 | 35000 | 18490 | 16510
6th feb,07 | 236000 | 32520 | 203480
7th feb,07 | 305000 | 39370 | 265630
8th feb,07 | 286000 | 35530 | 250470
9th feb,07 | 294000 | 36970 | 257030
10th feb,07 | 321000 | 37140 | 283860
11th feb,07 | 361000 | 40740 | 320260
12th feb,07 | 321000 | 37690 | 283310
13th feb,07 | 371000 | 39630 | 331370
14th feb,07 | 292000 | 35120 | 256880
15th feb,07 | 338000 | 33180 | 304820
16th feb,07 | 355000 | 33020 | 321980
17th feb,07 | 347000 | 33090 | 313910
18th feb,07 | 319000 | 38940 | 280060
19th feb,07 | 368000 | 41420 | 326580
20th feb,07 | 315000 | 38670 | 276330
21st feb,07 | 362000 | 39630 | 322370
22nd feb,07 | 331000 | 39650 | 291350
23rd feb,07 | 259000 | 38840 | 220160
24th feb,07 | 250000 | 38370 | 211630
25th feb,07 | 215000 | 34910 | 180090
26th feb,07 | 7000 | 22100 | -15100
27th feb,07 | 187000 | 30100 | 156900
28th feb,07 | 219000 | 31170 | 187830
TOTAL | 7473000 | 953270 | 6519730
(A.M.SAHAY) |  |  | (V.K.BAKSHI)
DGM (Power) |  |  | President (Power)

## Mar-07
CDM EXCLUSIVE REPORT FOR THE MONTH OF MARCH-2007
DATE | POWER GENERATION
| GROSS POWER GENERATION (kWh) | AUXILIARY POWER CONSUMPTION (kWh) | NET POWER GENERATED FROM TURBINE (kWh)
1st Mar,07 | 246000 | 32770 | 213230
2nd Mar,07 | 244000 | 30770 | 213230
3rd Mar,07 | 277000 | 32390 | 244610
4th Mar,07 | 282000 | 33320 | 248680
5th Mar,07 | 268000 | 33230 | 234770
6th Mar,07 | 307000 | 33040 | 273960
7th Mar,07 | 313000 | 36010 | 276990
8th Mar,07 | 283000 | 30120 | 252880
9th Mar,07 | 216000 | 27570 | 188430
10th Mar,07 | 205000 | 38030 | 166970
11th Mar,07 | 255000 | 31990 | 223010
12th Mar,07 | 264000 | 32260 | 231740
13th Mar,07 | 265000 | 32610 | 232390
14th Mar,07 | 201000 | 30460 | 170540
15th Mar,07 | 259000 | 32300 | 226700
16th Mar,07 | 267000 | 31800 | 235200
17th Mar,07 | 245000 | 31830 | 213170
18th Mar,07 | 243000 | 31710 | 211290
19th Mar,07 | 312000 | 33020 | 278980
20th Mar,07 | 295000 | 32850 | 262150
21st Mar,07 | 267000 | 32720 | 234280
22nd Mar,07 | 114000 | 23970 | 90030
23rd Mar,07 | 94000 | 24570 | 69430
24th Mar,07 | 76000 | 13300 | 62700
25th Mar,07 | 173000 | 22400 | 150600
26th Mar,07 | 198000 | 23500 | 174500
27th Mar,07 | 195000 | 29220 | 165780
28th Mar,07 | 207000 | 24040 | 182960
29th Mar,07 | 171000 | 22660 | 148340
30th Mar,07 | 178000 | 22260 | 155740
31st Mar,07 | 193000 | 23330 | 169670
TOTAL | 7113000 | 910050 | 6202950

## Apr-07
CDM EXCLUSIVE REPORT FOR THE MONTH OF APRIL-2007
DATE | POWER GENERATION
| GROSS POWER GENERATION (kWh) | AUXILIARY POWER CONSUMPTION (kWh) | NET POWER GENERATED FROM TURBINE (kWh)
1st Apr,07 | 167000 | 22190 | 144810
2nd Apr,07 | 198000 | 30680 | 167320
3rd Apr,07 | 196000 | 31130 | 164870
4th Apr,07 | 176000 | 31160 | 144840
5th Apr,07 | 42000 | 14850 | 27150
6th Apr,07 | 158000 | 23680 | 134320
7th Apr,07 | 176000 | 22530 | 153470
8th Apr,07 | 184000 | 21940 | 162060
9th Apr,07 | 189000 | 23430 | 165570
10th Apr,07 | 330000 | 32290 | 297710
11th Apr,07 | 380000 | 35230 | 344770
12th Apr,07 | 372000 | 33670 | 338330
13th Apr,07 | 362000 | 33550 | 328450
14th Apr,07 | 378000 | 34920 | 343080
15th Apr,07 | 347000 | 35430 | 311570
16th Apr,07 | 332000 | 34200 | 297800
17th Apr,07 | 313000 | 36340 | 276660
18th Apr,07 | 438000 | 44660 | 393340
19th Apr,07 | 380000 | 45560 | 334440
20th Apr,07 | 448000 | 48740 | 399260
21st Apr,07 | 436000 | 47910 | 388090
22nd Apr,07 | 382000 | 39790 | 342210
23rd Apr,07 | 282000 | 32150 | 249850
24th Apr,07 | 362000 | 33700 | 328300
25th Apr,07 | 318000 | 44860 | 273140
26th Apr,07 | 356000 | 34100 | 321900
27th Apr,07 | 379000 | 35240 | 343760
28th Apr,07 | 388000 | 35690 | 352310
29th Apr,07 | 355000 | 35790 | 319210
30th Apr,07 | 368000 | 36140 | 331860
TOTAL | 9192000 | 1011550 | 8180450
(A.M.SAHAY) |  |  | (V.K.BAKSHI)
DGM (Power) |  |  | President (Power)

## May-07
CDM EXCLUSIVE REPORT FOR THE MONTH OF MAY-2007
DATE | POWER GENERATION
| GROSS POWER GENERATION (kWh) | AUXILIARY POWER CONSUMPTION (kWh) | NET POWER GENERATED FROM TURBINE (kWh)
1st May,07 | 354000 | 36150 | 317850
2nd May,07 | 373000 | 36920 | 336080
3rd May,07 | 368000 | 38070 | 329930
4th May,07 | 342000 | 41020 | 300980
5th May,07 | 368000 | 42330 | 325670
6th May,07 | 350000 | 38590 | 311410
7th May,07 | 197000 | 30340 | 166660
8th May,07 | 355000 | 40720 | 314280
9th May,07 | 368000 | 36980 | 331020
10th May,07 | 297000 | 35570 | 261430
11th May,07 | 278000 | 33160 | 244840
12th May,07 | 93000 | 17950 | 75050
13th May,07 | 153000 | 23490 | 129510
14th May,07 | 107000 | 22680 | 84320
15th May,07 | 74000 | 19800 | 54200
16th May,07 | 104000 | 23810 | 80190
17th May,07 | 111000 | 22520 | 88480
18th May,07 | 137800 | 32200 | 105600
19th May,07 | 172000 | 25700 | 146300
20th May,07 | 145000 | 21970 | 123030
21st May,07 | 146000 | 21850 | 124150
22nd May,07 | 161000 | 22900 | 138100
23rd May,07 | 309000 | 38140 | 270860
24th May,07 | 341000 | 34520 | 306480
25th May,07 | 385000 | 34870 | 350130
26th May,07 | 250000 | 32190 | 217810
27th May,07 | 187000 | 31250 | 155750
28th May,07 | 183000 | 31860 | 151140
29th May,07 | 210000 | 29260 | 180740
30th May,07 | 175000 | 24580 | 150420
31st May,07 | 188000 | 29530 | 158470
TOTAL | 7281800 | 950920 | 6330880

## JUNE-07
CDM EXCLUSIVE REPORT FOR THE MONTH OF JUNE - 2007
DATE | GROSS POWER GENERATION (kWh) | AUXILIARY POWER CONSUMPTION (kWh) | NET POWER GENERATED FROM TURBINE (kWh) | REMARKS
01.06.07 | 200000 | 34350 | 165650 | *
02.06.07 | 220000 | 47780 | 172220 | *
03.06.07 | 231000 | 46610 | 184390 | *
04.06.07 | 245000 | 47310 | 197690 | *
05.06.07 | 299000 | 39350 | 259650
06.06.07 | 307000 | 43940 | 263060 | *
07.06.07 | 326000 | 48550 | 277450 | *
08.06.07 | 280000 | 37690 | 242310
09.06.07 | 329000 | 36010 | 292990
10.06.07 | 342000 | 37000 | 305000
11.06.07 | 312000 | 35260 | 276740
12.06.07 | 309000 | 33930 | 275070
13.06.07 | 277000 | 35270 | 241730
14.06.07 | 326000 | 41830 | 284170 | *
15.06.07 | 401000 | 42640 | 358360 | *
16.06.07 | 247000 | 34660 | 212340
17.06.07 | 206000 | 34600 | 171400
18.06.07 | 230000 | 32150 | 197850
19.06.07 | 224000 | 16260 | 207740 | *
20.06.07 | 136000 | 29160 | 106840 | *
21.06.07 | 90000 | 17770 | 72230
22.06.07 | 231000 | 41690 | 189310 | *
23.06.07 | 263000 | 44590 | 218410 | *
24.06.07 | 264220 | 33540 | 230680 | *
25.06.07 | 257000 | 30530 | 226470
26.06.07 | 174000 | 27630 | 146370
27.06.07 | 145000 | 29440 | 115560 | *
28.06.07 | 290760 | 43990 | 246770 | *
29.06.07 | 215000 | 37940 | 177060 | *
30.06.07 | 130000 | 23440 | 106560
TOTAL | 3482000 | 455290 | 3026710
* | The power generation for the day has not been accounted for in estimation of emission reductions as PP put on trial the AFBC boiler and some steam was supplied to the common header. This is conservative and tranmsparent.

## Emission reductions
Month | Net power supplied (kWh) | Emission factor (tCO2/MWh) | Baseline emissions (tCO2) | Project Emissions (tCO2) | Emission Reductions (tCO2)
2007-01-01 | 3183560 | 0.819 | 2607.3356 | 80.7902 | 2526.5454
2007-02-01 | 6519730 | 0.819 | 5339.6589 | 52.014 | 5287.6449
2007-03-01 | 6202950 | 0.819 | 5080.216 | 26.0544 | 5054.1617
2007-04-01 | 8180450 | 0.819 | 6699.7886 | 23.2241 | 6676.5644
2007-05-01 | 6330880 | 0.819 | 5184.9907 | 50.4973 | 5134.4934
2007-06-01 | 3026710 | 0.819 | 2478.8755 | 38.6564 | 2440.2191
Total | 33444280 |  | 27390.8653 | 271.2363 | 27119.629

## Project Emissions
| Month | DieselConsumption (l) | NCV (IPCC Default value) (TJ/Gg) | Density (kg/l) | Diesel quantity in Gg | Emission factor kg/TJ | Emissions tCO2
| 2007-01-01 | 29830 | 43 | 0.85 | 0.025355 | 74100 | 80.7902
| 2007-02-01 | 19205 | 43 | 0.85 | 0.016324 | 74100 | 52.014
| 2007-03-01 | 9620 | 43 | 0.85 | 0.008177 | 74100 | 26.0544
| 2007-04-01 | 8575 | 43 | 0.85 | 0.0072888 | 74100 | 23.2241
| 2007-05-01 | 18645 | 43 | 0.85 | 0.015848 | 74100 | 50.4973
| 2007-06-01 | 14273 | 43 | 0.85 | 0.012132 | 74100 | 38.6564
| Total | 100148 |  |  | 0.085126 | 444600 | 271.2363
| Data | Data sources
1 | DieselConsumption | Plant operation data on diesel consumption in DG sets
2 | NCV (IPCC Default value) TJ/Gg | IPCC default value, http://www.ipcc-nggip.iges.or.jp/public/2006gl/pdf/2_Volume2/V2_1_Ch1_Introduction.pdf, page 18
3 | Density | http://en.wikipedia.org/wiki/Diesel
4 | Emission factor kg/TJ | IPCC default value, http://www.ipcc-nggip.iges.or.jp/public/2006gl/pdf/2_Volume2/V2_1_Ch1_Introduction.pdf, page 23