## EF-Sample
SAMPLE CALCULATION FOR EMISSION FACTOR
SN | Parameter | Units | Value
a. | Fuel oil consumed in auxiliary boilers | T | 48205
b. | Steam generated in auxiliary boilers | T | 671193
c. | Specific fuel oil consumption in auxiliary boiler (a/b) | T / T | 0.07182
d | Naphtha consumed in HRSGs | T | 41308
e | Steam generated in HRSGs | T | 755821
f | Specific naphtha consumption in HRSGs (d/e) | T / T | 0.054653
g | Total Steam consumed in STG | T | 381325
h | steam in STG from aux boiler | T | 179355.4028
i | steam to STG from HSRG | T | 201969.5972
j | FO consumed for power in STG (c x h) | T | 12881.2833
k | IPCC default calorific value of FO | TJ/1000t | 40.19
l | Energy from FO for power generation (j x k) | TJ | 517.6988
m | IPCC default emission factor for FO | t C/TJ | 21.1
n | Oxidation factor for FO (IPCC) | fraction | 0.99
o | Fuel oil emission factor (m x n x 44 / 12) | t CO2/TJ | 76.593
p | Emission from FO combustion (l x o) | t CO2/yr | 39652.1024
q | Naphtha consumed for power in STG (i x f) | T | 11038.2751
r | IPCC default calorific value of naphtha | TJ/1000t | 45.01
s | Energy from naphtha for power generation (q x r) | TJ | 496.8328
t | IPCC default emission factor for naphtha | t C/TJ | 20
u | Oxidation factor for Naphtha (IPCC) | fraction | 0.99
v | Naphtha emission factor (t x u x 44 / 12) | t CO2/TJ | 72.6
w | Emission from Naphtha combustion (s x v) | t CO2/yr | 36070.0585
x | Total emission (FO + Naphtha) ( p + w) | t CO2/yr | 75722.1609
y | Power generated in STG | MWh/yr | 95422.971
z | Emission factor for CPP power (x / y) | t CO2/MWh | 0.79354

## EF 2005-06
CALCULATION OF EMISSION FACTOR (APR'05 - MAR'06)
SN | Parameter | Units | Value
a. | Fuel oil consumed in auxiliary boilers | T | 48617.1813
b. | Steam generated in auxiliary boilers | T | 674467.1991
c. | Specific fuel oil consumption in auxiliary boiler (a/b) | T / T | 0.072082
d | Naphtha consumed in HRSGs | T | 41485.039
e | Steam generated in HRSGs | T | 708863.6669
f | Specific naphtha consumption in HRSGs (d/e) | T / T | 0.058523
g | Total Steam consumed in STG | T | 341883.9484
h | steam in STG from aux boiler | T | 166691.5087
i | steam to STG from HSRG | T | 175192.4397
j | FO consumed for power in STG (c x h) | T | 12015.5158
k | IPCC default calorific value of FO | TJ/1000t | 40.19
l | Energy from FO for power generation (j x k) | TJ | 482.9036
m | IPCC default emission factor for FO | t C/TJ | 21.1
n | Oxidation factor for FO (IPCC) | fraction | 0.99
o | Fuel oil emission factor (m x n x 44 / 12) | t CO2/TJ | 76.593
p | Emission from FO combustion (l x o) | t CO2/yr | 36987.0339
q | Naphtha consumed for power in STG (i x f) | T | 10252.8392
r | IPCC default calorific value of naphtha | TJ/1000t | 45.01
s | Energy from naphtha for power generation (q x r) | TJ | 461.4803
t | IPCC default emission factor for naphtha | t C/TJ | 20
u | Oxidation factor for Naphtha (IPCC) | fraction | 0.99
v | Naphtha emission factor (t x u x 44 / 12) | t CO2/TJ | 72.6
w | Emission from Naphtha combustion (s x v) | t CO2/yr | 33503.4693
x | Total emission (FO + Naphtha) ( p + w) | t CO2/yr | 70490.5032
y | Power generated in STG | MWh/yr | 82100.24
z | Emission factor for CPP power (x / y) | t CO2/MWh | 0.85859

## EF 2006-7
CALCULATION OF EMISSION FACTOR (APR'06-SEP06)
SN | Parameter | Units | Value
a. | Fuel oil consumed in auxiliary boilers | T | 28191.134
b. | Steam generated in auxiliary boilers | T | 388376.4985
c. | Specific fuel oil consumption in auxiliary boiler (a/b) | T / T | 0.072587
d | Naphtha consumed in HRSGs | T | 22669.0145
e | Steam generated in HRSGs | T | 369372.5151
f | Specific naphtha consumption in HRSGs (d/e) | T / T | 0.061372
g | Total Steam consumed in STG | T | 163831.5491
h | steam in STG from aux boiler | T | 83970.1831
i | steam to STG from HSRG | T | 79861.3661
j | FO consumed for power in STG (c x h) | T | 6095.1543
k | IPCC default calorific value of FO | TJ/1000t | 40.19
l | Energy from FO for power generation (j x k) | TJ | 244.9643
m | IPCC default emission factor for FO | t C/TJ | 21.1
n | Oxidation factor for FO (IPCC) | fraction | 0.99
o | Fuel oil emission factor (m x n x 44 / 12) | t CO2/TJ | 76.593
p | Emission from FO combustion (l x o) | t CO2/yr | 18762.5469
q | Naphtha consumed for power in STG (i x f) | T | 4901.2268
r | IPCC default calorific value of naphtha | TJ/1000t | 45.01
s | Energy from naphtha for power generation (q x r) | TJ | 220.6042
t | IPCC default emission factor for naphtha | t C/TJ | 20
u | Oxidation factor for Naphtha (IPCC) | fraction | 0.99
v | Naphtha emission factor (t x u x 44 / 12) | t CO2/TJ | 72.6
w | Emission from Naphtha combustion (s x v) | t CO2/yr | 16015.8662
x | Total emission (FO + Naphtha) ( p + w) | t CO2/yr | 34778.4131
y | Power generated in STG | MWh/yr | 39580.167
z | Emission factor for CPP power (x / y) | t CO2/MWh | 0.87868

## <45GWhTH
CALCULATION OF TOTAL REDUCTION IN ENERGY CONSUMPTION BY MEASURE I + II
Measure I :
| For the period : | 22.09.05 to 21.09.06
a | Power consumption of compressors | 48998656.45 | kWh
b | Quantity of air generated by compressor | 412885651.4778 | Nm3
c | Sp power cons in project scenario (a/b) | 0.11867 | kWh/Nm3
d | Sp power consumption in baseline case (refer Section B.5. of PDD for baseline calculations) | 0.1347 | kWh/Nm3
e | Reduction in sp. power consumption | 0.016026 | kWh/Nm3
f | Reduction in power cons due to project activity (b x e) | 6617040.804 | kWh
g | Reduction in energy consumption due to Measure I (f/10^6) | 6.617 | GWhE
For conversion factor from electrical to thermal :
h | Fuel oil energy consumption in CPP | 556.588 | TJ
i | Naphtha energy consumption in CPP | 535.8214 | TJ
j | Total energy consumption (h + i) | 1092.4094 | TJ
k | Power generated in CPP | 96518.41 | MWh
l | Specific energy consumption for power generation (j / k) | 0.011318 | TJ/MWh
|  | 3.1439 | GWh/MWh
m | Reduction in energy consumption due to Measure I (g x l) | 20.8035 | GWhTH
Measure II :
For the same period as for Measure I :
n | Quantity of biogas consumed in heater | 3033362.16 | Nm3
o | Methane content in biogas | 0.70826 | fraction
p | Calorific value of methane | 35.7 | TJ/Nm3
q | Energy saved through use of biogas (a x b x c) | 76698720.0941 | MJ
r | Reduction in energy consumption through Measure II (d/3600) | 21.3052 | GWhTH
s | Total reduction in energy consumption : | 42.1087 | GWhTH

## Measure I ER
Date | Power consumption of compressors | Quantity of air generated by compressor | Sp power cons in project scenario | Sp power consumption in baseline case | Reduction in sp. power consumption | Reduction in daily power cons due to project activity | Emission factor for CPP power | baseline emission | Project emission | Emmission reduction
| kWh | Nm3 | kWh/Nm3 | kWh/Nm3 | kWh/Nm3 | kWh | t CO2/MWh | t CO2 | t CO2 | t CO2
2005-09-22 | 134190 | 1128293.2883 | 0.11893 | 0.1347 | 0.015768 | 17791.1059 | 0.85859 | 130.4896 | 115.2143 | 15.2753
2005-09-23 | 128555 | 1111091.5616 | 0.1157 | 0.1347 | 0.018998 | 21109.0333 | 0.85859 | 128.5001 | 110.3761 | 18.124
2005-09-24 | 131880 | 1133886.1713 | 0.11631 | 0.1347 | 0.018392 | 20854.4673 | 0.85859 | 131.1364 | 113.2309 | 17.9055
2005-09-25 | 127700 | 1115505.9841 | 0.11448 | 0.1347 | 0.020223 | 22558.6561 | 0.85859 | 129.0107 | 109.642 | 19.3687
2005-09-26 | 133750 | 1152744.7411 | 0.11603 | 0.1347 | 0.018673 | 21524.7166 | 0.85859 | 133.3174 | 114.8365 | 18.4809
2005-09-27 | 132900 | 1160025.842 | 0.11457 | 0.1347 | 0.020134 | 23355.4809 | 0.85859 | 134.1595 | 114.1067 | 20.0528
2005-09-28 | 131630 | 1149382.9928 | 0.11452 | 0.1347 | 0.020178 | 23191.8891 | 0.85859 | 132.9286 | 113.0163 | 19.9123
2005-09-29 | 132520 | 1136997.584 | 0.11655 | 0.1347 | 0.018147 | 20633.5746 | 0.85859 | 131.4962 | 113.7804 | 17.7158
2005-09-30 | 133420 | 1135964.5228 | 0.11745 | 0.1347 | 0.017249 | 19594.4212 | 0.85859 | 131.3768 | 114.5532 | 16.8236
2005-10-01 | 130470 | 1141346.6517 | 0.11431 | 0.1347 | 0.020388 | 23269.394 | 0.85859 | 131.9992 | 112.0203 | 19.9789
2005-10-02 | 131390 | 1146728.7806 | 0.11458 | 0.1347 | 0.020122 | 23074.3667 | 0.85859 | 132.6217 | 112.8102 | 19.8114
2005-10-03 | 128660 | 1152110.9095 | 0.11167 | 0.1347 | 0.023027 | 26529.3395 | 0.85859 | 133.2441 | 110.4663 | 22.7778
2005-10-04 | 127890 | 1157493.0384 | 0.11049 | 0.1347 | 0.024211 | 28024.3123 | 0.85859 | 133.8666 | 109.8052 | 24.0614
2005-10-05 | 131440 | 1162875.1673 | 0.11303 | 0.1347 | 0.02167 | 25199.285 | 0.85859 | 134.489 | 112.8532 | 21.6359
2005-10-06 | 121005 | 1168257.2962 | 0.10358 | 0.1347 | 0.031123 | 36359.2578 | 0.85859 | 135.1115 | 103.8938 | 31.2177
2005-10-07 | 129720 | 1173639.425 | 0.11053 | 0.1347 | 0.024172 | 28369.2306 | 0.85859 | 135.7339 | 111.3764 | 24.3576
2005-10-08 | 131060 | 1179021.5539 | 0.11116 | 0.1347 | 0.02354 | 27754.2033 | 0.85859 | 136.3564 | 112.5269 | 23.8295
2005-10-09 | 128790 | 1184403.6828 | 0.10874 | 0.1347 | 0.025962 | 30749.1761 | 0.85859 | 136.9789 | 110.5779 | 26.401
2005-10-10 | 131070 | 1189785.8117 | 0.11016 | 0.1347 | 0.024537 | 29194.1488 | 0.85859 | 137.6013 | 112.5355 | 25.0658
2005-10-11 | 128840 | 1195167.9406 | 0.1078 | 0.1347 | 0.026899 | 32149.1216 | 0.85859 | 138.2238 | 110.6208 | 27.6029
2005-10-12 | 132110 | 1200550.0695 | 0.11004 | 0.1347 | 0.024659 | 29604.0944 | 0.85859 | 138.8462 | 113.4284 | 25.4178
2005-10-13 | 128810 | 1205932.1984 | 0.10681 | 0.1347 | 0.027886 | 33629.0671 | 0.85859 | 139.4687 | 110.5951 | 28.8736
2005-10-14 | 126345 | 1211314.3272 | 0.1043 | 0.1347 | 0.030396 | 36819.0399 | 0.85859 | 140.0911 | 108.4786 | 31.6125
2005-10-15 | 142595 | 1216696.4561 | 0.1172 | 0.1347 | 0.017501 | 21294.0126 | 0.85859 | 140.7136 | 122.4307 | 18.2828
2005-10-16 | 136400 | 1222078.585 | 0.11161 | 0.1347 | 0.023087 | 28213.9854 | 0.85859 | 141.336 | 117.1118 | 24.2243
2005-10-17 | 135710 | 1227460.7139 | 0.11056 | 0.1347 | 0.024138 | 29628.9582 | 0.85859 | 141.9585 | 116.5193 | 25.4391
2005-10-18 | 134330 | 1232842.8428 | 0.10896 | 0.1347 | 0.02574 | 31733.9309 | 0.85859 | 142.5809 | 115.3345 | 27.2465
2005-10-19 | 130750 | 1238224.9717 | 0.10559 | 0.1347 | 0.029105 | 36038.9037 | 0.85859 | 143.2034 | 112.2607 | 30.9427
2005-10-20 | 138720 | 1243607.1006 | 0.11155 | 0.1347 | 0.023154 | 28793.8764 | 0.85859 | 143.8259 | 119.1037 | 24.7222
2005-10-21 | 137815 | 1248989.2294 | 0.11034 | 0.1347 | 0.024359 | 30423.8492 | 0.85859 | 144.4483 | 118.3267 | 26.1216
2005-10-22 | 141600 | 1254371.3583 | 0.11289 | 0.1347 | 0.021815 | 27363.822 | 0.85859 | 145.0708 | 121.5764 | 23.4943
2005-10-23 | 138455 | 1259753.4872 | 0.10991 | 0.1347 | 0.024794 | 31233.7947 | 0.85859 | 145.6932 | 118.8762 | 26.817
2005-10-24 | 139470 | 1265135.6161 | 0.11024 | 0.1347 | 0.024459 | 30943.7675 | 0.85859 | 146.3157 | 119.7476 | 26.568
2005-10-25 | 136855 | 1270517.745 | 0.10772 | 0.1347 | 0.026984 | 34283.7402 | 0.85859 | 146.9381 | 117.5024 | 29.4357
2005-10-26 | 136625 | 1275899.8739 | 0.10708 | 0.1347 | 0.027619 | 35238.713 | 0.85859 | 147.5606 | 117.305 | 30.2556
2005-10-27 | 136230 | 1281282.0027 | 0.10632 | 0.1347 | 0.028377 | 36358.6858 | 0.85859 | 148.183 | 116.9658 | 31.2172
2005-10-28 | 132440 | 1286664.1316 | 0.10293 | 0.1347 | 0.031767 | 40873.6585 | 0.85859 | 148.8055 | 113.7118 | 35.0937
2005-10-29 | 139000 | 1209847.9248 | 0.11489 | 0.1347 | 0.01981 | 23966.5155 | 0.85859 | 139.9215 | 119.3441 | 20.5774
2005-10-30 | 138860 | 1182483.6408 | 0.11743 | 0.1347 | 0.017269 | 20420.5464 | 0.85859 | 136.7568 | 119.2239 | 17.5329
2005-10-31 | 139160 | 1199986.8423 | 0.11597 | 0.1347 | 0.018732 | 22478.2277 | 0.85859 | 138.7811 | 119.4815 | 19.2996
2005-11-01 | 138955 | 1196913.9368 | 0.11609 | 0.1347 | 0.018606 | 22269.3073 | 0.85859 | 138.4257 | 119.3055 | 19.1202
2005-11-02 | 143180 | 1221052.03 | 0.11726 | 0.1347 | 0.01744 | 21295.7084 | 0.85859 | 141.2173 | 122.933 | 18.2843
2005-11-03 | 141190 | 1224797.7034 | 0.11528 | 0.1347 | 0.019424 | 23790.2507 | 0.85859 | 141.6505 | 121.2244 | 20.4261
2005-11-04 | 144000 | 1243908.1304 | 0.11576 | 0.1347 | 0.018936 | 23554.4252 | 0.85859 | 143.8607 | 123.6371 | 20.2236
2005-11-05 | 144400 | 1225302.4195 | 0.11785 | 0.1347 | 0.016852 | 20648.2359 | 0.85859 | 141.7089 | 123.9805 | 17.7284
2005-11-06 | 142740 | 1229767.5259 | 0.11607 | 0.1347 | 0.018629 | 22909.6857 | 0.85859 | 142.2253 | 122.5552 | 19.67
2005-11-07 | 144200 | 1225329.0876 | 0.11768 | 0.1347 | 0.017017 | 20851.8281 | 0.85859 | 141.712 | 123.8088 | 17.9032
2005-11-08 | 139560 | 1269728.233 | 0.10991 | 0.1347 | 0.024787 | 31472.393 | 0.85859 | 146.8468 | 119.8249 | 27.0219
2005-11-09 | 139405 | 1203167.8893 | 0.11586 | 0.1347 | 0.018835 | 22661.7147 | 0.85859 | 139.149 | 119.6918 | 19.4571
2005-11-10 | 143730 | 1261561.0251 | 0.11393 | 0.1347 | 0.02077 | 26202.2701 | 0.85859 | 145.9023 | 123.4052 | 22.497
2005-11-11 | 138450 | 1226256.4945 | 0.1129 | 0.1347 | 0.021795 | 26726.7498 | 0.85859 | 141.8192 | 118.8719 | 22.9473
2005-11-12 | 138830 | 1216207.3901 | 0.11415 | 0.1347 | 0.02055 | 24993.1354 | 0.85859 | 140.657 | 119.1981 | 21.4589
2005-11-13 | 133810 | 1197913.1295 | 0.1117 | 0.1347 | 0.022997 | 27548.8985 | 0.85859 | 138.5413 | 114.888 | 23.6532
2005-11-14 | 135490 | 1203389.4106 | 0.11259 | 0.1347 | 0.02211 | 26606.5536 | 0.85859 | 139.1746 | 116.3305 | 22.8441
2005-11-15 | 135110 | 1203035.5952 | 0.11231 | 0.1347 | 0.022392 | 26938.8947 | 0.85859 | 139.1337 | 116.0042 | 23.1295
2005-11-16 | 135370 | 1209191.0051 | 0.11195 | 0.1347 | 0.022749 | 27508.0284 | 0.85859 | 139.8456 | 116.2274 | 23.6181
2005-11-17 | 136900 | 1210439.8683 | 0.1131 | 0.1347 | 0.021601 | 26146.2503 | 0.85859 | 139.99 | 117.5411 | 22.4489
2005-11-18 | 140620 | 1234972.1346 | 0.11386 | 0.1347 | 0.020835 | 25730.7465 | 0.85859 | 142.8272 | 120.735 | 22.0922
2005-11-19 | 136160 | 1207841.3735 | 0.11273 | 0.1347 | 0.02197 | 26536.233 | 0.85859 | 139.6895 | 116.9057 | 22.7838
2005-11-20 | 138535 | 1232124.0713 | 0.11244 | 0.1347 | 0.022264 | 27432.1124 | 0.85859 | 142.4978 | 118.9449 | 23.553
2005-11-21 | 142215 | 1244680.5473 | 0.11426 | 0.1347 | 0.020442 | 25443.4697 | 0.85859 | 143.95 | 122.1045 | 21.8455
2005-11-22 | 143950 | 1247443.2218 | 0.1154 | 0.1347 | 0.019304 | 24080.602 | 0.85859 | 144.2695 | 123.5941 | 20.6754
2005-11-23 | 141590 | 1251330.3298 | 0.11315 | 0.1347 | 0.021548 | 26964.1954 | 0.85859 | 144.7191 | 121.5679 | 23.1512
2005-11-24 | 143580 | 1243690.9247 | 0.11545 | 0.1347 | 0.019253 | 23945.1676 | 0.85859 | 143.8356 | 123.2765 | 20.5591
2005-11-25 | 137460 | 1235111.0867 | 0.11129 | 0.1347 | 0.023406 | 28909.4634 | 0.85859 | 142.8433 | 118.0219 | 24.8214
2005-11-26 | 138320 | 1229720.2909 | 0.11248 | 0.1347 | 0.022219 | 27323.3232 | 0.85859 | 142.2198 | 118.7603 | 23.4596
2005-11-27 | 138930 | 1228596.2003 | 0.11308 | 0.1347 | 0.02162 | 26561.9082 | 0.85859 | 142.0898 | 119.284 | 22.8058
2005-11-28 | 140480 | 1309354.7199 | 0.10729 | 0.1347 | 0.027411 | 35890.0808 | 0.85859 | 151.4297 | 120.6148 | 30.8149
2005-11-29 | 151650 | 1243008.8647 | 0.122 | 0.1347 | 0.012698 | 15783.2941 | 0.85859 | 143.7567 | 130.2053 | 13.5514
2005-11-30 | 140710 | 1226620.8378 | 0.11471 | 0.1347 | 0.019986 | 24515.8269 | 0.85859 | 141.8614 | 120.8123 | 21.0491
2005-12-01 | 138190 | 1234950.1556 | 0.1119 | 0.1347 | 0.022801 | 28157.786 | 0.85859 | 142.8247 | 118.6486 | 24.176
2005-12-02 | 137895 | 1297039.3152 | 0.10632 | 0.1347 | 0.028385 | 36816.1958 | 0.85859 | 150.0054 | 118.3954 | 31.61
2005-12-03 | 136275 | 1200186.7213 | 0.11354 | 0.1347 | 0.021155 | 25390.1514 | 0.85859 | 138.8042 | 117.0044 | 21.7997
2005-12-04 | 136255 | 1108956.5646 | 0.12287 | 0.1347 | 0.011832 | 13121.4492 | 0.85859 | 128.2532 | 116.9873 | 11.266
2005-12-05 | 135015 | 1286717.9575 | 0.10493 | 0.1347 | 0.02977 | 38305.9089 | 0.85859 | 148.8117 | 115.9226 | 32.8891
2005-12-06 | 134220 | 1192503.7799 | 0.11255 | 0.1347 | 0.022147 | 26410.2592 | 0.85859 | 137.9156 | 115.24 | 22.6756
2005-12-07 | 137820 | 1261066.8368 | 0.10929 | 0.1347 | 0.025412 | 32045.7029 | 0.85859 | 145.8451 | 118.331 | 27.5141
2005-12-08 | 139165 | 1204644.243 | 0.11552 | 0.1347 | 0.019176 | 23100.5795 | 0.85859 | 139.3197 | 119.4858 | 19.8339
2005-12-09 | 137715 | 1220280.8193 | 0.11286 | 0.1347 | 0.021845 | 26656.8264 | 0.85859 | 141.1281 | 118.2408 | 22.8873
2005-12-10 | 139690 | 1231166.8319 | 0.11346 | 0.1347 | 0.021239 | 26148.1723 | 0.85859 | 142.3871 | 119.9365 | 22.4506
2005-12-11 | 139075 | 1218016.149 | 0.11418 | 0.1347 | 0.020518 | 24991.7753 | 0.85859 | 140.8662 | 119.4085 | 21.4577
2005-12-12 | 138575 | 1216076.183 | 0.11395 | 0.1347 | 0.020747 | 25230.4619 | 0.85859 | 140.6418 | 118.9792 | 21.6626
2005-12-13 | 140320 | 1310765.2911 | 0.10705 | 0.1347 | 0.027648 | 36240.0847 | 0.85859 | 151.5928 | 120.4774 | 31.1154
2005-12-14 | 136215 | 1208243.8829 | 0.11274 | 0.1347 | 0.021962 | 26535.451 | 0.85859 | 139.736 | 116.9529 | 22.7831
2005-12-15 | 135105 | 1287035.6972 | 0.10497 | 0.1347 | 0.029726 | 38258.7084 | 0.85859 | 148.8485 | 115.9999 | 32.8486
2005-12-16 | 139680 | 1323540.2406 | 0.10554 | 0.1347 | 0.029165 | 38600.8704 | 0.85859 | 153.0703 | 119.928 | 33.1423
2005-12-17 | 139000 | 1095717.8957 | 0.12686 | 0.1347 | 0.0078425 | 8593.2005 | 0.85859 | 126.7222 | 119.3441 | 7.378
2005-12-18 | 141750 | 1272486.9995 | 0.1114 | 0.1347 | 0.023304 | 29653.9988 | 0.85859 | 147.1659 | 121.7052 | 25.4606
2005-12-19 | 135990 | 1234152.472 | 0.11019 | 0.1347 | 0.024511 | 30250.338 | 0.85859 | 142.7324 | 116.7598 | 25.9727
2005-12-20 | 137930 | 1172911.5057 | 0.1176 | 0.1347 | 0.017104 | 20061.1798 | 0.85859 | 135.6498 | 118.4254 | 17.2243
2005-12-21 | 130840 | 1007465.045 | 0.12987 | 0.1347 | 0.0048295 | 4865.5416 | 0.85859 | 116.5155 | 112.338 | 4.1775
2005-12-22 | 133635 | 1171828.4773 | 0.11404 | 0.1347 | 0.02066 | 24210.2959 | 0.85859 | 135.5245 | 114.7378 | 20.7867
2005-12-23 | 133295 | 1195471.0952 | 0.1115 | 0.1347 | 0.0232 | 27734.9565 | 0.85859 | 138.2588 | 114.4458 | 23.813
2005-12-24 | 130420 | 1146215.7023 | 0.11378 | 0.1347 | 0.020917 | 23975.2551 | 0.85859 | 132.5623 | 111.9774 | 20.5849
2005-12-25 | 132025 | 1187549.8402 | 0.11117 | 0.1347 | 0.023526 | 27937.9635 | 0.85859 | 137.3427 | 113.3554 | 23.9873
2005-12-26 | 134665 | 1199804.0036 | 0.11224 | 0.1347 | 0.022461 | 26948.5993 | 0.85859 | 138.7599 | 115.6221 | 23.1378
2005-12-27 | 135230 | 1238704.6433 | 0.10917 | 0.1347 | 0.02553 | 31623.5154 | 0.85859 | 143.2589 | 116.1072 | 27.1517
2005-12-28 | 125656.8 | 1160585.4923 | 0.10827 | 0.1347 | 0.02643 | 30674.0658 | 0.85859 | 134.2242 | 107.8878 | 26.3365
2005-12-29 | 122445 | 1149785.6953 | 0.10649 | 0.1347 | 0.028206 | 32431.1332 | 0.85859 | 132.9752 | 105.1301 | 27.8451
2005-12-30 | 134840 | 1209049.5727 | 0.11153 | 0.1347 | 0.023174 | 28018.9774 | 0.85859 | 139.8292 | 115.7724 | 24.0568
2005-12-31 | 137278.2 | 1116767.1153 | 0.12292 | 0.1347 | 0.011775 | 13150.3304 | 0.85859 | 129.1565 | 117.8658 | 11.2908
2006-01-01 | 121060 | 1210102.5172 |  |  |  | 0 |  | 0 | 0 | 0
2006-01-02 | 239635.3299 | 1270091.3173 |  |  |  | 0 |  | 0 | 0 | 0
2006-01-03 | 143340.1702 | 1217072.0182 | 0.11777 | 0.1347 | 0.016925 | 20599.4307 | 0.85859 | 140.757 | 123.0705 | 17.6865
2006-01-04 | 145570.95 | 1308254.564 | 0.11127 | 0.1347 | 0.023429 | 30650.9398 | 0.85859 | 151.3025 | 124.9859 | 26.3166
2006-01-05 | 129080 | 1222390.0354 | 0.1056 | 0.1347 | 0.029104 | 35575.9378 | 0.85859 | 141.3721 | 110.8269 | 30.5452
2006-01-06 | 122390 | 1122204.2918 | 0.10906 | 0.1347 | 0.025638 | 28770.9181 | 0.85859 | 129.7854 | 105.0829 | 24.7024
2006-01-07 | 132890 | 1184567.0556 | 0.11218 | 0.1347 | 0.022516 | 26671.1824 | 0.85859 | 136.9977 | 114.0981 | 22.8996
2006-01-08 | 131980 | 1164496.7012 | 0.11334 | 0.1347 | 0.021363 | 24877.7057 | 0.85859 | 134.6766 | 113.3168 | 21.3598
2006-01-09 | 123590 | 1148032.1134 | 0.10765 | 0.1347 | 0.027046 | 31049.9257 | 0.85859 | 132.7724 | 106.1132 | 26.6592
2006-01-10 | 136040 | 1198585.1967 | 0.1135 | 0.1347 | 0.0212 | 25409.426 | 0.85859 | 138.619 | 116.8027 | 21.8163
2006-01-11 | 135890 | 1181159.4394 | 0.11505 | 0.1347 | 0.019652 | 23212.1765 | 0.85859 | 136.6037 | 116.6739 | 19.9298
2006-01-12 | 126890 | 1126408.382 | 0.11265 | 0.1347 | 0.02205 | 24837.2091 | 0.85859 | 130.2716 | 108.9466 | 21.325
2006-01-13 | 112980 | 972438.1661 | 0.11618 | 0.1347 | 0.018518 | 18007.421 | 0.85859 | 112.4646 | 97.0036 | 15.461
2006-01-14 | 132410 | 1136607.5532 | 0.1165 | 0.1347 | 0.018204 | 20691.0374 | 0.85859 | 131.4511 | 113.686 | 17.7651
2006-01-15 | 133800 | 1141662.6192 | 0.1172 | 0.1347 | 0.017503 | 19981.9548 | 0.85859 | 132.0358 | 114.8794 | 17.1563
2006-01-16 | 133200 | 1167617.0964 | 0.11408 | 0.1347 | 0.020622 | 24078.0229 | 0.85859 | 135.0374 | 114.3643 | 20.6732
2006-01-17 | 132250 | 1147628.5694 | 0.11524 | 0.1347 | 0.019462 | 22335.5683 | 0.85859 | 132.7257 | 113.5486 | 19.1771
2006-01-18 | 133860 | 1142661.8401 | 0.11715 | 0.1347 | 0.017552 | 20056.5499 | 0.85859 | 132.1513 | 114.931 | 17.2204
2006-01-19 | 139250 | 1154060.9198 | 0.12066 | 0.1347 | 0.014039 | 16202.0059 | 0.85859 | 133.4696 | 119.5588 | 13.9109
2006-01-20 | 133260 | 1180084.6309 | 0.11292 | 0.1347 | 0.021776 | 25697.3998 | 0.85859 | 136.4793 | 114.4158 | 22.0635
2006-01-21 | 134000 | 1164536.4434 | 0.11507 | 0.1347 | 0.019633 | 22863.0589 | 0.85859 | 134.6812 | 115.0512 | 19.63
2006-01-22 | 139090 | 1178652.7588 | 0.11801 | 0.1347 | 0.016692 | 19674.5266 | 0.85859 | 136.3137 | 119.4214 | 16.8924
2006-01-23 | 139580 | 1158303.6191 | 0.1205 | 0.1347 | 0.014196 | 16443.4975 | 0.85859 | 133.9603 | 119.8421 | 14.1182
2006-01-24 | 131420 | 1161443.7737 | 0.11315 | 0.1347 | 0.021548 | 25026.4763 | 0.85859 | 134.3235 | 112.836 | 21.4875
2006-01-25 | 137060 | 1153182.1692 | 0.11885 | 0.1347 | 0.015846 | 18273.6382 | 0.85859 | 133.368 | 117.6784 | 15.6896
2006-01-26 | 139040 | 1154375.832 | 0.12045 | 0.1347 | 0.014254 | 16454.4246 | 0.85859 | 133.5061 | 119.3785 | 14.1276
2006-01-27 | 138070 | 1137349.4826 | 0.1214 | 0.1347 | 0.013304 | 15130.9753 | 0.85859 | 131.5369 | 118.5456 | 12.9913
2006-01-28 | 137580 | 1160913.9081 | 0.11851 | 0.1347 | 0.01619 | 18795.1034 | 0.85859 | 134.2622 | 118.1249 | 16.1373
2006-01-29 | 138200 | 1211031.4125 | 0.11412 | 0.1347 | 0.020582 | 24925.9313 | 0.85859 | 140.0584 | 118.6572 | 21.4012
2006-01-30 | 141800 | 1238254.7185 | 0.11452 | 0.1347 | 0.020184 | 24992.9106 | 0.85859 | 143.2068 | 121.7482 | 21.4587
2006-01-31 | 134600 | 1246766.9297 | 0.10796 | 0.1347 | 0.026741 | 33339.5054 | 0.85859 | 144.1913 | 115.5663 | 28.625
2006-02-01 | 142100 | 1073615.4911 | 0.13236 | 0.1347 | 0.0023435 | 2516.0067 | 0.85859 | 124.166 | 122.0057 | 2.1602
2006-02-02 | 149100 | 1215373.8481 | 0.12268 | 0.1347 | 0.012022 | 14610.8573 | 0.85859 | 140.5606 | 128.0159 | 12.5447
2006-02-03 | 149580 | 0 | [5 empty] | 0 | 0 | 0
2006-02-04 | 157740 | 0 | [5 empty] | 0 | 0 | 0
2006-02-05 | 148680 | 0 | [5 empty] | 0 | 0 | 0
2006-02-06 | 148460 | 0 | [5 empty] | 0 | 0 | 0
2006-02-07 | 151460 | 0 | [5 empty] | 0 | 0 | 0
2006-02-08 | 147440 | 0 | [5 empty] | 0 | 0 | 0
2006-02-09 | 143200 | 1237087.3263 | 0.11576 | 0.1347 | 0.018944 | 23435.6628 | 0.85859 | 143.0718 | 122.9502 | 20.1216
2006-02-10 | 150200 | 1235610.9762 | 0.12156 | 0.1347 | 0.013141 | 16236.7985 | 0.85859 | 142.9011 | 128.9603 | 13.9408
2006-02-11 | 142500 | 1314629.2675 | 0.1084 | 0.1347 | 0.026304 | 34580.5623 | 0.85859 | 152.0397 | 122.3492 | 29.6905
2006-02-12 | 141500 | 1268253.3877 | 0.11157 | 0.1347 | 0.023129 | 29333.7313 | 0.85859 | 146.6763 | 121.4906 | 25.1857
2006-02-13 | 147400 | 1300909.1409 | 0.11331 | 0.1347 | 0.021395 | 27832.4613 | 0.85859 | 150.453 | 126.5563 | 23.8967
2006-02-14 | 138900 | 1222900.7018 | 0.11358 | 0.1347 | 0.021118 | 25824.7245 | 0.85859 | 141.4311 | 119.2582 | 22.1729
2006-02-15 | 143400 | 1224078.2648 | 0.11715 | 0.1347 | 0.017551 | 21483.3423 | 0.85859 | 141.5673 | 123.1219 | 18.4454
2006-02-16 | 144400 | 1184247.6131 | 0.12193 | 0.1347 | 0.012766 | 15118.1535 | 0.85859 | 136.9608 | 123.9805 | 12.9803
2006-02-17 | 145100 | 1313161.4675 | 0.1105 | 0.1347 | 0.024203 | 31782.8497 | 0.85859 | 151.87 | 124.5815 | 27.2885
2006-02-18 | 138600 | 1304003.2721 | 0.10629 | 0.1347 | 0.028412 | 37049.2407 | 0.85859 | 150.8108 | 119.0007 | 31.8101
2006-02-19 | 144700 | 1090450.7801 | 0.1327 | 0.1347 | 0.0020026 | 2183.7201 | 0.85859 | 126.113 | 124.2381 | 1.8749
2006-02-20 | 135800 | 1139859.2047 | 0.11914 | 0.1347 | 0.015562 | 17739.0349 | 0.85859 | 131.8272 | 116.5966 | 15.2306
2006-02-21 | 137000 | 1154078.2395 | 0.11871 | 0.1347 | 0.015991 | 18454.3389 | 0.85859 | 133.4717 | 117.6269 | 15.8447
2006-02-22 | 141400 | 1255535.043 | 0.11262 | 0.1347 | 0.022079 | 27720.5703 | 0.85859 | 145.2054 | 121.4047 | 23.8006
2006-02-23 | 142300 | 1246430.7071 | 0.11417 | 0.1347 | 0.020534 | 25594.2162 | 0.85859 | 144.1524 | 122.1775 | 21.975
2006-02-24 | 142500 | 1269885.1108 | 0.11221 | 0.1347 | 0.022485 | 28553.5244 | 0.85859 | 146.865 | 122.3492 | 24.5158
2006-02-25 | 151900 | 1270661.4972 | 0.11954 | 0.1347 | 0.015156 | 19258.1037 | 0.85859 | 146.9548 | 130.4199 | 16.5348
2006-02-26 | 162500 | 1382785.6189 | 0.11752 | 0.1347 | 0.017184 | 23761.2229 | 0.85859 | 159.9222 | 139.521 | 20.4012
2006-02-27 | 159800 | 1370007.9478 | 0.11664 | 0.1347 | 0.018058 | 24740.0706 | 0.85859 | 158.4444 | 137.2028 | 21.2416
2006-02-28 | 153400 | 1373746.7375 | 0.11167 | 0.1347 | 0.023035 | 31643.6855 | 0.85859 | 158.8768 | 131.7078 | 27.169
2006-03-01 | 153500 | 1356454.0522 | 0.11316 | 0.1347 | 0.021537 | 29214.3608 | 0.85859 | 156.8769 | 131.7937 | 25.0832
2006-03-02 | 159300 | 1395048.9913 | 0.11419 | 0.1347 | 0.02051 | 28613.0991 | 0.85859 | 161.3404 | 136.7735 | 24.5669
2006-03-03 | 164900 | 1406668.7054 | 0.11723 | 0.1347 | 0.017473 | 24578.2746 | 0.85859 | 162.6843 | 141.5816 | 21.1027
2006-03-04 | 160700 | 1393219.6014 | 0.11534 | 0.1347 | 0.019356 | 26966.6803 | 0.85859 | 161.1289 | 137.9755 | 23.1533
2006-03-05 | 166500 | 1396680.3751 | 0.11921 | 0.1347 | 0.015489 | 21632.8465 | 0.85859 | 161.5291 | 142.9554 | 18.5738
2006-03-06 | 157900 | 1400025.1571 | 0.11278 | 0.1347 | 0.021916 | 30683.3887 | 0.85859 | 161.9159 | 135.5715 | 26.3445
2006-03-07 | 167500 | 1433240.7443 | 0.11687 | 0.1347 | 0.017832 | 25557.5283 | 0.85859 | 165.7574 | 143.8139 | 21.9435
2006-03-08 | 168000 | 1453700.5236 | 0.11557 | 0.1347 | 0.019133 | 27813.4605 | 0.85859 | 168.1236 | 144.2432 | 23.8804
2006-03-09 | 170300 | 1441832.4072 | 0.11811 | 0.1347 | 0.016586 | 23914.8253 | 0.85859 | 166.751 | 146.218 | 20.533
2006-03-10 | 165800 | 1442383.4827 | 0.11495 | 0.1347 | 0.019751 | 28489.0551 | 0.85859 | 166.8148 | 142.3543 | 24.4604
2006-03-11 | 166800 | 1392505.42 | 0.11978 | 0.1347 | 0.014916 | 20770.4801 | 0.85859 | 161.0463 | 143.2129 | 17.8333
2006-03-12 | 158800 | 1343091.5446 | 0.11823 | 0.1347 | 0.016465 | 22114.4311 | 0.85859 | 155.3314 | 136.3442 | 18.9872
2006-03-13 | 149500 | 1282426.9235 | 0.11658 | 0.1347 | 0.018124 | 23242.9066 | 0.85859 | 148.3155 | 128.3593 | 19.9561
2006-03-14 | 159100 | 1324266.1453 | 0.12014 | 0.1347 | 0.014558 | 19278.6498 | 0.85859 | 153.1543 | 136.6018 | 16.5525
2006-03-15 | 157600 | 1333946.5472 | 0.11815 | 0.1347 | 0.016554 | 22082.5999 | 0.85859 | 154.2738 | 135.3139 | 18.9599
2006-03-16 | 158500 | 1318116.7636 | 0.12025 | 0.1347 | 0.014453 | 19050.3281 | 0.85859 | 152.4431 | 136.0866 | 16.3564
2006-03-17 | 152400 | 1283057.8308 | 0.11878 | 0.1347 | 0.015921 | 20427.8898 | 0.85859 | 148.3884 | 130.8492 | 17.5392
2006-03-18 | 155100 | 1301563.4343 | 0.11916 | 0.1347 | 0.015536 | 20220.5946 | 0.85859 | 150.5286 | 133.1674 | 17.3612
2006-03-19 | 152700 | 1313864.2345 | 0.11622 | 0.1347 | 0.018478 | 24277.5124 | 0.85859 | 151.9512 | 131.1068 | 20.8444
2006-03-20 | 151200 | 1318586.5712 | 0.11467 | 0.1347 | 0.020032 | 26413.6111 | 0.85859 | 152.4974 | 129.8189 | 22.6785
2006-03-21 | 157100 | 1343689.1773 | 0.11692 | 0.1347 | 0.017783 | 23894.9322 | 0.85859 | 155.4006 | 134.8846 | 20.516
2006-03-22 | 158100 | 1461189.0817 | 0.1082 | 0.1347 | 0.0265 | 38722.1693 | 0.85859 | 168.9897 | 135.7432 | 33.2465
2006-03-23 | 154800 | 1285933.5003 | 0.12038 | 0.1347 | 0.014321 | 18415.2425 | 0.85859 | 148.721 | 132.9098 | 15.8112
2006-03-24 | 155600 | 1293625.2828 | 0.12028 | 0.1347 | 0.014418 | 18651.3256 | 0.85859 | 149.6106 | 133.5967 | 16.0139
2006-03-25 | 152000 | 1288889.836 | 0.11793 | 0.1347 | 0.016769 | 21613.4609 | 0.85859 | 149.0629 | 130.5058 | 18.5571
2006-03-26 | 151000 | 1289094.4056 | 0.11714 | 0.1347 | 0.017564 | 22641.0164 | 0.85859 | 149.0866 | 129.6472 | 19.4394
2006-03-27 | 147400 | 1253955.0413 | 0.11755 | 0.1347 | 0.017152 | 21507.7441 | 0.85859 | 145.0226 | 126.5563 | 18.4663
2006-03-28 | 144700 | 1247420.4839 | 0.116 | 0.1347 | 0.018701 | 23327.5392 | 0.85859 | 144.2669 | 124.2381 | 20.0288
2006-03-29 | 151000 | 1260023.8745 | 0.11984 | 0.1347 | 0.014861 | 18725.2159 | 0.85859 | 145.7245 | 129.6472 | 16.0773
2006-03-30 | 148900 | 1268620.2486 | 0.11737 | 0.1347 | 0.017328 | 21983.1475 | 0.85859 | 146.7187 | 127.8442 | 18.8745
2006-03-31 | 152900 | 1277144.9636 | 0.11972 | 0.1347 | 0.01498 | 19131.4266 | 0.85859 | 147.7046 | 131.2785 | 16.4261
2006-04-01 | 156500 | 1328981.6549 | 0.11776 | 0.1347 | 0.016941 | 22513.8289 | 0.87868 | 157.2964 | 137.5139 | 19.7825
2006-04-02 | 159600 | 1350288.3151 | 0.1182 | 0.1347 | 0.016503 | 22283.836 | 0.87868 | 159.8182 | 140.2378 | 19.5804
2006-04-03 | 148700 | 1341233.3579 | 0.11087 | 0.1347 | 0.023832 | 31964.1333 | 0.87868 | 158.7465 | 130.6601 | 28.0863
2006-04-04 | 157400 | 1352624.6043 | 0.11637 | 0.1347 | 0.018334 | 24798.5342 | 0.87868 | 160.0947 | 138.3047 | 21.79
2006-04-05 | 160100 | 1366833.3917 | 0.11713 | 0.1347 | 0.017568 | 24012.4579 | 0.87868 | 161.7765 | 140.6771 | 21.0993
2006-04-06 | 147000 | 1306486.4863 | 0.11252 | 0.1347 | 0.022184 | 28983.7297 | 0.87868 | 154.6339 | 129.1664 | 25.4675
2006-04-07 | 164000 | 1369828.0605 | 0.11972 | 0.1347 | 0.014977 | 20515.8397 | 0.87868 | 162.1309 | 144.104 | 18.0269
2006-04-08 | 146000 | 1329491.5961 | 0.10982 | 0.1347 | 0.024884 | 33082.518 | 0.87868 | 157.3567 | 128.2877 | 29.069
2006-04-09 | 168000 | 1343053.4065 | 0.12509 | 0.1347 | 0.0096119 | 12909.2938 | 0.87868 | 158.9619 | 147.6187 | 11.3432
2006-04-10 | 162000 | 1361295.1799 | 0.119 | 0.1347 | 0.015696 | 21366.4607 | 0.87868 | 161.121 | 142.3466 | 18.7743
2006-04-11 | 167000 | 1384082.9431 | 0.12066 | 0.1347 | 0.014042 | 19435.9724 | 0.87868 | 163.8181 | 146.74 | 17.0781
2006-04-12 | 110000 | 968371.0769 | 0.11359 | 0.1347 | 0.021107 | 20439.5841 | 0.87868 | 114.615 | 96.6551 | 17.9599
2006-04-13 | 110000 | 913103.7656 | 0.12047 | 0.1347 | 0.014232 | 12995.0772 | 0.87868 | 108.0737 | 96.6551 | 11.4186
2006-04-14 | 113000 | 913747.9553 | 0.12367 | 0.1347 | 0.011034 | 10081.8496 | 0.87868 | 108.1499 | 99.2912 | 8.8587
2006-04-15 | 109000 | 899474.3403 | 0.12118 | 0.1347 | 0.013518 | 12159.1936 | 0.87868 | 106.4605 | 95.7764 | 10.6841
2006-04-16 | 112000 | 904327.1627 | 0.12385 | 0.1347 | 0.010851 | 9812.8688 | 0.87868 | 107.0349 | 98.4125 | 8.6224
2006-04-17 | 114000 | 906758.2946 | 0.12572 | 0.1347 | 0.0089774 | 8140.3423 | 0.87868 | 107.3226 | 100.1698 | 7.1528
2006-04-18 | 110000 | 908586.8064 | 0.12107 | 0.1347 | 0.013633 | 12386.6428 | 0.87868 | 107.539 | 96.6551 | 10.8839
2006-04-19 | 134000 | 1217974.0171 | 0.11002 | 0.1347 | 0.024681 | 30061.1001 | 0.87868 | 144.1577 | 117.7435 | 26.4142
2006-04-20 | 126000 | 965455.2344 | 0.13051 | 0.1347 | 0.0041916 | 4046.8201 | 0.87868 | 114.2699 | 110.714 | 3.5559
2006-04-21 | 129000 | 965082.8888 | 0.13367 | 0.1347 | 0.0010327 | 996.6651 | 0.87868 | 114.2258 | 113.3501 | 0.87575
2006-04-22 | 109000 | 904471.7853 | 0.12051 | 0.1347 | 0.014188 | 12832.3495 | 0.87868 | 107.052 | 95.7764 | 11.2756
2006-04-23 | 141000 | 1333194.2103 | 0.10576 | 0.1347 | 0.028939 | 38581.2601 | 0.87868 | 157.795 | 123.8943 | 33.9007
2006-04-24 | 166000 | 1368368.4489 | 0.12131 | 0.1347 | 0.013388 | 18319.2301 | 0.87868 | 161.9581 | 145.8613 | 16.0968
2006-04-25 | 167000 | 1378112.0599 | 0.12118 | 0.1347 | 0.01352 | 18631.6945 | 0.87868 | 163.1114 | 146.74 | 16.3714
2006-04-26 | 124000 | 1011542.8833 | 0.12259 | 0.1347 | 0.012115 | 12254.8264 | 0.87868 | 119.7248 | 108.9567 | 10.7681
2006-04-27 | 107000 | 880755.2711 | 0.12149 | 0.1347 | 0.013213 | 11637.735 | 0.87868 | 104.2449 | 94.0191 | 10.2259
2006-04-28 | 108000 | 874585.8275 | 0.12349 | 0.1347 | 0.011213 | 9806.711 | 0.87868 | 103.5147 | 94.8977 | 8.617
2006-04-29 | 113000 | 907430.6848 | 0.12453 | 0.1347 | 0.010173 | 9230.9132 | 0.87868 | 107.4022 | 99.2912 | 8.111
2006-04-30 | 114000 | 900658.9685 | 0.12657 | 0.1347 | 0.008126 | 7318.7631 | 0.87868 | 106.6007 | 100.1698 | 6.4309
2006-05-01 | 110000 | 895442.1234 | 0.12284 | 0.1347 | 0.011856 | 10616.054 | 0.87868 | 105.9833 | 96.6551 | 9.3281
2006-05-02 | 108000 | 892445.7023 | 0.12102 | 0.1347 | 0.013684 | 12212.4361 | 0.87868 | 105.6286 | 94.8977 | 10.7309
2006-05-03 | 119000 | 960073.443 | 0.12395 | 0.1347 | 0.010751 | 10321.8928 | 0.87868 | 113.6329 | 104.5633 | 9.0697
2006-05-04 | 108000 | 916151.7116 | 0.11788 | 0.1347 | 0.016816 | 15405.6356 | 0.87868 | 108.4344 | 94.8977 | 13.5367
2006-05-05 | 109000 | 892188.2872 | 0.12217 | 0.1347 | 0.012528 | 11177.7623 | 0.87868 | 105.5981 | 95.7764 | 9.8217
2006-05-06 | 112000 | 925670.85 | 0.12099 | 0.1347 | 0.013707 | 12687.8635 | 0.87868 | 109.5611 | 98.4125 | 11.1486
2006-05-07 | 111000 | 911583.4351 | 0.12177 | 0.1347 | 0.012934 | 11790.2887 | 0.87868 | 107.8937 | 97.5338 | 10.3599
2006-05-08 | 113000 | 928652.134 | 0.12168 | 0.1347 | 0.013018 | 12089.4424 | 0.87868 | 109.9139 | 99.2912 | 10.6228
2006-05-09 | 118000 | 962863.7813 | 0.12255 | 0.1347 | 0.012149 | 11697.7513 | 0.87868 | 113.9632 | 103.6846 | 10.2786
2006-05-10 | 131000 | 1034330.9783 | 0.12665 | 0.1347 | 0.0080481 | 8324.3828 | 0.87868 | 122.4219 | 115.1075 | 7.3145
2006-05-11 | 117000 | 993801.0934 | 0.11773 | 0.1347 | 0.01697 | 16865.0073 | 0.87868 | 117.6249 | 102.8059 | 14.819
2006-05-12 | 121000 | 1015989.4917 | 0.1191 | 0.1347 | 0.015604 | 15853.7845 | 0.87868 | 120.2511 | 106.3206 | 13.9304
2006-05-13 | 121000 | 998879.8614 | 0.12114 | 0.1347 | 0.013564 | 13549.1173 | 0.87868 | 118.226 | 106.3206 | 11.9054
2006-05-14 | 118000 | 936330.587 | 0.12602 | 0.1347 | 0.0086761 | 8123.7301 | 0.87868 | 110.8228 | 103.6846 | 7.1382
2006-05-15 | 152000 | 1299145.301 | 0.117 | 0.1347 | 0.0177 | 22994.872 | 0.87868 | 153.765 | 133.5598 | 20.2052
2006-05-16 | 167000 | 1419312.8321 | 0.11766 | 0.1347 | 0.017037 | 24181.4385 | 0.87868 | 167.9878 | 146.74 | 21.2478
2006-05-17 | 125000 | 1019496.7315 | 0.12261 | 0.1347 | 0.01209 | 12326.2097 | 0.87868 | 120.6662 | 109.8354 | 10.8308
2006-05-18 | 119000 | 970168.753 | 0.12266 | 0.1347 | 0.012041 | 11681.731 | 0.87868 | 114.8278 | 104.5633 | 10.2645
2006-05-19 | 121000 | 978685.4775 | 0.12364 | 0.1347 | 0.011065 | 10828.9338 | 0.87868 | 115.8358 | 106.3206 | 9.5152
2006-05-20 | 119000 | 991211.4659 | 0.12006 | 0.1347 | 0.014645 | 14516.1845 | 0.87868 | 117.3184 | 104.5633 | 12.7551
2006-05-21 | 116000 | 988200.2813 | 0.11739 | 0.1347 | 0.017315 | 17110.5779 | 0.87868 | 116.962 | 101.9272 | 15.0348
2006-05-22 | 119000 | 1001762.381 | 0.11879 | 0.1347 | 0.015909 | 15937.3927 | 0.87868 | 118.5672 | 104.5633 | 14.0039
2006-05-23 | 119000 | 998919.7941 | 0.11913 | 0.1347 | 0.015571 | 15554.4963 | 0.87868 | 118.2307 | 104.5633 | 13.6675
2006-05-24 | 116000 | 971896.335 | 0.11935 | 0.1347 | 0.015346 | 14914.4363 | 0.87868 | 115.0323 | 101.9272 | 13.1051
2006-05-25 | 120000 | 991990.1567 | 0.12097 | 0.1347 | 0.013731 | 13621.0741 | 0.87868 | 117.4105 | 105.4419 | 11.9686
2006-05-26 | 120000 | 990694.304 | 0.12113 | 0.1347 | 0.013573 | 13446.5227 | 0.87868 | 117.2572 | 105.4419 | 11.8152
2006-05-27 | 116000 | 974001.8471 | 0.1191 | 0.1347 | 0.015604 | 15198.0488 | 0.87868 | 115.2815 | 101.9272 | 13.3543
2006-05-28 | 119000 | 969692.9015 | 0.12272 | 0.1347 | 0.011981 | 11617.6338 | 0.87868 | 114.7715 | 104.5633 | 10.2082
2006-05-29 | 117000 | 975154.4687 | 0.11998 | 0.1347 | 0.014719 | 14353.3069 | 0.87868 | 115.4179 | 102.8059 | 12.612
2006-05-30 | 121000 | 992044.9651 | 0.12197 | 0.1347 | 0.01273 | 12628.4568 | 0.87868 | 117.417 | 106.3206 | 11.0964
2006-05-31 | 126000 | 1019004.2262 | 0.12365 | 0.1347 | 0.01105 | 11259.8693 | 0.87868 | 120.6079 | 110.714 | 9.8939
2006-06-01 | 120000 | 991744.2182 | 0.121 | 0.1347 | 0.013701 | 13587.9462 | 0.87868 | 117.3814 | 105.4419 | 11.9395
2006-06-02 | 118000 | 1044331.2145 | 0.11299 | 0.1347 | 0.021709 | 22671.4146 | 0.87868 | 123.6056 | 103.6846 | 19.921
2006-06-03 | 118000 | 1007316.6903 | 0.11714 | 0.1347 | 0.017557 | 17685.5582 | 0.87868 | 119.2246 | 103.6846 | 15.54
2006-06-04 | 118000 | 1002578.9403 | 0.1177 | 0.1347 | 0.017004 | 17047.3833 | 0.87868 | 118.6638 | 103.6846 | 14.9792
2006-06-05 | 124000 | 994500.1177 | 0.12469 | 0.1347 | 0.010014 | 9959.1659 | 0.87868 | 117.7076 | 108.9567 | 8.7509
2006-06-06 | 125000 | 1002749.4415 | 0.12466 | 0.1347 | 0.010043 | 10070.3498 | 0.87868 | 118.684 | 109.8354 | 8.8486
2006-06-07 | 121000 | 993212.8595 | 0.12183 | 0.1347 | 0.012873 | 12785.7722 | 0.87868 | 117.5553 | 106.3206 | 11.2346
2006-06-08 | 118000 | 968625.4307 | 0.12182 | 0.1347 | 0.012878 | 12473.8455 | 0.87868 | 114.6451 | 103.6846 | 10.9606
2006-06-09 | 118000 | 1018089.4344 | 0.1159 | 0.1347 | 0.018797 | 19136.6468 | 0.87868 | 120.4996 | 103.6846 | 16.815
2006-06-10 | 125000 | 1040214.0151 | 0.12017 | 0.1347 | 0.014532 | 15116.8278 | 0.87868 | 123.1183 | 109.8354 | 13.2829
2006-06-11 | 122000 | 1032748.1857 | 0.11813 | 0.1347 | 0.016569 | 17111.1806 | 0.87868 | 122.2346 | 107.1993 | 15.0353
2006-06-12 | 125000 | 1042151.2433 | 0.11994 | 0.1347 | 0.014756 | 15377.7725 | 0.87868 | 123.3475 | 109.8354 | 13.5122
2006-06-13 | 123000 | 1040329.6121 | 0.11823 | 0.1347 | 0.016468 | 17132.3988 | 0.87868 | 123.1319 | 108.078 | 15.0539
2006-06-14 | 124000 | 1045797.5707 | 0.11857 | 0.1347 | 0.01613 | 16868.9328 | 0.87868 | 123.7791 | 108.9567 | 14.8224
2006-06-15 | 124000 | 1056316.9656 | 0.11739 | 0.1347 | 0.017311 | 18285.8953 | 0.87868 | 125.0242 | 108.9567 | 16.0675
2006-06-16 | 124000 | 1034188.522 | 0.1199 | 0.1347 | 0.014799 | 15305.1939 | 0.87868 | 122.4051 | 108.9567 | 13.4484
2006-06-17 | 124000 | 1044481.4333 | 0.11872 | 0.1347 | 0.015981 | 16691.6491 | 0.87868 | 123.6233 | 108.9567 | 14.6667
2006-06-18 | 122000 | 1026755.9996 | 0.11882 | 0.1347 | 0.015879 | 16304.0332 | 0.87868 | 121.5254 | 107.1993 | 14.3261
2006-06-19 | 123000 | 1050918.1248 | 0.11704 | 0.1347 | 0.017659 | 18558.6714 | 0.87868 | 124.3852 | 108.078 | 16.3072
2006-06-20 | 122000 | 1107697.4194 | 0.11014 | 0.1347 | 0.024562 | 27206.8424 | 0.87868 | 131.1055 | 107.1993 | 23.9062
2006-06-21 | 126000 | 1065757.4817 | 0.11823 | 0.1347 | 0.016474 | 17557.5328 | 0.87868 | 126.1415 | 110.714 | 15.4275
2006-06-22 | 124000 | 1063804.9301 | 0.11656 | 0.1347 | 0.018137 | 19294.5241 | 0.87868 | 125.9104 | 108.9567 | 16.9538
2006-06-23 | 119000 | 1057091.6094 | 0.11257 | 0.1347 | 0.022127 | 23390.2398 | 0.87868 | 125.1159 | 104.5633 | 20.5526
2006-06-24 | 126000 | 1056122.6523 | 0.1193 | 0.1347 | 0.015396 | 16259.7213 | 0.87868 | 125.0012 | 110.714 | 14.2871
2006-06-25 | 132000 | 1059012.9202 | 0.12464 | 0.1347 | 0.010056 | 10649.0404 | 0.87868 | 125.3433 | 115.9861 | 9.3571
2006-06-26 | 171000 | 1458889.4098 | 0.11721 | 0.1347 | 0.017488 | 25512.4035 | 0.87868 | 172.6721 | 150.2548 | 22.4173
2006-06-27 | 137000 | 1146134.8904 | 0.11953 | 0.1347 | 0.015168 | 17384.3697 | 0.87868 | 135.6549 | 120.3795 | 15.2753
2006-06-28 | 121000 | 1026965.9726 | 0.11782 | 0.1347 | 0.016877 | 17332.3165 | 0.87868 | 121.5502 | 106.3206 | 15.2296
2006-06-29 | 131000 | 1053703.821 | 0.12432 | 0.1347 | 0.010377 | 10933.9047 | 0.87868 | 124.7149 | 115.1075 | 9.6074
2006-06-30 | 130000 | 1051867.9929 | 0.12359 | 0.1347 | 0.01111 | 11686.6186 | 0.87868 | 124.4976 | 114.2288 | 10.2688
2006-07-01 | 147000 | 1291861.5503 | 0.11379 | 0.1347 | 0.020911 | 27013.7508 | 0.87868 | 152.9029 | 129.1664 | 23.7365
2006-07-02 | 129000 | 1069871.1011 | 0.12058 | 0.1347 | 0.014125 | 15111.6373 | 0.87868 | 126.6284 | 113.3501 | 13.2783
2006-07-03 | 123000 | 1042341.1064 | 0.118 | 0.1347 | 0.016696 | 17403.347 | 0.87868 | 123.37 | 108.078 | 15.292
2006-07-04 | 120000 | 1022196.8648 | 0.11739 | 0.1347 | 0.017306 | 17689.9177 | 0.87868 | 120.9858 | 105.4419 | 15.5438
2006-07-05 | 120000 | 992129.8988 | 0.12095 | 0.1347 | 0.013748 | 13639.8974 | 0.87868 | 117.4271 | 105.4419 | 11.9851
2006-07-06 | 117000 | 986416.1967 | 0.11861 | 0.1347 | 0.016089 | 15870.2617 | 0.87868 | 116.7508 | 102.8059 | 13.9449
2006-07-07 | 116000 | 1000794.7172 | 0.11591 | 0.1347 | 0.018792 | 18807.0484 | 0.87868 | 118.4526 | 101.9272 | 16.5254
2006-07-08 | 123000 | 1027018.5378 | 0.11976 | 0.1347 | 0.014936 | 15339.397 | 0.87868 | 121.5565 | 108.078 | 13.4785
2006-07-09 | 123000 | 1013204.1954 | 0.1214 | 0.1347 | 0.013303 | 13478.6051 | 0.87868 | 119.9214 | 108.078 | 11.8434
2006-07-10 | 123000 | 1035526.1633 | 0.11878 | 0.1347 | 0.01592 | 16485.3742 | 0.87868 | 122.5634 | 108.078 | 14.4854
2006-07-11 | 117000 | 976186.847 | 0.11985 | 0.1347 | 0.014846 | 14492.3683 | 0.87868 | 115.5401 | 102.8059 | 12.7342
2006-07-12 | 122000 | 1023558.8731 | 0.11919 | 0.1347 | 0.015508 | 15873.3802 | 0.87868 | 121.147 | 107.1993 | 13.9477
2006-07-13 | 139000 | 1154736.9783 | 0.12037 | 0.1347 | 0.014326 | 16543.071 | 0.87868 | 136.673 | 122.1369 | 14.5361
2006-07-14 | 123000 | 1024715.3465 | 0.12003 | 0.1347 | 0.014667 | 15029.1572 | 0.87868 | 121.2839 | 108.078 | 13.2059
2006-07-15 | 122000 | 1004517.2892 | 0.12145 | 0.1347 | 0.013249 | 13308.4789 | 0.87868 | 118.8932 | 107.1993 | 11.6939
2006-07-16 | 122000 | 1006379.1697 | 0.12123 | 0.1347 | 0.013473 | 13559.2742 | 0.87868 | 119.1136 | 107.1993 | 11.9143
2006-07-17 | 121000 | 1012681.9028 | 0.11948 | 0.1347 | 0.015215 | 15408.2523 | 0.87868 | 119.8596 | 106.3206 | 13.539
2006-07-18 | 117000 | 982235.9949 | 0.11912 | 0.1347 | 0.015584 | 15307.1885 | 0.87868 | 116.2561 | 102.8059 | 13.4502
2006-07-19 | 124000 | 1008171.9471 | 0.12299 | 0.1347 | 0.011705 | 11800.7613 | 0.87868 | 119.3258 | 108.9567 | 10.3691
2006-07-20 | 125000 | 1011606.354 | 0.12357 | 0.1347 | 0.011134 | 11263.3759 | 0.87868 | 119.7323 | 109.8354 | 9.8969
2006-07-21 | 127000 | 1026406.6176 | 0.12373 | 0.1347 | 0.010967 | 11256.9714 | 0.87868 | 121.484 | 111.5927 | 9.8913
2006-07-22 | 126000 | 1059763.1938 | 0.11889 | 0.1347 | 0.015806 | 16750.1022 | 0.87868 | 125.4321 | 110.714 | 14.718
2006-07-23 | 128000 | 1055291.4027 | 0.12129 | 0.1347 | 0.013406 | 14147.752 | 0.87868 | 124.9028 | 112.4714 | 12.4314
2006-07-24 | 128000 | 1042254.7492 | 0.12281 | 0.1347 | 0.011889 | 12391.7147 | 0.87868 | 123.3598 | 112.4714 | 10.8884
2006-07-25 | 124000 | 1039867.2228 | 0.11925 | 0.1347 | 0.015454 | 16070.1149 | 0.87868 | 123.0772 | 108.9567 | 14.1205
2006-07-26 | 122000 | 1029279.9616 | 0.11853 | 0.1347 | 0.016171 | 16644.0108 | 0.87868 | 121.8241 | 107.1993 | 14.6248
2006-07-27 | 122000 | 1109409.6156 | 0.10997 | 0.1347 | 0.024732 | 27437.4752 | 0.87868 | 131.3081 | 107.1993 | 24.1088
2006-07-28 | 124000 | 1025525.5347 | 0.12091 | 0.1347 | 0.013786 | 14138.2895 | 0.87868 | 121.3797 | 108.9567 | 12.4231
2006-07-29 | 122000 | 1008925.8569 | 0.12092 | 0.1347 | 0.013779 | 13902.3129 | 0.87868 | 119.415 | 107.1993 | 12.2157
2006-07-30 | 124000 | 1018920.0767 | 0.1217 | 0.1347 | 0.013003 | 13248.5343 | 0.87868 | 120.5979 | 108.9567 | 11.6413
2006-07-31 | 124000 | 1032332.238 | 0.12012 | 0.1347 | 0.014584 | 15055.1525 | 0.87868 | 122.1854 | 108.9567 | 13.2287
2006-08-01 | 136000 | 1108240.631 | 0.12272 | 0.1347 | 0.011983 | 13280.013 | 0.87868 | 131.1698 | 119.5009 | 11.6689
2006-08-02 | 127000 | 1062759.1809 | 0.1195 | 0.1347 | 0.0152 | 16153.6617 | 0.87868 | 125.7867 | 111.5927 | 14.1939
2006-08-03 | 130000 | 1072886.4211 | 0.12117 | 0.1347 | 0.013532 | 14517.8009 | 0.87868 | 126.9853 | 114.2288 | 12.7565
2006-08-04 | 125000 | 1083783.5806 | 0.11534 | 0.1347 | 0.019363 | 20985.6483 | 0.87868 | 128.2751 | 109.8354 | 18.4397
2006-08-05 | 138000 | 1135188.2851 | 0.12157 | 0.1347 | 0.013134 | 14909.862 | 0.87868 | 134.3593 | 121.2582 | 13.101
2006-08-06 | 130000 | 1184170.2919 | 0.10978 | 0.1347 | 0.024918 | 29507.7383 | 0.87868 | 140.1567 | 114.2288 | 25.9279
2006-08-07 | 134000 | 1173281.7751 | 0.11421 | 0.1347 | 0.02049 | 24041.0551 | 0.87868 | 138.868 | 117.7435 | 21.1245
2006-08-08 | 137000 | 1345665.6228 | 0.10181 | 0.1347 | 0.032892 | 44261.1594 | 0.87868 | 159.2711 | 120.3795 | 38.8915
2006-08-09 | 139000 | 1343198.8833 | 0.10348 | 0.1347 | 0.031216 | 41928.8896 | 0.87868 | 158.9791 | 122.1369 | 36.8422
2006-08-10 | 132000 | 1299950.6777 | 0.10154 | 0.1347 | 0.033158 | 43103.3563 | 0.87868 | 153.8603 | 115.9861 | 37.8742
2006-08-11 | 122000 | 1237141.7476 | 0.098614 | 0.1347 | 0.036086 | 44642.9934 | 0.87868 | 146.4263 | 107.1993 | 39.227
2006-08-12 | 129000 | 1150767.3987 | 0.1121 | 0.1347 | 0.022601 | 26008.3686 | 0.87868 | 136.2032 | 113.3501 | 22.8531
2006-08-13 | 133000 | 1094254.8832 | 0.12154 | 0.1347 | 0.013156 | 14396.1328 | 0.87868 | 129.5145 | 116.8648 | 12.6496
2006-08-14 | 129000 | 1086809.376 | 0.1187 | 0.1347 | 0.016004 | 17393.2229 | 0.87868 | 128.6332 | 113.3501 | 15.2831
2006-08-15 | 140000 | 1165519.4218 | 0.12012 | 0.1347 | 0.014582 | 16995.4661 | 0.87868 | 137.9492 | 123.0156 | 14.9336
2006-08-16 | 129000 | 1090480.7895 | 0.1183 | 0.1347 | 0.016404 | 17887.7624 | 0.87868 | 129.0678 | 113.3501 | 15.7177
2006-08-17 | 138000 | 1119187.4424 | 0.1233 | 0.1347 | 0.011396 | 12754.5485 | 0.87868 | 132.4654 | 121.2582 | 11.2072
2006-08-18 | 136000 | 1120951.4368 | 0.12133 | 0.1347 | 0.013374 | 14992.1585 | 0.87868 | 132.6742 | 119.5009 | 13.1734
2006-08-19 | 129000 | 1106824.6124 | 0.11655 | 0.1347 | 0.01815 | 20089.2753 | 0.87868 | 131.0022 | 113.3501 | 17.6521
2006-08-20 | 129000 | 1025149.2763 | 0.12584 | 0.1347 | 0.0088647 | 9087.6075 | 0.87868 | 121.3352 | 113.3501 | 7.9851
2006-08-21 | 125000 | 1076269.7155 | 0.11614 | 0.1347 | 0.018558 | 19973.5307 | 0.87868 | 127.3858 | 109.8354 | 17.5504
2006-08-22 | 123000 | 1092015.6017 | 0.11264 | 0.1347 | 0.022064 | 24094.5016 | 0.87868 | 129.2494 | 108.078 | 21.1714
2006-08-23 | 125000 | 1096826.4049 | 0.11397 | 0.1347 | 0.020735 | 22742.5167 | 0.87868 | 129.8188 | 109.8354 | 19.9835
2006-08-24 | 121000 | 995874.6001 | 0.1215 | 0.1347 | 0.013199 | 13144.3086 | 0.87868 | 117.8703 | 106.3206 | 11.5497
2006-08-25 | 124000 | 1057691.75 | 0.11724 | 0.1347 | 0.017464 | 18471.0787 | 0.87868 | 125.1869 | 108.9567 | 16.2302
2006-08-26 | 140000 | 1147211.7214 | 0.12204 | 0.1347 | 0.012665 | 14529.4189 | 0.87868 | 135.7823 | 123.0156 | 12.7668
2006-08-27 | 133000 | 1055638.3992 | 0.12599 | 0.1347 | 0.0087099 | 9194.4924 | 0.87868 | 124.9439 | 116.8648 | 8.079
2006-08-28 | 134000 | 1068586.8364 | 0.1254 | 0.1347 | 0.0093007 | 9938.6469 | 0.87868 | 126.4764 | 117.7435 | 8.7329
2006-08-29 | 125000 | 1035427.2047 | 0.12072 | 0.1347 | 0.013977 | 14472.0445 | 0.87868 | 122.5517 | 109.8354 | 12.7163
2006-08-30 | 127000 | 1033443.9704 | 0.12289 | 0.1347 | 0.01181 | 12204.9028 | 0.87868 | 122.317 | 111.5927 | 10.7242
2006-08-31 | 128000 | 958482.4257 | 0.13354 | 0.1347 | 0.0011556 | 1107.5827 | 0.87868 | 113.4446 | 112.4714 | 0.97321
2006-09-01 | 128000 | 989847.6121 | 0.12931 | 0.1347 | 0.0053872 | 5332.4734 | 0.87868 | 117.157 | 112.4714 | 4.6856
2006-09-02 | 120000 | 1051496.511 | 0.11412 | 0.1347 | 0.020577 | 21636.58 | 0.87868 | 124.4536 | 105.4419 | 19.0117
2006-09-03 | 125000 | 1034562.9365 | 0.12082 | 0.1347 | 0.013876 | 14355.6275 | 0.87868 | 122.4494 | 109.8354 | 12.614
2006-09-04 | 126000 | 1120459.6349 | 0.11245 | 0.1347 | 0.022246 | 24925.9128 | 0.87868 | 132.616 | 110.714 | 21.902
2006-09-05 | 131000 | 1101476.6055 | 0.11893 | 0.1347 | 0.015769 | 17368.8988 | 0.87868 | 130.3692 | 115.1075 | 15.2618
2006-09-06 | 130000 | 1109951.5731 | 0.11712 | 0.1347 | 0.017578 | 19510.4769 | 0.87868 | 131.3723 | 114.2288 | 17.1435
2006-09-07 | 129000 | 1109743.6364 | 0.11624 | 0.1347 | 0.018457 | 20482.4678 | 0.87868 | 131.3477 | 113.3501 | 17.9976
2006-09-08 | 130000 | 1128324.1069 | 0.11522 | 0.1347 | 0.019485 | 21985.2572 | 0.87868 | 133.5468 | 114.2288 | 19.3181
2006-09-09 | 141000 | 1211855.6817 | 0.11635 | 0.1347 | 0.01835 | 22236.9603 | 0.87868 | 143.4335 | 123.8943 | 19.5392
2006-09-10 | 132000 | 1101181.3834 | 0.11987 | 0.1347 | 0.014829 | 16329.1323 | 0.87868 | 130.3343 | 115.9861 | 14.3481
2006-09-11 | 136000 | 1235605.9152 | 0.11007 | 0.1347 | 0.024633 | 30436.1168 | 0.87868 | 146.2446 | 119.5009 | 26.7437
2006-09-12 | 134000 | 1139292.5588 | 0.11762 | 0.1347 | 0.017083 | 19462.7077 | 0.87868 | 134.845 | 117.7435 | 17.1015
2006-09-13 | 126000 | 1138670.8757 | 0.11066 | 0.1347 | 0.024045 | 27378.967 | 0.87868 | 134.7715 | 110.714 | 24.0574
2006-09-14 | 129000 | 1156083.5216 | 0.11158 | 0.1347 | 0.023116 | 26724.4504 | 0.87868 | 136.8324 | 113.3501 | 23.4823
2006-09-15 | 134000 | 1108824.9725 | 0.12085 | 0.1347 | 0.013851 | 15358.7238 | 0.87868 | 131.2389 | 117.7435 | 13.4954
2006-09-16 | 130000 | 1121293.8876 | 0.11594 | 0.1347 | 0.018763 | 21038.2867 | 0.87868 | 132.7147 | 114.2288 | 18.486
2006-09-17 | 131000 | 1100356.7353 | 0.11905 | 0.1347 | 0.015648 | 17218.0522 | 0.87868 | 130.2367 | 115.1075 | 15.1292
2006-09-18 | [7 empty] | 0 | 0 | 0
2006-09-19 | 137000 | 1152216.0946 | 0.1189 | 0.1347 | 0.015799 | 18203.5079 | 0.87868 | 136.3747 | 120.3795 | 15.9951
2006-09-20 | 129000 | 1099596.1367 | 0.11732 | 0.1347 | 0.017384 | 19115.5996 | 0.87868 | 130.1466 | 113.3501 | 16.7965
2006-09-21 | 129000 | 1081900.8977 | 0.11923 | 0.1347 | 0.015465 | 16732.0509 | 0.87868 | 128.0523 | 113.3501 | 14.7022
| 48998656.45 | 412885651.4778 | 0.11867 | 0.1347 |  | 7547014.0244 | 0.86835 | 47966.0672 | 41427.1807 | 6538.8865

## Measure IIER
Date | Quantity of biogas consumed in heater | Methane content in biogas | Energy content of biogas | Fuel oil energy saved equivalent to biogas used | Emission reduction | Project power consumption | Emission factor for CPP power | Project emission | Net Emission reduction
| Nm3 | fraction | MJ | MJ | t CO2 | MWh | t CO2/MWh | t CO2 | t CO2
2005-09-22 | 9038.16 | 0.6838 | 220636.4889 | 220636.4889 | 16.8992 | 0.66616 | 0.85859 | 0.57196 | 16.3273
2005-09-23 | 9047.52 | 0.6838 | 220864.9821 | 220864.9821 | 16.9167 | 0.66685 | 0.85859 | 0.57255 | 16.3442
2005-09-24 | 9177.84 | 0.6838 | 224046.3096 | 224046.3096 | 17.1604 | 0.67645 | 0.85859 | 0.5808 | 16.5796
2005-09-25 | 9210.24 | 0.6838 | 224837.2474 | 224837.2474 | 17.221 | 0.67884 | 0.85859 | 0.58285 | 16.6381
2005-09-26 | 9281.76 | 0.6838 | 226583.1693 | 226583.1693 | 17.3547 | 0.68411 | 0.85859 | 0.58737 | 16.7673
2005-09-27 | 9464.4 | 0.6838 | 231041.7149 | 231041.7149 | 17.6962 | 0.69758 | 0.85859 | 0.59893 | 17.0972
2005-09-28 | 9597.6 | 0.6838 | 234293.348 | 234293.348 | 17.9452 | 0.70739 | 0.85859 | 0.60736 | 17.3379
2005-09-29 | 9444.24 | 0.6838 | 230549.5758 | 230549.5758 | 17.6585 | 0.69609 | 0.85859 | 0.59766 | 17.0608
2005-09-30 | 9369.36 | 0.6838 | 228721.6307 | 228721.6307 | 17.5185 | 0.69057 | 0.85859 | 0.59292 | 16.9256
2005-10-01 | 9498.24 | 0.7142 | 242176.0554 | 242176.0554 | 18.549 | 0.70007 | 0.85859 | 0.60107 | 17.9479
2005-10-02 | 9578.16 | 0.7142 | 244213.7708 | 244213.7708 | 18.7051 | 0.70596 | 0.85859 | 0.60613 | 18.0989
2005-10-03 | 9555.36 | 0.7142 | 243632.4406 | 243632.4406 | 18.6605 | 0.70428 | 0.85859 | 0.60469 | 18.0559
2005-10-04 | 9544.32 | 0.7142 | 243350.9544 | 243350.9544 | 18.639 | 0.70347 | 0.85859 | 0.60399 | 18.035
2005-10-05 | 9406.8 | 0.7142 | 239844.6152 | 239844.6152 | 18.3704 | 0.69333 | 0.85859 | 0.59529 | 17.7751
2005-10-06 | 8961.6 | 0.7142 | 228493.3775 | 228493.3775 | 17.501 | 0.66052 | 0.85859 | 0.56711 | 16.9339
2005-10-07 | 9124.32 | 0.7142 | 232642.2396 | 232642.2396 | 17.8188 | 0.67251 | 0.85859 | 0.57741 | 17.2414
2005-10-08 | 9405.84 | 0.7142 | 239820.1381 | 239820.1381 | 18.3685 | 0.69326 | 0.85859 | 0.59523 | 17.7733
2005-10-09 | 6620.64 | 0.7142 | 168806.0608 | 168806.0608 | 12.9294 | 0.48798 | 0.85859 | 0.41897 | 12.5104
2005-10-10 | 6303.6 | 0.7142 | 160722.511 | 160722.511 | 12.3102 | 0.46461 | 0.85859 | 0.39891 | 11.9113
2005-10-11 | 9293.76 | 0.7142 | 236962.4411 | 236962.4411 | 18.1497 | 0.685 | 0.85859 | 0.58813 | 17.5615
2005-10-12 | 6366.48 | 0.7142 | 162325.7586 | 162325.7586 | 12.433 | 0.46924 | 0.85859 | 0.40289 | 12.0301
2005-10-13 | 0.48 | 0.7142 | 12.2385 | 12.2385 | 0.00093739 | 3.5378e-05 | 0.85859 | 3.0376e-05 | 0.00090701
2005-10-14 | 7124.88 | 0.7142 | 181662.6379 | 181662.6379 | 13.9141 | 0.52514 | 0.85859 | 0.45088 | 13.4632
2005-10-15 | 9247.2 | 0.7142 | 235775.3036 | 235775.3036 | 18.0587 | 0.68157 | 0.85859 | 0.58519 | 17.4736
2005-10-16 | 9305.52 | 0.7142 | 237262.2851 | 237262.2851 | 18.1726 | 0.68587 | 0.85859 | 0.58888 | 17.5838
2005-10-17 | 9139.68 | 0.7142 | 233033.8726 | 233033.8726 | 17.8488 | 0.67364 | 0.85859 | 0.57838 | 17.2704
2005-10-18 | 9106.8 | 0.7142 | 232195.5332 | 232195.5332 | 17.7846 | 0.67122 | 0.85859 | 0.5763 | 17.2083
2005-10-19 | 9456.96 | 0.7142 | 241123.5417 | 241123.5417 | 18.4684 | 0.69703 | 0.85859 | 0.59846 | 17.8699
2005-10-20 | 9362.88 | 0.7142 | 238724.7896 | 238724.7896 | 18.2846 | 0.69009 | 0.85859 | 0.59251 | 17.6921
2005-10-21 | 9455.52 | 0.7142 | 241086.8261 | 241086.8261 | 18.4656 | 0.69692 | 0.85859 | 0.59837 | 17.8672
2005-10-22 | 9526.32 | 0.7142 | 242892.0095 | 242892.0095 | 18.6038 | 0.70214 | 0.85859 | 0.60285 | 18.001
2005-10-23 | 9447.84 | 0.7142 | 240891.0096 | 240891.0096 | 18.4506 | 0.69635 | 0.85859 | 0.59788 | 17.8527
2005-10-24 | 9395.28 | 0.7142 | 239550.8904 | 239550.8904 | 18.3479 | 0.69248 | 0.85859 | 0.59456 | 17.7534
2005-10-25 | 9488.88 | 0.7142 | 241937.404 | 241937.404 | 18.5307 | 0.69938 | 0.85859 | 0.60048 | 17.9302
2005-10-26 | 9724.8 | 0.7142 | 247952.6421 | 247952.6421 | 18.9914 | 0.71677 | 0.85859 | 0.61541 | 18.376
2005-10-27 | 9746.4 | 0.7142 | 248503.376 | 248503.376 | 19.0336 | 0.71836 | 0.85859 | 0.61678 | 18.4168
2005-10-28 | 8954.64 | 0.7142 | 228315.9188 | 228315.9188 | 17.4874 | 0.66 | 0.85859 | 0.56667 | 16.9207
2005-10-29 | 9578.88 | 0.7142 | 244232.1286 | 244232.1286 | 18.7065 | 0.70601 | 0.85859 | 0.60618 | 18.1003
2005-10-30 | 9689.76 | 0.7142 | 247059.2293 | 247059.2293 | 18.923 | 0.71419 | 0.85859 | 0.61319 | 18.3098
2005-10-31 | 9640.08 | 0.7142 | 245792.5414 | 245792.5414 | 18.826 | 0.71052 | 0.85859 | 0.61005 | 18.2159
2005-11-01 | 9660.48 | 0.699 | 241070.5161 | 241070.5161 | 18.4643 | 0.71203 | 0.85859 | 0.61134 | 17.853
2005-11-02 | 9731.52 | 0.699 | 242843.2695 | 242843.2695 | 18.6001 | 0.71726 | 0.85859 | 0.61584 | 17.9843
2005-11-03 | 9547.92 | 0.699 | 238261.6601 | 238261.6601 | 18.2492 | 0.70373 | 0.85859 | 0.60422 | 17.645
2005-11-04 | 7655.04 | 0.699 | 191026.1647 | 191026.1647 | 14.6313 | 0.56422 | 0.85859 | 0.48443 | 14.1468
2005-11-05 | 9471.36 | 0.699 | 236351.1588 | 236351.1588 | 18.1028 | 0.69809 | 0.85859 | 0.59937 | 17.5035
2005-11-06 | 9569.76 | 0.699 | 238806.662 | 238806.662 | 18.2909 | 0.70534 | 0.85859 | 0.6056 | 17.6853
2005-11-07 | 9423.6 | 0.699 | 235159.3415 | 235159.3415 | 18.0116 | 0.69457 | 0.85859 | 0.59635 | 17.4152
2005-11-08 | 9405.12 | 0.699 | 234698.186 | 234698.186 | 17.9762 | 0.69321 | 0.85859 | 0.59518 | 17.3811
2005-11-09 | 9578.16 | 0.699 | 239016.2781 | 239016.2781 | 18.307 | 0.70596 | 0.85859 | 0.60613 | 17.7008
2005-11-10 | 9658.32 | 0.699 | 241016.6148 | 241016.6148 | 18.4602 | 0.71187 | 0.85859 | 0.6112 | 17.849
2005-11-11 | 9276.72 | 0.699 | 231494.0539 | 231494.0539 | 17.7308 | 0.68374 | 0.85859 | 0.58705 | 17.1438
2005-11-12 | 9294 | 0.699 | 231925.2642 | 231925.2642 | 17.7639 | 0.68502 | 0.85859 | 0.58815 | 17.1757
2005-11-13 | 9634.56 | 0.699 | 240423.7006 | 240423.7006 | 18.4148 | 0.71012 | 0.85859 | 0.6097 | 17.8051
2005-11-14 | 9626.64 | 0.699 | 240226.0626 | 240226.0626 | 18.3996 | 0.70953 | 0.85859 | 0.6092 | 17.7904
2005-11-15 | 9614.16 | 0.699 | 239914.6329 | 239914.6329 | 18.3758 | 0.70861 | 0.85859 | 0.60841 | 17.7674
2005-11-16 | 9407.52 | 0.699 | 234758.0763 | 234758.0763 | 17.9808 | 0.69338 | 0.85859 | 0.59533 | 17.3855
2005-11-17 | 9000.48 | 0.699 | 224600.6781 | 224600.6781 | 17.2028 | 0.66338 | 0.85859 | 0.56957 | 16.6333
2005-11-18 | 8665.92 | 0.699 | 216251.9675 | 216251.9675 | 16.5634 | 0.63872 | 0.85859 | 0.5484 | 16.015
2005-11-19 | 9310.56 | 0.699 | 232338.5074 | 232338.5074 | 17.7955 | 0.68624 | 0.85859 | 0.5892 | 17.2063
2005-11-20 | 9325.44 | 0.699 | 232709.8274 | 232709.8274 | 17.8239 | 0.68733 | 0.85859 | 0.59014 | 17.2338
2005-11-21 | 9306.48 | 0.699 | 232236.6939 | 232236.6939 | 17.7877 | 0.68594 | 0.85859 | 0.58894 | 17.1988
2005-11-22 | 9347.52 | 0.699 | 233260.8183 | 233260.8183 | 17.8661 | 0.68896 | 0.85859 | 0.59154 | 17.2746
2005-11-23 | 9383.28 | 0.699 | 234153.1841 | 234153.1841 | 17.9345 | 0.6916 | 0.85859 | 0.5938 | 17.3407
2005-11-24 | 9456.96 | 0.699 | 235991.8169 | 235991.8169 | 18.0753 | 0.69703 | 0.85859 | 0.59846 | 17.4769
2005-11-25 | 9176.16 | 0.699 | 228984.6495 | 228984.6495 | 17.5386 | 0.67633 | 0.85859 | 0.58069 | 16.9579
2005-11-26 | 7764.72 | 0.699 | 193763.1523 | 193763.1523 | 14.8409 | 0.5723 | 0.85859 | 0.49137 | 14.3495
2005-11-27 | 8028.96 | 0.699 | 200357.0765 | 200357.0765 | 15.3459 | 0.59178 | 0.85859 | 0.50809 | 14.8379
2005-11-28 | 9587.04 | 0.699 | 239237.8723 | 239237.8723 | 18.3239 | 0.70661 | 0.85859 | 0.60669 | 17.7173
2005-11-29 | 9538.32 | 0.699 | 238022.0988 | 238022.0988 | 18.2308 | 0.70302 | 0.85859 | 0.60361 | 17.6272
2005-11-30 | 7098 | 0.699 | 177125.6214 | 177125.6214 | 13.5666 | 0.52316 | 0.85859 | 0.44918 | 13.1174
2005-12-01 | 7071.12 | 0.69405 | 175205.2768 | 175205.2768 | 13.4195 | 0.52118 | 0.85859 | 0.44748 | 12.972
2005-12-02 | 9855.36 | 0.69405 | 244192.0201 | 244192.0201 | 18.7034 | 0.72639 | 0.85859 | 0.62367 | 18.0797
2005-12-03 | 9841.2 | 0.69405 | 243841.1695 | 243841.1695 | 18.6765 | 0.72535 | 0.85859 | 0.62278 | 18.0538
2005-12-04 | 9712.56 | 0.69405 | 240653.781 | 240653.781 | 18.4324 | 0.71587 | 0.85859 | 0.61464 | 17.8178
2005-12-05 | 6515.52 | 0.69405 | 161438.8506 | 161438.8506 | 12.3651 | 0.48023 | 0.85859 | 0.41232 | 11.9528
2005-12-06 | 6435.6 | 0.69405 | 159458.626 | 159458.626 | 12.2134 | 0.47434 | 0.85859 | 0.40726 | 11.8062
2005-12-07 | 8311.68 | 0.69405 | 205943.3577 | 205943.3577 | 15.7738 | 0.61261 | 0.85859 | 0.52598 | 15.2478
2005-12-08 | 6906 | 0.69405 | 171114.002 | 171114.002 | 13.1061 | 0.50901 | 0.85859 | 0.43703 | 12.6691
2005-12-09 | 9779.28 | 0.69405 | 242306.9414 | 242306.9414 | 18.559 | 0.72078 | 0.85859 | 0.61886 | 17.9402
2005-12-10 | 10003.92 | 0.69405 | 247872.9781 | 247872.9781 | 18.9853 | 0.73734 | 0.85859 | 0.63307 | 18.3523
2005-12-11 | 10023.84 | 0.69405 | 248366.5476 | 248366.5476 | 19.0231 | 0.73881 | 0.85859 | 0.63433 | 18.3888
2005-12-12 | 9799.44 | 0.69405 | 242806.4576 | 242806.4576 | 18.5973 | 0.72227 | 0.85859 | 0.62013 | 17.9771
2005-12-13 | 9791.52 | 0.69405 | 242610.2191 | 242610.2191 | 18.5822 | 0.72169 | 0.85859 | 0.61963 | 17.9626
2005-12-14 | 9839.28 | 0.69405 | 243793.5965 | 243793.5965 | 18.6729 | 0.72521 | 0.85859 | 0.62266 | 18.0502
2005-12-15 | 9895.2 | 0.69405 | 245179.1591 | 245179.1591 | 18.779 | 0.72933 | 0.85859 | 0.62619 | 18.1528
2005-12-16 | 7807.68 | 0.69405 | 193455.4549 | 193455.4549 | 14.8173 | 0.57547 | 0.85859 | 0.49409 | 14.3232
2005-12-17 | 9772.8 | 0.69405 | 242146.3827 | 242146.3827 | 18.5467 | 0.72031 | 0.85859 | 0.61845 | 17.9283
2005-12-18 | 6341.04 | 0.69405 | 157115.6576 | 157115.6576 | 12.034 | 0.46737 | 0.85859 | 0.40128 | 11.6327
2005-12-19 | 3.36 | 0.69405 | 83.2527 | 83.2527 | 0.0063766 | 0.00024765 | 0.85859 | 0.00021263 | 0.0061639
2005-12-20 | 980.16 | 0.69405 | 24285.9977 | 24285.9977 | 1.8601 | 0.072243 | 0.85859 | 0.062027 | 1.7981
2005-12-21 | 2255.04 | 0.69405 | 55874.4453 | 55874.4453 | 4.2796 | 0.16621 | 0.85859 | 0.1427 | 4.1369
2005-12-22 | 9766.8 | 0.69405 | 241997.7172 | 241997.7172 | 18.5353 | 0.71986 | 0.85859 | 0.61807 | 17.9173
2005-12-23 | 9916.32 | 0.69405 | 245702.4617 | 245702.4617 | 18.8191 | 0.73088 | 0.85859 | 0.62753 | 18.1916
2005-12-24 | 9775.2 | 0.69405 | 242205.8489 | 242205.8489 | 18.5513 | 0.72048 | 0.85859 | 0.6186 | 17.9327
2005-12-25 | 9753.84 | 0.69405 | 241676.5997 | 241676.5997 | 18.5107 | 0.71891 | 0.85859 | 0.61725 | 17.8935
2005-12-26 | 9767.52 | 0.69405 | 242015.557 | 242015.557 | 18.5367 | 0.71992 | 0.85859 | 0.61811 | 17.9186
2005-12-27 | 9455.28 | 0.69405 | 234279.0039 | 234279.0039 | 17.9441 | 0.6969 | 0.85859 | 0.59835 | 17.3458
2005-12-28 | 9781.92 | 0.69405 | 242372.3543 | 242372.3543 | 18.564 | 0.72098 | 0.85859 | 0.61903 | 17.945
2005-12-29 | 9950.64 | 0.69405 | 246552.8284 | 246552.8284 | 18.8842 | 0.73341 | 0.85859 | 0.6297 | 18.2545
2005-12-30 | 9943.68 | 0.69405 | 246380.3764 | 246380.3764 | 18.871 | 0.7329 | 0.85859 | 0.62926 | 18.2418
2005-12-31 | 9790.8 | 0.69405 | 242592.3792 | 242592.3792 | 18.5809 | 0.72163 | 0.85859 | 0.61959 | 17.9613
2006-01-01 | 9895.92 | 0.704 | 248712.1782 | 248712.1782 | 19.0496 | 0.72938 | 0.85859 | 0.62624 | 18.4234
2006-01-02 | 9969.6 | 0.704 | 250563.9629 | 250563.9629 | 19.1914 | 0.73481 | 0.85859 | 0.6309 | 18.5605
2006-01-03 | 9638.4 | 0.704 | 242239.9795 | 242239.9795 | 18.5539 | 0.7104 | 0.85859 | 0.60994 | 17.9439
2006-01-04 | 10060.32 | 0.704 | 252844.0105 | 252844.0105 | 19.3661 | 0.7415 | 0.85859 | 0.63664 | 18.7294
2006-01-05 | 10063.68 | 0.704 | 252928.4567 | 252928.4567 | 19.3725 | 0.74175 | 0.85859 | 0.63686 | 18.7357
2006-01-06 | 9982.56 | 0.704 | 250889.684 | 250889.684 | 19.2164 | 0.73577 | 0.85859 | 0.63172 | 18.5847
2006-01-07 | 10196.64 | 0.704 | 256270.1138 | 256270.1138 | 19.6285 | 0.75155 | 0.85859 | 0.64527 | 18.9832
2006-01-08 | 9180.24 | 0.704 | 230725.1359 | 230725.1359 | 17.6719 | 0.67663 | 0.85859 | 0.58095 | 17.091
2006-01-09 | 9430.08 | 0.704 | 237004.3146 | 237004.3146 | 18.1529 | 0.69505 | 0.85859 | 0.59676 | 17.5561
2006-01-10 | 9450.96 | 0.704 | 237529.0875 | 237529.0875 | 18.1931 | 0.69658 | 0.85859 | 0.59808 | 17.595
2006-01-11 | 9956.64 | 0.704 | 250238.2418 | 250238.2418 | 19.1665 | 0.73386 | 0.85859 | 0.63008 | 18.5364
2006-01-12 | 9909.36 | 0.704 | 249049.963 | 249049.963 | 19.0755 | 0.73037 | 0.85859 | 0.62709 | 18.4484
2006-01-13 | 9835.68 | 0.704 | 247198.1783 | 247198.1783 | 18.9337 | 0.72494 | 0.85859 | 0.62243 | 18.3112
2006-01-14 | 9679.44 | 0.704 | 243271.4296 | 243271.4296 | 18.6329 | 0.71342 | 0.85859 | 0.61254 | 18.0203
2006-01-15 | 9880.08 | 0.704 | 248314.0746 | 248314.0746 | 19.0191 | 0.72821 | 0.85859 | 0.62524 | 18.3939
2006-01-16 | 9773.04 | 0.704 | 245623.8597 | 245623.8597 | 18.8131 | 0.72032 | 0.85859 | 0.61846 | 18.1946
2006-01-17 | 9718.32 | 0.704 | 244248.5929 | 244248.5929 | 18.7077 | 0.71629 | 0.85859 | 0.615 | 18.0927
2006-01-18 | 9767.52 | 0.704 | 245485.1267 | 245485.1267 | 18.8024 | 0.71992 | 0.85859 | 0.61811 | 18.1843
2006-01-19 | 10030.32 | 0.704 | 252090.0265 | 252090.0265 | 19.3083 | 0.73929 | 0.85859 | 0.63474 | 18.6736
2006-01-20 | 9797.04 | 0.704 | 246227.0469 | 246227.0469 | 18.8593 | 0.72209 | 0.85859 | 0.61998 | 18.2393
2006-01-21 | 9852.24 | 0.704 | 247614.3775 | 247614.3775 | 18.9655 | 0.72616 | 0.85859 | 0.62348 | 18.3421
2006-01-22 | 9314.16 | 0.704 | 234090.9204 | 234090.9204 | 17.9297 | 0.6865 | 0.85859 | 0.58942 | 17.3403
2006-01-23 | 9870.48 | 0.704 | 248072.7997 | 248072.7997 | 19.0006 | 0.72751 | 0.85859 | 0.62463 | 18.376
2006-01-24 | 10193.04 | 0.704 | 256179.6357 | 256179.6357 | 19.6216 | 0.75128 | 0.85859 | 0.64504 | 18.9765
2006-01-25 | 9937.92 | 0.704 | 249767.7558 | 249767.7558 | 19.1305 | 0.73248 | 0.85859 | 0.6289 | 18.5016
2006-01-26 | 10197.36 | 0.704 | 256288.2094 | 256288.2094 | 19.6299 | 0.7516 | 0.85859 | 0.64532 | 18.9846
2006-01-27 | 10079.76 | 0.704 | 253332.5921 | 253332.5921 | 19.4035 | 0.74293 | 0.85859 | 0.63787 | 18.7656
2006-01-28 | 10209.6 | 0.704 | 256595.8349 | 256595.8349 | 19.6534 | 0.7525 | 0.85859 | 0.64609 | 19.0074
2006-01-29 | 10132.56 | 0.704 | 254659.604 | 254659.604 | 19.5051 | 0.74682 | 0.85859 | 0.64121 | 18.8639
2006-01-30 | 9670.56 | 0.704 | 243048.2504 | 243048.2504 | 18.6158 | 0.71277 | 0.85859 | 0.61198 | 18.0038
2006-01-31 | 9978 | 0.704 | 250775.0784 | 250775.0784 | 19.2076 | 0.73543 | 0.85859 | 0.63143 | 18.5762
2006-02-01 | 10011.6 | 0.73645 | 263217.6287 | 263217.6287 | 20.1606 | 0.73791 | 0.85859 | 0.63356 | 19.5271
2006-02-02 | 5770.08 | 0.73645 | 151702.7024 | 151702.7024 | 11.6194 | 0.42528 | 0.85859 | 0.36515 | 11.2542
2006-02-03 | 1.2 | 0.73645 | 31.5495 | 31.5495 | 0.0024165 | 8.8446e-05 | 0.85859 | 7.5939e-05 | 0.0023405
2006-02-04 | 4604.16 | 0.73645 | 121049.1907 | 121049.1907 | 9.2715 | 0.33935 | 0.85859 | 0.29136 | 8.9802
2006-02-05 | 8363.04 | 0.73645 | 219874.9008 | 219874.9008 | 16.8409 | 0.6164 | 0.85859 | 0.52923 | 16.3116
2006-02-06 | 8968.32 | 0.73645 | 235788.4777 | 235788.4777 | 18.0597 | 0.66101 | 0.85859 | 0.56754 | 17.4922
2006-02-07 | 9429.12 | 0.73645 | 247903.4926 | 247903.4926 | 18.9877 | 0.69497 | 0.85859 | 0.5967 | 18.391
2006-02-08 | 9549.6 | 0.73645 | 251071.0642 | 251071.0642 | 19.2303 | 0.70385 | 0.85859 | 0.60432 | 18.626
2006-02-09 | 9483.6 | 0.73645 | 249335.8408 | 249335.8408 | 19.0974 | 0.69899 | 0.85859 | 0.60015 | 18.4972
2006-02-10 | 9614.4 | 0.73645 | 252774.7382 | 252774.7382 | 19.3608 | 0.70863 | 0.85859 | 0.60842 | 18.7524
2006-02-11 | 9647.04 | 0.73645 | 253632.8851 | 253632.8851 | 19.4265 | 0.71104 | 0.85859 | 0.61049 | 18.816
2006-02-12 | 9576.24 | 0.73645 | 251771.4635 | 251771.4635 | 19.2839 | 0.70582 | 0.85859 | 0.60601 | 18.6779
2006-02-13 | 9228.24 | 0.73645 | 242622.1033 | 242622.1033 | 18.5832 | 0.68017 | 0.85859 | 0.58399 | 17.9992
2006-02-14 | 8781.12 | 0.73645 | 230866.7529 | 230866.7529 | 17.6828 | 0.64721 | 0.85859 | 0.55569 | 17.1271
2006-02-15 | 9146.64 | 0.73645 | 240476.7361 | 240476.7361 | 18.4188 | 0.67415 | 0.85859 | 0.57882 | 17.84
2006-02-16 | 9358.56 | 0.73645 | 246048.381 | 246048.381 | 18.8456 | 0.68977 | 0.85859 | 0.59223 | 18.2533
2006-02-17 | 9610.8 | 0.73645 | 252680.0897 | 252680.0897 | 19.3535 | 0.70837 | 0.85859 | 0.6082 | 18.7453
2006-02-18 | 9480.24 | 0.73645 | 249247.5021 | 249247.5021 | 19.0906 | 0.69874 | 0.85859 | 0.59993 | 18.4907
2006-02-19 | 9575.52 | 0.73645 | 251752.5338 | 251752.5338 | 19.2825 | 0.70577 | 0.85859 | 0.60596 | 18.6765
2006-02-20 | 9585.6 | 0.73645 | 252017.5498 | 252017.5498 | 19.3028 | 0.70651 | 0.85859 | 0.6066 | 18.6962
2006-02-21 | 9645.12 | 0.73645 | 253582.4059 | 253582.4059 | 19.4226 | 0.7109 | 0.85859 | 0.61037 | 18.8123
2006-02-22 | 0 | 0.73645 | 0 | 0 | 0 | 0 | 0.85859 | 0 | 0
2006-02-23 | 9350.64 | 0.73645 | 245840.1542 | 245840.1542 | 18.8296 | 0.68919 | 0.85859 | 0.59173 | 18.2379
2006-02-24 | 9051.36 | 0.73645 | 237971.7044 | 237971.7044 | 18.227 | 0.66713 | 0.85859 | 0.57279 | 17.6542
2006-02-25 | 7262.88 | 0.73645 | 190950.3027 | 190950.3027 | 14.6255 | 0.53531 | 0.85859 | 0.45961 | 14.1658
2006-02-26 | 8694.96 | 0.73645 | 228601.4975 | 228601.4975 | 17.5093 | 0.64086 | 0.85859 | 0.55024 | 16.959
2006-02-27 | 9470.64 | 0.73645 | 248995.106 | 248995.106 | 19.0713 | 0.69804 | 0.85859 | 0.59933 | 18.472
2006-02-28 | 9623.28 | 0.73645 | 253008.2046 | 253008.2046 | 19.3787 | 0.70929 | 0.85859 | 0.60899 | 18.7697
2006-03-01 | 9560.4 | 0.6955 | 237378.5177 | 237378.5177 | 18.1815 | 0.70465 | 0.85859 | 0.60501 | 17.5765
2006-03-02 | 9702 | 0.6955 | 240894.3537 | 240894.3537 | 18.4508 | 0.71509 | 0.85859 | 0.61397 | 17.8369
2006-03-03 | 9736.08 | 0.6955 | 241740.5379 | 241740.5379 | 18.5156 | 0.7176 | 0.85859 | 0.61612 | 17.8995
2006-03-04 | 9636.48 | 0.6955 | 239267.5347 | 239267.5347 | 18.3262 | 0.71026 | 0.85859 | 0.60982 | 17.7164
2006-03-05 | 9765.36 | 0.6955 | 242467.5413 | 242467.5413 | 18.5713 | 0.71976 | 0.85859 | 0.61798 | 17.9533
2006-03-06 | 9769.44 | 0.6955 | 242568.8451 | 242568.8451 | 18.5791 | 0.72006 | 0.85859 | 0.61824 | 17.9608
2006-03-07 | 9614.16 | 0.6955 | 238713.3436 | 238713.3436 | 18.2838 | 0.70861 | 0.85859 | 0.60841 | 17.6754
2006-03-08 | 9655.68 | 0.6955 | 239744.2582 | 239744.2582 | 18.3627 | 0.71167 | 0.85859 | 0.61104 | 17.7517
2006-03-09 | 9002.16 | 0.6955 | 223517.7814 | 223517.7814 | 17.1199 | 0.66351 | 0.85859 | 0.56968 | 16.5502
2006-03-10 | 9252.72 | 0.6955 | 229739.0233 | 229739.0233 | 17.5964 | 0.68197 | 0.85859 | 0.58554 | 17.0109
2006-03-11 | 9567.6 | 0.6955 | 237557.2891 | 237557.2891 | 18.1952 | 0.70518 | 0.85859 | 0.60546 | 17.5898
2006-03-12 | 9819.84 | 0.6955 | 243820.2443 | 243820.2443 | 18.6749 | 0.72377 | 0.85859 | 0.62142 | 18.0535
2006-03-13 | 9524.64 | 0.6955 | 236490.6202 | 236490.6202 | 18.1135 | 0.70202 | 0.85859 | 0.60274 | 17.5108
2006-03-14 | 9256.56 | 0.6955 | 229834.368 | 229834.368 | 17.6037 | 0.68226 | 0.85859 | 0.58578 | 17.0179
2006-03-15 | 8655.6 | 0.6955 | 214912.9219 | 214912.9219 | 16.4608 | 0.63796 | 0.85859 | 0.54775 | 15.9131
2006-03-16 | 9721.92 | 0.6955 | 241388.9544 | 241388.9544 | 18.4887 | 0.71656 | 0.85859 | 0.61523 | 17.8735
2006-03-17 | 9367.92 | 0.6955 | 232599.3645 | 232599.3645 | 17.8155 | 0.69046 | 0.85859 | 0.59283 | 17.2227
2006-03-18 | 9632.16 | 0.6955 | 239160.2719 | 239160.2719 | 18.318 | 0.70994 | 0.85859 | 0.60955 | 17.7085
2006-03-19 | 9168.96 | 0.6955 | 227659.317 | 227659.317 | 17.4371 | 0.6758 | 0.85859 | 0.58024 | 16.8569
2006-03-20 | 9526.56 | 0.6955 | 236538.2925 | 236538.2925 | 18.1172 | 0.70216 | 0.85859 | 0.60287 | 17.5143
2006-03-21 | 7969.68 | 0.6955 | 197881.9741 | 197881.9741 | 15.1564 | 0.58741 | 0.85859 | 0.50434 | 14.652
2006-03-22 | 9617.52 | 0.6955 | 238796.7702 | 238796.7702 | 18.2902 | 0.70886 | 0.85859 | 0.60862 | 17.6815
2006-03-23 | 8851.68 | 0.6955 | 219781.4608 | 219781.4608 | 16.8337 | 0.65241 | 0.85859 | 0.56016 | 16.2736
2006-03-24 | 9217.2 | 0.6955 | 228857.0848 | 228857.0848 | 17.5289 | 0.67936 | 0.85859 | 0.58329 | 16.9456
2006-03-25 | 9425.52 | 0.6955 | 234029.535 | 234029.535 | 17.925 | 0.69471 | 0.85859 | 0.59647 | 17.3286
2006-03-26 | 9384.96 | 0.6955 | 233022.4566 | 233022.4566 | 17.8479 | 0.69172 | 0.85859 | 0.5939 | 17.254
2006-03-27 | 9407.52 | 0.6955 | 233582.6067 | 233582.6067 | 17.8908 | 0.69338 | 0.85859 | 0.59533 | 17.2955
2006-03-28 | 9114.96 | 0.6955 | 226318.5321 | 226318.5321 | 17.3344 | 0.67182 | 0.85859 | 0.57682 | 16.7576
2006-03-29 | 5393.28 | 0.6955 | 133911.6368 | 133911.6368 | 10.2567 | 0.39751 | 0.85859 | 0.3413 | 9.9154
2006-03-30 | 6438.48 | 0.6955 | 159863.2734 | 159863.2734 | 12.2444 | 0.47455 | 0.85859 | 0.40744 | 11.837
2006-03-31 | 192.24 | 0.6955 | 4773.1942 | 4773.1942 | 0.36559 | 0.014169 | 0.85859 | 0.012165 | 0.35343
2006-04-01 | 0 | 0.69264 | 0 | 0 | 0 | 0 | 0.87868 | 0 | 0
2006-04-02 | 6605.76 | 0.69264 | 163342.2657 | 163342.2657 | 12.5109 | 0.48688 | 0.87868 | 0.42781 | 12.0831
2006-04-03 | 766.08 | 0.69264 | 18943.0501 | 18943.0501 | 1.4509 | 0.056464 | 0.87868 | 0.049614 | 1.4013
2006-04-04 | 6518.4 | 0.69264 | 161182.0934 | 161182.0934 | 12.3454 | 0.48044 | 0.87868 | 0.42215 | 11.9233
2006-04-05 | 9138 | 0.69264 | 225957.5922 | 225957.5922 | 17.3068 | 0.67352 | 0.87868 | 0.59181 | 16.715
2006-04-06 | 0 | 0.69264 | 0 | 0 | 0 | 0 | 0.87868 | 0 | 0
2006-04-07 | 9052.56 | 0.69264 | 223844.8962 | 223844.8962 | 17.145 | 0.66722 | 0.87868 | 0.58628 | 16.5587
2006-04-08 | 8292.24 | 0.69264 | 205044.275 | 205044.275 | 15.705 | 0.61118 | 0.87868 | 0.53703 | 15.1679
2006-04-09 | 7556.64 | 0.69264 | 186854.9113 | 186854.9113 | 14.3118 | 0.55696 | 0.87868 | 0.48939 | 13.8224
2006-04-10 | 7472.16 | 0.69264 | 184765.9534 | 184765.9534 | 14.1518 | 0.55074 | 0.87868 | 0.48392 | 13.6679
2006-04-11 | 7596.48 | 0.69264 | 187840.0449 | 187840.0449 | 14.3872 | 0.5599 | 0.87868 | 0.49197 | 13.8953
2006-04-12 | 8839.68 | 0.69264 | 218580.9596 | 218580.9596 | 16.7418 | 0.65153 | 0.87868 | 0.57249 | 16.1693
2006-04-13 | 9266.88 | 0.69264 | 229144.4399 | 229144.4399 | 17.5509 | 0.68302 | 0.87868 | 0.60016 | 16.9507
2006-04-14 | 9270.72 | 0.69264 | 229239.3926 | 229239.3926 | 17.5581 | 0.6833 | 0.87868 | 0.6004 | 16.9577
2006-04-15 | 9460.08 | 0.69264 | 233921.7443 | 233921.7443 | 17.9168 | 0.69726 | 0.87868 | 0.61267 | 17.3041
2006-04-16 | 9598.8 | 0.69264 | 237351.9081 | 237351.9081 | 18.1795 | 0.70748 | 0.87868 | 0.62165 | 17.5578
2006-04-17 | 9373.44 | 0.69264 | 231779.3755 | 231779.3755 | 17.7527 | 0.69087 | 0.87868 | 0.60706 | 17.1456
2006-04-18 | 9047.28 | 0.69264 | 223714.3363 | 223714.3363 | 17.135 | 0.66683 | 0.87868 | 0.58593 | 16.549
2006-04-19 | 9443.76 | 0.69264 | 233518.1956 | 233518.1956 | 17.8859 | 0.69605 | 0.87868 | 0.61161 | 17.2742
2006-04-20 | 8285.76 | 0.69264 | 204884.0424 | 204884.0424 | 15.6927 | 0.6107 | 0.87868 | 0.53661 | 15.1561
2006-04-21 | 9368.16 | 0.69264 | 231648.8156 | 231648.8156 | 17.7427 | 0.69048 | 0.87868 | 0.60671 | 17.136
2006-04-22 | 9061.68 | 0.69264 | 224070.4087 | 224070.4087 | 17.1622 | 0.66789 | 0.87868 | 0.58687 | 16.5754
2006-04-23 | 9225.36 | 0.69264 | 228117.7646 | 228117.7646 | 17.4722 | 0.67996 | 0.87868 | 0.59747 | 16.8748
2006-04-24 | 9319.44 | 0.69264 | 230444.1041 | 230444.1041 | 17.6504 | 0.68689 | 0.87868 | 0.60356 | 17.0468
2006-04-25 | 9335.04 | 0.69264 | 230829.8492 | 230829.8492 | 17.68 | 0.68804 | 0.87868 | 0.60457 | 17.0754
2006-04-26 | 8564.16 | 0.69264 | 211768.1082 | 211768.1082 | 16.22 | 0.63122 | 0.87868 | 0.55464 | 15.6653
2006-04-27 | 9535.68 | 0.69264 | 235791.1242 | 235791.1242 | 18.0599 | 0.70283 | 0.87868 | 0.61756 | 17.4424
2006-04-28 | 9385.2 | 0.69264 | 232070.1679 | 232070.1679 | 17.775 | 0.69174 | 0.87868 | 0.60782 | 17.1671
2006-04-29 | 9373.92 | 0.69264 | 231791.2446 | 231791.2446 | 17.7536 | 0.69091 | 0.87868 | 0.60709 | 17.1465
2006-04-30 | 9524.64 | 0.69264 | 235518.1354 | 235518.1354 | 18.039 | 0.70202 | 0.87868 | 0.61685 | 17.4222
2006-05-01 | 9508.56 | 0.7179 | 243695.1695 | 243695.1695 | 18.6653 | 0.70083 | 0.87868 | 0.61581 | 18.0495
2006-05-02 | 9267.84 | 0.7179 | 237525.7494 | 237525.7494 | 18.1928 | 0.68309 | 0.87868 | 0.60022 | 17.5926
2006-05-03 | 7630.08 | 0.7179 | 195551.5492 | 195551.5492 | 14.9779 | 0.56238 | 0.87868 | 0.49415 | 14.4837
2006-05-04 | 5546.16 | 0.7179 | 142142.701 | 142142.701 | 10.8871 | 0.40878 | 0.87868 | 0.35919 | 10.5279
2006-05-05 | 5960.88 | 0.7179 | 152771.5723 | 152771.5723 | 11.7012 | 0.43935 | 0.87868 | 0.38605 | 11.3152
2006-05-06 | 7584 | 0.7179 | 194370.5635 | 194370.5635 | 14.8874 | 0.55898 | 0.87868 | 0.49117 | 14.3963
2006-05-07 | 7214.4 | 0.7179 | 184898.074 | 184898.074 | 14.1619 | 0.53174 | 0.87868 | 0.46723 | 13.6947
2006-05-08 | 6958.56 | 0.7179 | 178341.143 | 178341.143 | 13.6597 | 0.51288 | 0.87868 | 0.45066 | 13.209
2006-05-09 | 8945.76 | 0.7179 | 229271.1514 | 229271.1514 | 17.5606 | 0.65935 | 0.87868 | 0.57936 | 16.9812
2006-05-10 | 9000.96 | 0.7179 | 230685.8739 | 230685.8739 | 17.6689 | 0.66342 | 0.87868 | 0.58293 | 17.086
2006-05-11 | 9238.56 | 0.7179 | 236775.3314 | 236775.3314 | 18.1353 | 0.68093 | 0.87868 | 0.59832 | 17.537
2006-05-12 | 9524.88 | 0.7179 | 244113.4353 | 244113.4353 | 18.6974 | 0.70203 | 0.87868 | 0.61686 | 18.0805
2006-05-13 | 9374.4 | 0.7179 | 240256.7788 | 240256.7788 | 18.402 | 0.69094 | 0.87868 | 0.60712 | 17.7949
2006-05-14 | 8015.28 | 0.7179 | 205423.8516 | 205423.8516 | 15.734 | 0.59077 | 0.87868 | 0.5191 | 15.2149
2006-05-15 | 7762.8 | 0.7179 | 198953.0341 | 198953.0341 | 15.2384 | 0.57216 | 0.87868 | 0.50275 | 14.7357
2006-05-16 | 7696.08 | 0.7179 | 197243.0652 | 197243.0652 | 15.1074 | 0.56724 | 0.87868 | 0.49842 | 14.609
2006-05-17 | 7974.24 | 0.7179 | 204372.0362 | 204372.0362 | 15.6535 | 0.58774 | 0.87868 | 0.51644 | 15.137
2006-05-18 | 8424.48 | 0.7179 | 215911.2507 | 215911.2507 | 16.5373 | 0.62093 | 0.87868 | 0.5456 | 15.9917
2006-05-19 | 7857.36 | 0.7179 | 201376.5152 | 201376.5152 | 15.424 | 0.57913 | 0.87868 | 0.50887 | 14.9152
2006-05-20 | 8431.68 | 0.7179 | 216095.7797 | 216095.7797 | 16.5514 | 0.62146 | 0.87868 | 0.54606 | 16.0054
2006-05-21 | 8240.16 | 0.7179 | 211187.3078 | 211187.3078 | 16.1755 | 0.60734 | 0.87868 | 0.53366 | 15.6418
2006-05-22 | 7645.44 | 0.7179 | 195945.2111 | 195945.2111 | 15.008 | 0.56351 | 0.87868 | 0.49515 | 14.5129
2006-05-23 | 8358.72 | 0.7179 | 214225.8856 | 214225.8856 | 16.4082 | 0.61608 | 0.87868 | 0.54134 | 15.8669
2006-05-24 | 8292.72 | 0.7179 | 212534.3697 | 212534.3697 | 16.2786 | 0.61122 | 0.87868 | 0.53707 | 15.7416
2006-05-25 | 7310.88 | 0.7179 | 187370.7628 | 187370.7628 | 14.3513 | 0.53885 | 0.87868 | 0.47348 | 13.8778
2006-05-26 | 6804.72 | 0.7179 | 174398.373 | 174398.373 | 13.3577 | 0.50154 | 0.87868 | 0.4407 | 12.917
2006-05-27 | 6419.28 | 0.7179 | 164519.9197 | 164519.9197 | 12.6011 | 0.47313 | 0.87868 | 0.41573 | 12.1853
2006-05-28 | 6502.8 | 0.7179 | 166660.4563 | 166660.4563 | 12.765 | 0.47929 | 0.87868 | 0.42114 | 12.3439
2006-05-29 | 3813.36 | 0.7179 | 97732.7178 | 97732.7178 | 7.4856 | 0.28106 | 0.87868 | 0.24697 | 7.2387
2006-05-30 | 7871.28 | 0.7179 | 201733.2713 | 201733.2713 | 15.4514 | 0.58015 | 0.87868 | 0.50977 | 14.9416
2006-05-31 | 7168.08 | 0.7179 | 183710.9374 | 183710.9374 | 14.071 | 0.52832 | 0.87868 | 0.46423 | 13.6067
2006-06-01 | 6738.24 | 0.72075 | 173380.1373 | 173380.1373 | 13.2797 | 0.49664 | 0.87868 | 0.43639 | 12.8433
2006-06-02 | 7342.32 | 0.72075 | 188923.5839 | 188923.5839 | 14.4702 | 0.54117 | 0.87868 | 0.47551 | 13.9947
2006-06-03 | 8182.56 | 0.72075 | 210543.6103 | 210543.6103 | 16.1262 | 0.6031 | 0.87868 | 0.52993 | 15.5962
2006-06-04 | 7334.4 | 0.72075 | 188719.7962 | 188719.7962 | 14.4546 | 0.54058 | 0.87868 | 0.475 | 13.9796
2006-06-05 | 7687.44 | 0.72075 | 197803.789 | 197803.789 | 15.1504 | 0.5666 | 0.87868 | 0.49787 | 14.6525
2006-06-06 | 7829.76 | 0.72075 | 201465.7929 | 201465.7929 | 15.4309 | 0.57709 | 0.87868 | 0.50708 | 14.9238
2006-06-07 | 9011.52 | 0.72075 | 231873.3935 | 231873.3935 | 17.7599 | 0.6642 | 0.87868 | 0.58362 | 17.1763
2006-06-08 | 7743.6 | 0.72075 | 199248.8293 | 199248.8293 | 15.2611 | 0.57074 | 0.87868 | 0.5015 | 14.7596
2006-06-09 | 7328.88 | 0.72075 | 188577.7623 | 188577.7623 | 14.4437 | 0.54018 | 0.87868 | 0.47464 | 13.9691
2006-06-10 | 8077.68 | 0.72075 | 207844.9666 | 207844.9666 | 15.9195 | 0.59537 | 0.87868 | 0.52314 | 15.3963
2006-06-11 | 7829.28 | 0.72075 | 201453.4421 | 201453.4421 | 15.4299 | 0.57706 | 0.87868 | 0.50705 | 14.9229
2006-06-12 | 7240.56 | 0.72075 | 186305.2202 | 186305.2202 | 14.2697 | 0.53367 | 0.87868 | 0.46892 | 13.8008
2006-06-13 | 3982.56 | 0.72075 | 102474.3553 | 102474.3553 | 7.8488 | 0.29354 | 0.87868 | 0.25792 | 7.5909
2006-06-14 | 0 |  | 0 | 0 | 0 | 0 | 0.87868 | 0 | 0
2006-06-15 | 0 |  | 0 | 0 | 0 | 0 | 0.87868 | 0 | 0
2006-06-16 | 0 |  | 0 | 0 | 0 | 0 | 0.87868 | 0 | 0
2006-06-17 | 0 |  | 0 | 0 | 0 | 0 | 0.87868 | 0 | 0
2006-06-18 | 0 |  | 0 | 0 | 0 | 0 | 0.87868 | 0 | 0
2006-06-19 | 0 |  | 0 | 0 | 0 | 0 | 0.87868 | 0 | 0
2006-06-20 | 6361.2 | 0.72075 | 163678.6059 | 163678.6059 | 12.5366 | 0.46885 | 0.87868 | 0.41197 | 12.1247
2006-06-21 | 7472.88 | 0.72075 | 192282.9939 | 192282.9939 | 14.7275 | 0.55079 | 0.87868 | 0.48397 | 14.2436
2006-06-22 | 7230.72 | 0.72075 | 186052.0294 | 186052.0294 | 14.2503 | 0.53294 | 0.87868 | 0.46829 | 13.782
2006-06-23 | 7941.6 | 0.72075 | 204343.5227 | 204343.5227 | 15.6513 | 0.58534 | 0.87868 | 0.51433 | 15.137
2006-06-24 | 7197.84 | 0.72075 | 185206.0015 | 185206.0015 | 14.1855 | 0.53052 | 0.87868 | 0.46616 | 13.7193
2006-06-25 | 7100.4 | 0.72075 | 182698.7948 | 182698.7948 | 13.9934 | 0.52334 | 0.87868 | 0.45985 | 13.5336
2006-06-26 | 7944.72 | 0.72075 | 204423.8028 | 204423.8028 | 15.6574 | 0.58557 | 0.87868 | 0.51453 | 15.1429
2006-06-27 | 8693.04 | 0.72075 | 223678.6563 | 223678.6563 | 17.1322 | 0.64072 | 0.87868 | 0.56299 | 16.5692
2006-06-28 | 7620.72 | 0.72075 | 196087.0317 | 196087.0317 | 15.0189 | 0.56169 | 0.87868 | 0.49354 | 14.5253
2006-06-29 | 6325.44 | 0.72075 | 162758.4734 | 162758.4734 | 12.4662 | 0.46622 | 0.87868 | 0.40966 | 12.0565
2006-06-30 | 6156.96 | 0.72075 | 158423.3524 | 158423.3524 | 12.1341 | 0.4538 | 0.87868 | 0.39875 | 11.7354
2006-07-01 | 6417.12 | 0.72245 | 165506.9259 | 165506.9259 | 12.6767 | 0.47297 | 0.87868 | 0.41559 | 12.2611
2006-07-02 | 7821.84 | 0.72245 | 201736.7126 | 201736.7126 | 15.4516 | 0.57651 | 0.87868 | 0.50657 | 14.9451
2006-07-03 | 6034.8 | 0.72245 | 155646.333 | 155646.333 | 11.9214 | 0.4448 | 0.87868 | 0.39083 | 11.5306
2006-07-04 | 6154.32 | 0.72245 | 158728.9289 | 158728.9289 | 12.1575 | 0.45361 | 0.87868 | 0.39858 | 11.7589
2006-07-05 | 5861.52 | 0.72245 | 151177.1879 | 151177.1879 | 11.5791 | 0.43202 | 0.87868 | 0.37961 | 11.1995
2006-07-06 | 5875.2 | 0.72245 | 151530.0152 | 151530.0152 | 11.6061 | 0.43303 | 0.87868 | 0.3805 | 11.2256
2006-07-07 | 6355.44 | 0.72245 | 163916.1083 | 163916.1083 | 12.5548 | 0.46843 | 0.87868 | 0.4116 | 12.1432
2006-07-08 | 6638.16 | 0.72245 | 171207.8713 | 171207.8713 | 13.1133 | 0.48927 | 0.87868 | 0.42991 | 12.6834
2006-07-09 | 7394.4 | 0.72245 | 190712.4088 | 190712.4088 | 14.6072 | 0.54501 | 0.87868 | 0.47889 | 14.1283
2006-07-10 | 7500.48 | 0.72245 | 193448.3674 | 193448.3674 | 14.8168 | 0.55282 | 0.87868 | 0.48576 | 14.331
2006-07-11 | 7157.28 | 0.72245 | 184596.7366 | 184596.7366 | 14.1388 | 0.52753 | 0.87868 | 0.46353 | 13.6753
2006-07-12 | 7165.68 | 0.72245 | 184813.3849 | 184813.3849 | 14.1554 | 0.52815 | 0.87868 | 0.46407 | 13.6913
2006-07-13 | 7511.76 | 0.72245 | 193739.2951 | 193739.2951 | 14.8391 | 0.55366 | 0.87868 | 0.48649 | 14.3526
2006-07-14 | 7185.84 | 0.72245 | 185333.3409 | 185333.3409 | 14.1952 | 0.52963 | 0.87868 | 0.46538 | 13.7299
2006-07-15 | 6083.04 | 0.72245 | 156890.5133 | 156890.5133 | 12.0167 | 0.44835 | 0.87868 | 0.39396 | 11.6228
2006-07-16 | 6718.32 | 0.72245 | 173275.3151 | 173275.3151 | 13.2717 | 0.49517 | 0.87868 | 0.4351 | 12.8366
2006-07-17 | 7120.32 | 0.72245 | 183643.4841 | 183643.4841 | 14.0658 | 0.5248 | 0.87868 | 0.46114 | 13.6047
2006-07-18 | 7652.4 | 0.72245 | 197366.6068 | 197366.6068 | 15.1169 | 0.56402 | 0.87868 | 0.4956 | 14.6213
2006-07-19 | 8028.48 | 0.72245 | 207066.2609 | 207066.2609 | 15.8598 | 0.59174 | 0.87868 | 0.51995 | 15.3399
2006-07-20 | 8529.36 | 0.72245 | 219984.6899 | 219984.6899 | 16.8493 | 0.62866 | 0.87868 | 0.55239 | 16.2969
2006-07-21 | 7112.16 | 0.72245 | 183433.0257 | 183433.0257 | 14.0497 | 0.5242 | 0.87868 | 0.46061 | 13.5891
2006-07-22 | 8122.32 | 0.72245 | 209486.532 | 209486.532 | 16.0452 | 0.59866 | 0.87868 | 0.52603 | 15.5192
2006-07-23 | 8223.6 | 0.72245 | 212098.6916 | 212098.6916 | 16.2453 | 0.60612 | 0.87868 | 0.53259 | 15.7127
2006-07-24 | 8865.12 | 0.72245 | 228644.4322 | 228644.4322 | 17.5126 | 0.65341 | 0.87868 | 0.57414 | 16.9384
2006-07-25 | 8728.32 | 0.72245 | 225116.1598 | 225116.1598 | 17.2423 | 0.64332 | 0.87868 | 0.56528 | 16.677
2006-07-26 | 8184.48 | 0.72245 | 211089.7295 | 211089.7295 | 16.168 | 0.60324 | 0.87868 | 0.53006 | 15.6379
2006-07-27 | 7814.88 | 0.72245 | 201557.204 | 201557.204 | 15.4379 | 0.576 | 0.87868 | 0.50612 | 14.9318
2006-07-28 | 8077.92 | 0.72245 | 208341.391 | 208341.391 | 15.9575 | 0.59538 | 0.87868 | 0.52315 | 15.4343
2006-07-29 | 7739.04 | 0.72245 | 199601.1793 | 199601.1793 | 15.2881 | 0.57041 | 0.87868 | 0.50121 | 14.7868
2006-07-30 | 7899.84 | 0.72245 | 203748.4469 | 203748.4469 | 15.6057 | 0.58226 | 0.87868 | 0.51162 | 15.0941
2006-07-31 | 8294.88 | 0.72245 | 213937.1072 | 213937.1072 | 16.3861 | 0.61138 | 0.87868 | 0.53721 | 15.8489
2006-08-01 | 7493.52 | 0.7229 | 193389.2422 | 193389.2422 | 14.8123 | 0.55231 | 0.87868 | 0.48531 | 14.327
2006-08-02 | 7648.32 | 0.7229 | 197384.2478 | 197384.2478 | 15.1183 | 0.56372 | 0.87868 | 0.49533 | 14.6229
2006-08-03 | 8673.36 | 0.7229 | 223837.9984 | 223837.9984 | 17.1444 | 0.63927 | 0.87868 | 0.56172 | 16.5827
2006-08-04 | 9178.56 | 0.7229 | 236875.9626 | 236875.9626 | 18.143 | 0.67651 | 0.87868 | 0.59444 | 17.5486
2006-08-05 | 9128.88 | 0.7229 | 235593.8445 | 235593.8445 | 18.0448 | 0.67285 | 0.87868 | 0.59122 | 17.4536
2006-08-06 | 8270.64 | 0.7229 | 213444.7899 | 213444.7899 | 16.3484 | 0.60959 | 0.87868 | 0.53564 | 15.8127
2006-08-07 | 7714.32 | 0.7229 | 199087.5448 | 199087.5448 | 15.2487 | 0.56859 | 0.87868 | 0.49961 | 14.7491
2006-08-08 | 7560 | 0.7229 | 195104.9268 | 195104.9268 | 14.9437 | 0.55721 | 0.87868 | 0.48961 | 14.4541
2006-08-09 | 7789.2 | 0.7229 | 201020.0127 | 201020.0127 | 15.3967 | 0.5741 | 0.87868 | 0.50446 | 14.8923
2006-08-10 | 8670.96 | 0.7229 | 223776.0603 | 223776.0603 | 17.1397 | 0.63909 | 0.87868 | 0.56156 | 16.5781
2006-08-11 | 8630.4 | 0.7229 | 222729.3069 | 222729.3069 | 17.0595 | 0.63611 | 0.87868 | 0.55893 | 16.5006
2006-08-12 | 8675.76 | 0.7229 | 223899.9365 | 223899.9365 | 17.1492 | 0.63945 | 0.87868 | 0.56187 | 16.5873
2006-08-13 | 8821.2 | 0.7229 | 227653.3836 | 227653.3836 | 17.4367 | 0.65017 | 0.87868 | 0.57129 | 16.8654
2006-08-14 | 8605.68 | 0.7229 | 222091.3448 | 222091.3448 | 17.0106 | 0.63428 | 0.87868 | 0.55733 | 16.4533
2006-08-15 | 8781.12 | 0.7229 | 226619.0178 | 226619.0178 | 17.3574 | 0.64721 | 0.87868 | 0.5687 | 16.7887
2006-08-16 | 8671.44 | 0.7229 | 223788.4479 | 223788.4479 | 17.1406 | 0.63913 | 0.87868 | 0.56159 | 16.579
2006-08-17 | 8028.24 | 0.7229 | 207189.0446 | 207189.0446 | 15.8692 | 0.59172 | 0.87868 | 0.51994 | 15.3493
2006-08-18 | 7551.84 | 0.7229 | 194894.3374 | 194894.3374 | 14.9275 | 0.55661 | 0.87868 | 0.48908 | 14.4385
2006-08-19 | 8815.68 | 0.7229 | 227510.9261 | 227510.9261 | 17.4257 | 0.64976 | 0.87868 | 0.57093 | 16.8548
2006-08-20 | 8431.92 | 0.7229 | 217607.0284 | 217607.0284 | 16.6672 | 0.62148 | 0.87868 | 0.54608 | 16.1211
2006-08-21 | 8941.92 | 0.7229 | 230768.8687 | 230768.8687 | 17.6753 | 0.65907 | 0.87868 | 0.57911 | 17.0962
2006-08-22 | 8809.68 | 0.7229 | 227356.0809 | 227356.0809 | 17.4139 | 0.64932 | 0.87868 | 0.57055 | 16.8433
2006-08-23 | 9222.48 | 0.7229 | 238009.4293 | 238009.4293 | 18.2299 | 0.67974 | 0.87868 | 0.59728 | 17.6326
2006-08-24 | 9266.4 | 0.7229 | 239142.896 | 239142.896 | 18.3167 | 0.68298 | 0.87868 | 0.60012 | 17.7165
2006-08-25 | 9382.8 | 0.7229 | 242146.8925 | 242146.8925 | 18.5468 | 0.69156 | 0.87868 | 0.60766 | 17.9391
2006-08-26 | 8007.36 | 0.7229 | 206650.1834 | 206650.1834 | 15.828 | 0.59018 | 0.87868 | 0.51858 | 15.3094
2006-08-27 | 8338.56 | 0.7229 | 215197.6374 | 215197.6374 | 16.4826 | 0.6146 | 0.87868 | 0.54003 | 15.9426
2006-08-28 | 8732.4 | 0.7229 | 225361.675 | 225361.675 | 17.2611 | 0.64362 | 0.87868 | 0.56554 | 16.6956
2006-08-29 | 9361.68 | 0.7229 | 241601.8375 | 241601.8375 | 18.505 | 0.69 | 0.87868 | 0.60629 | 17.8987
2006-08-30 | 9234.72 | 0.7229 | 238325.3134 | 238325.3134 | 18.2541 | 0.68065 | 0.87868 | 0.59807 | 17.656
2006-08-31 | 6032.64 | 0.7229 | 155687.5378 | 155687.5378 | 11.9246 | 0.44464 | 0.87868 | 0.39069 | 11.5339
2006-09-01 | 8257.92 | 0.68305 | 201368.4295 | 201368.4295 | 15.4234 | 0.60865 | 0.87868 | 0.53481 | 14.8886
2006-09-02 | 9465.36 | 0.68305 | 230811.7151 | 230811.7151 | 17.6786 | 0.69765 | 0.87868 | 0.61301 | 17.0656
2006-09-03 | 9367.2 | 0.68305 | 228418.0948 | 228418.0948 | 17.4952 | 0.69041 | 0.87868 | 0.60665 | 16.8886
2006-09-04 | 9550.8 | 0.68305 | 232895.1597 | 232895.1597 | 17.8381 | 0.70394 | 0.87868 | 0.61854 | 17.2196
2006-09-05 | 9407.04 | 0.68305 | 229389.5886 | 229389.5886 | 17.5696 | 0.69335 | 0.87868 | 0.60923 | 16.9604
2006-09-06 | 5845.2 | 0.68305 | 142534.5298 | 142534.5298 | 10.9171 | 0.43082 | 0.87868 | 0.37856 | 10.5386
2006-09-07 | 8095.92 | 0.68305 | 197418.0782 | 197418.0782 | 15.1208 | 0.59671 | 0.87868 | 0.52432 | 14.5965
2006-09-08 | 9251.28 | 0.68305 | 225591.3989 | 225591.3989 | 17.2787 | 0.68187 | 0.87868 | 0.59915 | 16.6796
2006-09-09 | 9552.96 | 0.68305 | 232947.831 | 232947.831 | 17.8422 | 0.7041 | 0.87868 | 0.61868 | 17.2235
2006-09-10 | 8908.08 | 0.68305 | 217222.5064 | 217222.5064 | 16.6377 | 0.65657 | 0.87868 | 0.57692 | 16.0608
2006-09-11 | 8512.08 | 0.68305 | 207566.0919 | 207566.0919 | 15.8981 | 0.62738 | 0.87868 | 0.55127 | 15.3468
2006-09-12 | 8829.6 | 0.68305 | 215308.7806 | 215308.7806 | 16.4911 | 0.65079 | 0.87868 | 0.57184 | 15.9193
2006-09-13 | 8491.92 | 0.68305 | 207074.4926 | 207074.4926 | 15.8605 | 0.6259 | 0.87868 | 0.54997 | 15.3105
2006-09-14 | 6862.8 | 0.68305 | 167348.5888 | 167348.5888 | 12.8177 | 0.50582 | 0.87868 | 0.44446 | 12.3733
2006-09-15 | 9051.12 | 0.68305 | 220710.5203 | 220710.5203 | 16.9049 | 0.66711 | 0.87868 | 0.58618 | 16.3187
2006-09-16 | 9480 | 0.68305 | 231168.7098 | 231168.7098 | 17.7059 | 0.69873 | 0.87868 | 0.61396 | 17.0919
2006-09-17 | 9446.16 | 0.68305 | 230343.5253 | 230343.5253 | 17.6427 | 0.69623 | 0.87868 | 0.61177 | 17.0309
2006-09-18 | 9132.48 | 0.68305 | 222694.4746 | 222694.4746 | 17.0568 | 0.67311 | 0 | 0 | 17.0568
2006-09-19 | 9562.8 | 0.68305 | 233187.7783 | 233187.7783 | 17.8606 | 0.70483 | 0.87868 | 0.61932 | 17.2412
2006-09-20 | 9032.4 | 0.68305 | 220254.0353 | 220254.0353 | 16.8699 | 0.66573 | 0.87868 | 0.58497 | 16.2849
2006-09-21 | 8966.16 | 0.68305 | 218638.7805 | 218638.7805 | 16.7462 | 0.66085 | 0.87868 | 0.58068 | 16.1655
| 3033362.16 | 0.70826 | 76637633.5325 | 76637633.5325 | 5869.9063 | 0.61253 | 0.86576 | 193.3383 | 5676.5679