## SUMMARY
MEN-Tangerang 13.6MW Natural Gas Co-generation Project
WORKSHEET SUMMARY
| WORKSHEET NAME | Content Description
| EMISSION | Emission Reduction Calculation
| FINANCE | Financial Analysis of Project
| FSA-0 | Sensitivity Analysis of the Project with exchange rate as defining parameter
| FSA-1 | Sensitivity Analysis of the Project with power revenue as defining parameter
| FSA-2 | Sensitivity Analysis of the Project with steam revenue as defining parameter
| FSA-3 | Sensitivity Analysis of the Project with operating load as defining parameter
| GRID-EF | Summary of 2006 JAMALI Grid Emission Factor Calculation
| RD-2005IPP | Raw Data obtained from PLN P3B for IPP Generation & its associated fuel consumption
| RD-2006ALL | Raw Data obtained from PLN P3B for all power plants from the grid
| RD-2006DataAnalysis | Data analysis from RD-2006ALL
| ESAV | Calculation of energy savings resulting from this Project activity
This spreadsheet corresponds with the following PDD:
ID-MEN-TNG-PDD Version 6.1.3

## EMISSION
General Information |  |  |  |  | Unit | Value
1 | Project Electrical Output (Gross) |  |  |  | MW | 13.61
2 | Project Load |  |  |  |  | 90%
3 | Project Electrical Output (Net) |  |  |  | MW | 11.8815
4 | Steam Flowrate |  |  |  | t/hr | 9.5
5 | Steam Enthalpy |  |  |  | MJ/t | 2767.5
6 | Operational hour |  |  |  | hr/yr | 8000
Year | Column1 | Column2 | Estimation of project activity emissions | Estimation of baseline emissions | Estimation of leakage | Estimation of overall emission reduction
1 |  |  | 46337 | 103787.852 | 14829 | 42621.852
2 |  |  | 46337 | 103787.852 | 14829 | 42621.852
3 |  |  | 46337 | 103787.852 | 14829 | 42621.852
4 |  |  | 46337 | 103787.852 | 14829 | 42621.852
5 |  |  | 46337 | 103787.852 | 14829 | 42621.852
6 |  |  | 46337 | 103787.852 | 14829 | 42621.852
7 |  |  | 46337 | 103787.852 | 14829 | 42621.852
Total |  |  | 324359 | 726514.964 | 103803 | 298352.964
BASELINE EMISSIONS
Emission associated with displacement of residue oil |  |  |  |  | t-CO2/yr | 18146
[5 empty] | Unit | Value
CAHO | Heat generated by the baseline boiler equivalent to the project output |  |  |  | TJ/yr | 210.33
EB | Efficiency of baseline boiler |  |  |  | fraction | 0.9
ABEC | Energy that would have been consumed to generate heat in the baseline |  |  |  | TJ/yr | 233.7
EF_CO2_R | CO2 emission factor of combustion of residue oil |  |  |  | t-CO2/TJ | 77.4
EF_CH4_R | CH4 emission factor of combustion of residue oil |  |  |  | t-CH4/TJ | 0.003
EF_N2O_R | N2O emission factor of combustion of residue oil |  |  |  | t-N2O/TJ | 0.0006
GWP_CO2 | Global warming potential of CO2 |  |  |  | t-CO2/t-CO2 | 1
GWP_CH4 | Global warming potential of CH4 |  |  |  | t-CO2/t-CH4 | 21
GWP_N2O | Global warming potential of N2O |  |  |  | t-CO2/t-N2O | 310
BER | Baseline emission from displacement of residue oil |  |  |  | t-CO2/yr | 18146
Emission associated with displacement of grid electricity |  |  |  |  | t-CO2/yr | 85641.852
[5 empty] | Unit | Value
CEO | Net electricity generation |  |  |  | MWh/yr | 95052
EFY | Grid emission factor |  |  |  | t-CO2/MWh | 0.901
BEELEC | Baseline emission from displacement of grid electricity |  |  |  | t-CO2/yr | 85641.852
PROJECT EMISSIONS
Project emisssions associated with combustion of natural gas |  |  |  |  | t-CO2/yr | 46337
[5 empty] | Unit | Value
VNG | Amt. of natural gas consumed by project |  |  |  | m3/yr | 24560000
D_NG | Density of natural gas |  |  |  | kg/m3 | 0.7
NCVNG | Net calorific value of natural gas |  |  |  | TJ/kg | 4.8e-05
AEC | Annual natural gas consumption in energy unit |  |  |  | TJ/yr | 825.216
EF_CO2_NG | CO2 emission factor of combustion of NG |  |  |  | t-CO2/TJ | 56.1
EF_CH4_NG | CH4 emission factor of combustion of NG |  |  |  | t-CH4/TJ | 0.001
EF_N2O_NG | N2O emission factor of combustion of NG |  |  |  | t-N2O/TJ | 0.0001
GWP_CO2 | Global warming potential of CO2 |  |  |  | t-CO2/t-CO2 | 1
GWP_CH4 | Global warming potential of CH4 |  |  |  | t-CO2/t-CH4 | 21
GWP_N2O | Global warming potential of N2O |  |  |  | t-CO2/t-N2O | 310
PENG | Project emission associated with combustion of natural gas |  |  |  | t-CO2/yr | 46337
LEAKAGE EMISSION
Leakage emissions associated with natural gas production |  |  |  |  | t-CO2/yr | 14829
[5 empty] | Unit | Value
Methane leakage rate |  |  |  |  | Gg-CH4/10^6m3 | 0.028752
| Gas production |  |  |  | Gg-CH4/10^6m3 | 0.024001
| Gas processing (default weighted total) |  |  |  | Gg-CH4/10^6m3 | 0.0003528
| Gas transmission & storage |  |  |  | Gg-CH4/10^6m3 | 0.001898
| Gas distribution |  |  |  | Gg-CH4/10^6m3 | 0.0025
VNG | Amt of natural gas consumed |  |  |  | m3/yr | 24560000
GWP_CH4 | Global warming potential of CH4 |  |  |  | t-CO2/t-CH4 | 21
LE | Leakage emissions associated with natural gas production, etc. |  |  |  | t-CO2/yr | 14829
EMISSION REDUCTION | [5 empty] | 42621.852

## FINANCE
FINANCIAL PARAMETERS | [5 empty] | Summary to sensitivity analysis |  |  | Resulting IRR
Total Project Costs |  |  |  | 12499720 |  | Exchange Rate is improved by 5% |  |  | 15.2%
Project Parameters | [5 empty] | PLN Rate is increased by 5% |  |  | 14.73%
Exchange Rate |  |  | IDR/USD | 9500 |  | Steam rate goes up to Rp65 |  |  | 11.13%
Initial Natural Gas Price |  |  | /MMBTU | 5 |  | Load is increased to 95% |  |  | 15.16%
Natural gas costs |  |  | /TJ | 4743.833 |  | Benchmark
Steam Sales Rates |  |  | /tonnes | 6.3158 |  | SBI |  |  | 12.75%
Electricity Price from PLN |  |  | /kWh | 0.071678 |  | Typical Bank Charges |  |  | 4%
Electricity Price to users |  |  | /kWh | 0.069528 |  | Benchmark Return |  |  | 16.75%
CER Price |  |  |  | 12 |  | Realistic Return |  |  | 19.75%
CASH FLOW ANALYSIS | Capital Expenditure | Sales Revenue |  |  | Overhead |  |  |  | Net Cash Flow | CDM Revenue
Annual Increased Rate |  | 2.5% | 5% |  | 7% | 0% | 0%
Year |  | Steam | Power | Total Sales Revenue | Gas | Other costs | Operating Expense | Total Overhead |  | Emission Reduction | Cash Flow
0 | -12499720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12499720 | 0 | -12499720
1 | 0 | 480000 | 6608750.1196 | 7088750.1196 | -3914686.907 | -1420276.5 | -147100.5 | -5482063.907 | 1606686.2126 | 511462.224 | 2118148.4366
2 | 0 | 492000 | 6939187.6256 | 7431187.6256 | -3914686.907 | -1410013 | -123996 | -5448695.907 | 1982491.7186 | 511462.224 | 2493953.9426
3 | 0 | 504300 | 7286147.0069 | 7790447.0069 | -4188714.9905 | -1414632 | -135075 | -5738421.9905 | 2052025.0164 | 511462.224 | 2563487.2404
4 | 0 | 516907.5 | 7650454.3572 | 8167361.8572 | -4481925.0398 | -1420489 | -147196 | -6049610.0398 | 2117751.8174 | 511462.224 | 2629214.0414
5 | 0 | 529830.1875 | 8032977.0751 | 8562807.2626 | -4795659.7926 | -1427708 | -160459 | -6383826.7926 | 2178980.47 | 511462.224 | 2690442.694
6 | 0 | 543075.9422 | 8434625.9288 | 8977701.871 | -5131355.9781 | -1436422 | -174976 | -6742753.9781 | 2234947.8929 | 511462.224 | 2746410.1169
7 | 0 | 556652.8407 | 8856357.2253 | 9413010.066 | -5490550.8966 | -1446782 | -190868 | -7128200.8966 | 2284809.1694 | 511462.224 | 2796271.3934
8 | 0 | 570569.1618 | 9299175.0866 | 9869744.2483 | -5874889.4594 | -1458949 | -208269 | -7542107.4594 | 2327636.789 | 511462.224 | 2839099.013
9 | 0 | 584833.3908 | 9764133.8409 | 10348967.2317 | -6286131.7215 | -1473104 | -227326 | -7986561.7215 | 2362405.5102 | 511462.224 | 2873867.7342
10 | 0 | 599454.2256 | 10252340.5329 | 10851794.7585 | -6726160.942 | -1489444 | -248200 | -8463804.942 | 2387989.8165 | 511462.224 | 2899452.0405
[9 empty] | 10.67% |  | 15.9%
Note on F17: Cynthia Hendrayani: Based on 8 months Adjusted for 12 months
Note on F19: Cynthia Hendrayani : grow by 7%/year since 2009
Note on G26: Cynthia Hendrayani: Based on 6 months, adjusted for 12 months
Note on H17: Cynthia Hendrayani: Based on 8 months, adjusted for 12 months
Note on H26: Cynthia Hendrayani: Based on 6 months, adjusted for 12 months

## FSA-0
FINANCIAL PARAMETERS | [5 empty] | Sensitivity Scenario
Total Project Costs |  |  |  | 12499720 |  | Exchange Rate is improved to Rp9025
Project Parameters | [5 empty] | IRR | 15.2%
Exchange Rate |  |  | IDR/USD | 9025
Initial Natural Gas Price |  |  | /MMBTU | 5
Natural gas costs |  |  | /TJ | 4743.833
Steam Sales Rates |  |  | /tonnes | 6.6482
Electricity Price from PLN |  |  | /kWh | 0.07545
Electricity Price to users |  |  | /kWh | 0.073187
CER Price |  |  |  | 12
CASH FLOW ANALYSIS |  | Sales Revenue |  |  | Overhead |  |  |  | Net Cash Flow
Annual Increased Rate |  | 2.5% | 5% | 0 | 7%
Year | Capital Expenditure | Steam | Power | Total Sales Revenue | Gas | Other costs | Operating Expense | Total Overhead
0 | -12499720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12499720
2007 | 0 | 505263.1579 | 6956579.0733 | 7461842.2312 | -3914686.907 | -1420276.5 | -147100.5 | -5482063.907 | 1979778.3242
2008 | 0 | 517894.7368 | 7304408.027 | 7822302.7638 | -3914686.907 | -1410013 | -123996 | -5448695.907 | 2373606.8568
2009 | 0 | 530842.1053 | 7669628.4283 | 8200470.5336 | -4188714.9905 | -1414632 | -135075 | -5738421.9905 | 2462048.5431
2010 | 0 | 544113.1579 | 8053109.8497 | 8597223.0076 | -4481925.0398 | -1420489 | -147196 | -6049610.0398 | 2547612.9678
2011 | 0 | 557715.9868 | 8455765.3422 | 9013481.329 | -4795659.7926 | -1427708 | -160459 | -6383826.7926 | 2629654.5364
2012 | 0 | 571658.8865 | 8878553.6093 | 9450212.4958 | -5131355.9781 | -1436422 | -174976 | -6742753.9781 | 2707458.5177
2013 | 0 | 585950.3587 | 9322481.2898 | 9908431.6485 | -5490550.8966 | -1446782 | -190868 | -7128200.8966 | 2780230.7519
2014 | 0 | 600599.1176 | 9788605.3543 | 10389204.4719 | -5874889.4594 | -1458949 | -208269 | -7542107.4594 | 2847097.0126
2015 | 0 | 615614.0956 | 10278035.622 | 10893649.7176 | -6286131.7215 | -1473104 | -227326 | -7986561.7215 | 2907087.9961
2016 | 0 | 631004.448 | 10791937.4031 | 11422941.8511 | -6726160.942 | -1489444 | -248200 | -8463804.942 | 2959136.909
15.2%
Note on F17: Cynthia Hendrayani: Based on 8 months
Note on F19: Cynthia Hendrayani : grow by 7%/year since 2009
Note on G26: Cynthia Hendrayani: Based on 6 months, adjusted for 12 months

## FSA-1
FINANCIAL PARAMETERS | [5 empty] | Sensitivity Scenario
Total Project Costs |  |  |  | 12499720 |  | PLN Rate is increased by 5%
Project Parameters | [5 empty] | IRR |  | 14.73%
Exchange Rate |  |  | IDR/USD | 9500
Initial Natural Gas Price |  |  | /MMBTU | 5
Natural gas costs |  |  | /TJ | 4743.833
Steam Sales Rates |  |  | /tonnes | 6.3158
Electricity Price from PLN |  |  | /kWh | 0.075262
Electricity Price to users |  |  | /kWh | 0.073004
CER Price |  |  |  | 12
CASH FLOW ANALYSIS |  | Sales Revenue |  |  | Overhead |  |  |  | Net Cash Flow
Annual Increased Rate |  | 2.5% | 5% | 0 | 7%
Year | Capital Expenditure | Steam | Power | Total Sales Revenue | Gas | Other costs | Operating Expense | Total Overhead
0 | -12499720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12499720
2007 | 0 | 480000 | 6939187.6256 | 7419187.6256 | -3914686.907 | -1420276.5 | -147100.5 | -5482063.907 | 1937123.7186
2008 | 0 | 492000 | 7286147.0069 | 7778147.0069 | -3914686.907 | -1410013 | -123996 | -5448695.907 | 2329451.0999
2009 | 0 | 504300 | 7650454.3572 | 8154754.3572 | -4188714.9905 | -1414632 | -135075 | -5738421.9905 | 2416332.3667
2010 | 0 | 516907.5 | 8032977.0751 | 8549884.5751 | -4481925.0398 | -1420489 | -147196 | -6049610.0398 | 2500274.5352
2011 | 0 | 529830.1875 | 8434625.9288 | 8964456.1163 | -4795659.7926 | -1427708 | -160459 | -6383826.7926 | 2580629.3237
2012 | 0 | 543075.9422 | 8856357.2253 | 9399433.1675 | -5131355.9781 | -1436422 | -174976 | -6742753.9781 | 2656679.1894
2013 | 0 | 556652.8407 | 9299175.0866 | 9855827.9273 | -5490550.8966 | -1446782 | -190868 | -7128200.8966 | 2727627.0307
2014 | 0 | 570569.1618 | 9764133.8409 | 10334703.0026 | -5874889.4594 | -1458949 | -208269 | -7542107.4594 | 2792595.5433
2015 | 0 | 584833.3908 | 10252340.5329 | 10837173.9237 | -6286131.7215 | -1473104 | -227326 | -7986561.7215 | 2850612.2022
2016 | 0 | 599454.2256 | 10764957.5596 | 11364411.7851 | -6726160.942 | -1489444 | -248200 | -8463804.942 | 2900606.8431
14.73%
Note on F17: : Based on 8 months
Note on F19: : grow by 7%/year since 2009
Note on G26: Cynthia Hendrayani: Based on 6 months, adjusted for 12 months

## FSA-2
FINANCIAL PARAMETERS | [5 empty] | Sensitivity Scenario
Total Project Costs |  |  |  | 12499720 |  | Steam rate goes up to Rp65
Project Parameters | [5 empty] | IRR |  | 11.13%
Exchange Rate |  |  | IDR/USD | 9500
Initial Natural Gas Price |  |  | /MMBTU | 5
Natural gas costs |  |  | /TJ | 4743.833
Steam Sales Rates |  |  | /tonnes | 6.8421
Electricity Price from PLN |  |  | /kWh | 0.071678
Electricity Price to users |  |  | /kWh | 0.069528
CER Price |  |  |  | 12
CASH FLOW ANALYSIS |  | Sales Revenue |  |  |  | Overhead |  |  | Net Cash Flow
Annual Increased Rate |  | 2.5% | 5% | 0 | 7%
Year | Capital Expenditure | Steam | Power | Total Sales Revenue | Gas | Other costs | Operating Expense | Total Overhead
0 | -12499720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12499720
2007 | 0 | 520000 | 6608750.1196 | 7128750.1196 | -3914686.907 | -1420276.5 | -147100.5 | -5482063.907 | 1646686.2126
2008 | 0 | 533000 | 6939187.6256 | 7472187.6256 | -3914686.907 | -1410013 | -123996 | -5448695.907 | 2023491.7186
2009 | 0 | 546325 | 7286147.0069 | 7832472.0069 | -4188714.9905 | -1414632 | -135075 | -5738421.9905 | 2094050.0164
2010 | 0 | 559983.125 | 7650454.3572 | 8210437.4822 | -4481925.0398 | -1420489 | -147196 | -6049610.0398 | 2160827.4424
2011 | 0 | 573982.7031 | 8032977.0751 | 8606959.7782 | -4795659.7926 | -1427708 | -160459 | -6383826.7926 | 2223132.9856
2012 | 0 | 588332.2707 | 8434625.9288 | 9022958.1995 | -5131355.9781 | -1436422 | -174976 | -6742753.9781 | 2280204.2214
2013 | 0 | 603040.5775 | 8856357.2253 | 9459397.8028 | -5490550.8966 | -1446782 | -190868 | -7128200.8966 | 2331196.9062
2014 | 0 | 618116.5919 | 9299175.0866 | 9917291.6785 | -5874889.4594 | -1458949 | -208269 | -7542107.4594 | 2375184.2191
2015 | 0 | 633569.5067 | 9764133.8409 | 10397703.3476 | -6286131.7215 | -1473104 | -227326 | -7986561.7215 | 2411141.6261
2016 | 0 | 649408.7444 | 10252340.5329 | 10901749.2773 | -6726160.942 | -1489444 | -248200 | -8463804.942 | 2437944.3353
11.13%
Note on F17: : Based on 8 months
Note on F19: : grow by 7%/year since 2009
Note on G26: Cynthia Hendrayani: Based on 6 months, adjusted for 12 months

## FSA-3
FINANCIAL PARAMETERS | [5 empty] | Sensitivity Scenario
Total Project Costs |  |  |  | 12499720 |  | Electrical load increased to 95%
Project Parameters | [5 empty] | IRR |  | 15.16%
Electrical output at 95% load |  |  | MWh/yr | 100332.6667
Exchange Rate |  |  | IDR/USD | 9500
Initial Natural Gas Price |  |  | /MMBTU | 5
Natural gas costs |  |  | /TJ | 4743.833
Steam Sales Rates |  |  | /tonnes | 6.3158
Electricity Price from PLN |  |  | /kWh | 0.071678
Electricity Price to users |  |  | /kWh | 0.069528
CER Price |  |  |  | 12
CASH FLOW ANALYSIS |  | Sales Revenue |  |  |  | Overhead |  |  | Net Cash Flow | Revenue from CDM
Annual Increased Rate |  | 2.5% | 5% | 0 | 7%
Year | Capital Expenditure | Steam | Power | Total Sales Revenue | Gas | Other costs | Operating Expense | Total Overhead |  | Revenue from CDM | Cash Flow
0 | -12499720 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -12499720 | 0 | -12499720
2007 | 0 | 480000 | 6975885.2904 | 7455885.2904 | -3914686.907 | -1420276.5 | -147100.5 | -5482063.907 | 1973821.3834 | 511462.224 | 2485283.6074
2008 | 0 | 492000 | 7324679.5549 | 7816679.5549 | -3914686.907 | -1410013 | -123996 | -5448695.907 | 2367983.6479 | 511462.224 | 2879445.8719
2009 | 0 | 504300 | 7690913.5327 | 8195213.5327 | -4188714.9905 | -1414632 | -135075 | -5738421.9905 | 2456791.5422 | 511462.224 | 2968253.7662
2010 | 0 | 516907.5 | 8075459.2093 | 8592366.7093 | -4481925.0398 | -1420489 | -147196 | -6049610.0398 | 2542756.6695 | 511462.224 | 3054218.8935
2011 | 0 | 529830.1875 | 8479232.1698 | 9009062.3573 | -4795659.7926 | -1427708 | -160459 | -6383826.7926 | 2625235.5646 | 511462.224 | 3136697.7886
2012 | 0 | 543075.9422 | 8903193.7783 | 9446269.7204 | -5131355.9781 | -1436422 | -174976 | -6742753.9781 | 2703515.7423 | 511462.224 | 3214977.9663
2013 | 0 | 556652.8407 | 9348353.4672 | 9905006.3079 | -5490550.8966 | -1446782 | -190868 | -7128200.8966 | 2776805.4113 | 511462.224 | 3288267.6353
2014 | 0 | 570569.1618 | 9815771.1405 | 10386340.3023 | -5874889.4594 | -1458949 | -208269 | -7542107.4594 | 2844232.8429 | 511462.224 | 3355695.0669
2015 | 0 | 584833.3908 | 10306559.6975 | 10891393.0884 | -6286131.7215 | -1473104 | -227326 | -7986561.7215 | 2904831.3668 | 511462.224 | 3416293.5908
2016 | 0 | 599454.2256 | 10821887.6824 | 11421341.908 | -6726160.942 | -1489444 | -248200 | -8463804.942 | 2957536.966 | 511462.224 | 3468999.19
[9 empty] | 15.16% |  | 20.04%
Note on F18: : Based on 8 months
Note on F20: : grow by 7%/year since 2009
Note on G27: Cynthia Hendrayani: Based on 6 months, adjusted for 12 months

## GRID-EF
JAVA - BALI ELECTRICITY GRID DATA
published by PLN in their website not inclusive of power generated by IPP
Generating Capacity (GWhr)
Source | Type | 2006 | 2005 | 2004 | 2003 | 2002
PLTA | Hydroelectric | 5207.6686 | 7090.79 | 5428.22 | 4891.32 | 5983.13
PLTU |  | 64628.7479 | 55699.1 | 37034.58 | 37526.42 | 34279.21
PLTG |  | 1890.6436 | 5293.5 | 2147.86 | 1685.68 | 1091.08
PLTGU |  | 26939.1244 | 26184.8 | 25475.8 | 23817.38 | 24272.31
PLTP | Geothermal | 6499.7609 | 6466.25 | 2988.24 | 2803.52 | 3055.7
PLTD |  | 108.2029 | 161.15 | 94.09 | 117.23 | 110.52
Purchased (IPP) | Assumed low-cost/must-run |  |  | 22236 | 19110 | 13425
Total (GWh) |  | 105274.1483 | 100895.59 | 95404.79 | 89951.55 | 82216.95
% of low cost must run |  | 0.11121 | 0.13437 | 0.32129 | 0.29799 | 0.27323
Source |  |  | Fuel Usage
|  | 2006 | 2005 | 2004 | 2003 | 2002
Fuel Oil (kL=1m3) | High Speed Diesel | 4393415 | 5148475.53 | 3267163.25 | 2332127.53 | 2154519.85
| Industrial Diesel Oil | 0 | 14288.58 | 9586 | 9701.72 | 11346.53
| Marine Fuel Oil | 2340481 | 1933927.72 | 2096786.7 | 2088045.28 | 1939015.56
| Total Fuel Oil | 6733896 | 7096691.83 | 5373535.95 | 4429874.53 | 4104881.94
Coal (T) |  | 26978371.5212 | 23878644.72 | 13425337.19 | 13294500.82 | 11864647.82
Natural Gas (MMSCF) |  | 142494.2514 | 124003.7073 | 138693.3 | 154901.93 | 159646.41
Conversion Data
Density of HSD |  | Based www.pertamina.co.id |  |  | 820 | kg/m3
Density of Diesel Oil |  | Based www.pertamina.co.id |  |  | 840 | kg/m3
Density of MFO |  | Based www.pertamina.co.id |  |  | 990 | kg/m3
Density of Natural Gas |  |  |  |  | 0.654 | kg/m3
Source |  |  | Fuel Usage (kT)
|  | 2006 | 2005 | 2004 | 2003 | 2002
HSD |  | 3602.6003 | 4221.7499 | 2679.0739 | 1912.3446 | 1766.7063
Diesel Oil |  | 0 | 12.0024 | 8.0522 | 8.1494 | 9.5311
MFO |  | 2317.0762 | 1914.5884 | 2075.8188 | 2067.1648 | 1919.6254
Coal |  | 26978.3715 | 23878.6447 | 13425.3372 | 13294.5008 | 11864.6478
Natural Gas |  | 2638.8796 | 2296.4495 | 2568.489 | 2868.6599 | 2956.5238
Total |  | 31934.3273 | 28101.6851 | 18077.6973 | 18238.4749 | 16750.3281
IPCC Data |  |  |  |  | NCV | EF-CO2
[5 empty] | TJ/kT | T-CO2/TJ
HSD+Diesel Oil |  |  |  |  | 43 | 74.1
MFO |  |  |  |  | 40.4 | 77.4
Coal |  |  |  |  | 21.3389 | 96.1
Natural Gas |  |  |  |  | 48 | 56.1
Carbon Emission (T_CO2) |  | 2006 | 2005 | 2004 | 2003 | 2002
HSD+Diesel Oil |  | 11478965.3359 | 13490005.0867 | 8561989.9084 | 6119270.094 | 5659625.1072
MFO |  | 7245404.5631 | 5986841.4771 | 6491002.458 | 6463941.7281 | 6002591.8545
Coal |  | 55323722.453 | 48967207.3796 | 27530928.9129 | 27262626.7652 | 24330470.8915
Natural Gas |  | 7105974.9091 | 6183879.1676 | 6916427.1572 | 7724727.2605 | 7961327.3725
Total CO2 Emission (T_CO2) |  | 81154067.2611 | 74627933.1109 | 49500348.4365 | 47570565.8478 | 43954015.2257
Operating Margin |  | 2006 | 2005 | 2004 | 2003 | 2002
Total CO2 Emission (T_CO2) |  | 81154067.2611 | 74627933.1109 | 49500348.4365 | 47570565.8478 | 43954015.2257
Total Power Generated (MWh) |  | 105274148.3401 | 100895590 | 95404790 | 89951550 | 82216950
Power from Low cost/must-run sources
| Hydroelectric | 5207668.6223 | 7090790 | 5428220 | 4891320 | 5983130
| Geothermal | 6499760.8845 | 6466250 | 2988240 | 2803520 | 3055700
| IPP | 0 | 0 | 22236000 | 19110000 | 13425000
| Low-cost Must Run | 11707429.5069 | 13557040 | 30652460 | 26804840 | 22463830
Power from non-Low-Cost Must Run Sources(MWh) |  | 93566718.8333 | 87338550 | 64752330 | 63146710 | 59753120
Average Operating Margin Emission Factor (T_CO2/MWh) |  | 0.86734 | 0.85447 | 0.76446 | 0.75333 | 0.73559
2006 Build Margin |  |  | Fuel Type | Accumulative | annual generation | fuel consumption
Recently Built Power Plants |  |  |  | % | MWh/yr | in kT
2006 | Cilegon |  | gas | 0.7349% | 773675.5077 | 6.7
2006 | Tanjung Jati B |  | coal | 4.547% | 4013074.2779 | 1887.07
2006 | Cilacap |  | coal | 6.353% | 1901659.0479 | 965.13
2005 | Muara Tawar 3-4 |  | HSD | 7.913% | 1641877.0843 | 582.46
2005 | Wayang Windhu |  | geothermal | 8.789% | 922298.925 | 0
2004 | Paiton (PEC) |  | coal | 17.77% | 9451481.5065 | 4565.84
2004 | Jawa Power |  | coal | 26.74% | 9446178.5037 | 4520.18
Total annual generation from sample group m |  |  |  |  | 28150244.8529
Total annual generation from all power plants attached to the grid |  |  |  |  | 105274148.3401
% of newly installed plant from overall generation |  |  |  |  | 0.2674
2006 Build Margin |  |  |  |  | CO2 emission
Recently Built Power Plants |  |  |  |  | tCO2/yr
| Cilegon | gas |  |  | 18041.76
| Tanjung Jati B | coal |  |  | 3869756.8105
| Cilacap | coal |  |  | 1979162.6121
| Muara Tawar 3-4 | hsd |  |  | 1855892.298
| Wayang Windhu | geothermal |  |  | 0
| Paiton (PEC) | coal |  |  | 9363028.6293
| Jawa Power | coal |  |  | 9269395.0619
Total emissions from sample group m |  |  |  |  | 26355277.1718 | tCO2
Total generations from sample group m |  |  |  |  | 28150244.8529 | MWh
Renewable energy generations (Low-Cost/Must Run) |  |  |  |  | 922298.925 | MWh
Total from energy generations excluding Low-Cost/Must Run |  |  |  |  | 27227945.9279 | MWh
Build margin emission factor |  |  |  |  | 0.93624 | tCO2/MWh
Emission Factor of Grid |  |  |  |  | 0.901
Note on F29: Cynthia Hendrayani: Calculated using ideal gas equation for 100% methane at STP
Note on F40: Cynthia Hendrayani: 2006 IPCC Table 1.2
Note on F44: Cynthia Hendrayani: Based on mid-rank sub-bituminous coal 5100kcal/kg
Note on F43: : Based on Residual Fuel
Note on F45: CH: Default value of IPCC Table 1.2
Note on D21: Cynthia Hendrayani: No IPP uses oil-based fuel
Note on D5: Cynthia Hendrayani: IPP Data has been added as per information provided by PLN (data is provided in 2005IPP worksheet)
Note on C22: Cynthia Hendrayani: Consumption of coal increases significantly due to the incoming Muara Tawar Power Plant, Tanjung Jati I, Cilacap Power Plants in 2006.
Note on D22: Cynthia Hendrayani: 2005 IPP Data is included covers only Paiton PEC and Jawa Power
Note on D23: Cynthia Hendrayani: 2005 IPP Data is included covers only Cikarang Listrindo

## RD-2005IPP
The following generation data is provided by PLN covers only all IPPs exporting power to PLN to compliment Table 23 of 2005 data published by PLN.
Since, no fuel consumption data is provided. It is estimated based on Specific Fuel Consumption of corresponding plant (non-Renewable) in 2006.
2005 IPP Power Plants | Type | Fuel Type | Generation (GWh) | SFC | Fuel Consumption | Units
PO Jatiluhur | PLTA | Hydro | 843
PT Cikarang | PLTG | Natural Gas | 545 | 0.0164 | 8.938 | 1000 GBTU
PT DSP/Salak | PLTP | Geothermal | 1586
PT Geo Dipa Eng | PLTP | Geothermal | 321
PT Paiton (PEC) | PLTU | Coal | 9363 | 0.48308 | 4523.078 | kT
PT Jawa Power | PLTU | Coal | 9072 | 0.47852 | 4341.1334 | kT
PT Magma Nusantara | PLTP | Geothermal | 936
PT Amoseas Inc | PLTP | Geothermal | 753
PT Krakatau Jaya | PLTG | Natural Gas | 2 | Unknown
N/A | Not Available
N/R | Not Relevant
2005 IPP Power Plants | Generation (GWh) | Fuel Type | Fuel Consumption | Unit
PLTA | 843 | Hydro | N/R | Unit
PLTU | 18435 | Coal | 8864.2115 | kT
PLTG | 545 | Natural Gas | 10599.6373 | MMSCF
PLTGU | 0 | N/A | N/R | N/R
PLTP | 3596 | Geothermal | N/R | N/R
PLTD | 0 | N/A | N/R | N/R
Note on E5: Cynthia Hendrayani: SFC=Specific Fuel Consumption, based on PLN publication (2007 Report)
Note on D14: Cynthia Hendrayani: PT Krakatau Daya is excluded as its SFC is unknown
Note on D22: Cynthia Hendrayani: Converted based on: 9.486*10^-4 TBTU/TJ 35.314 SCF/M3

## RD-2006ALL
Type | Name | Owner | Fuel Type | Own Usage % | SFC | SFC P3B | Capacity | Generation (GWh) | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | CF | Total Fuel | Unit
PLTA | Saguling | INER | HYDRO | 0.35 | 1 | 0 | 700.72 | 1551.3714 | 182.932 | 190.8337 | 178.6462 | 136.0854 | 165.032 | 121.6631 | 111.4437 | 105.3783 | 85.0297 | 55.4778 | 31.2243 | 187.6251 | 0.25274 | 1551.3714 | GWH
PLTA | Area 1 | INER | HYDRO | 0.5 | 1 | 0 | 37.26 | 108.456 | 13.5882 | 11.8217 | 10.7153 | 10.8775 | 9.9698 | 7.3713 | 6.0064 | 4.9332 | 4.2351 | 5.6929 | 9.7581 | 13.4864 | 0.33228 | 108.456 | GWH
PLTA | Area 2 | INER | HYDRO | 0.4 | 1 | 0 | 59.38 | 201.8352 | 23.241 | 25.3874 | 25.3335 | 24.897 | 27.1999 | 17.9179 | 11.1909 | 9.5166 | 7.9002 | 8.2054 | 7.9573 | 13.0879 | 0.38802 | 201.8352 | GWH
PLTA | Area 3 | INER | HYDRO | 1.0132 | 1 | 0 | 305.69 | 745.7868 | 123.9254 | 102.9339 | 75.0092 | 102.7368 | 90.0545 | 57.7494 | 37.8596 | 22.8542 | 29.9207 | 34.6491 | 34.0469 | 34.0469 | 0.2785 | 745.7868 | GWH
PLTU | Suralaya 1-4 | INER | COAL | 6.675 | 0.50102 | 0.50102 | 1600 | 11959.1103 | 1001.3034 | 754.8704 | 1029.0529 | 1009.9185 | 1102.3541 | 868.26 | 1105.9275 | 985.8542 | 1102.9202 | 890.6064 | 1015.363 | 1092.6798 | 0.85325 | 5991.7935 | KTON
PLTU | Suralaya 5-7 | INER | COAL | 4.475 | 0.47695 | 0.47695 | 1800 | 13310.2707 | 1210.5583 | 1143.9884 | 1013.8355 | 826.8763 | 1148.4165 | 1252.9936 | 989.896 | 1170.3541 | 1171.3398 | 903.8386 | 1194.9832 | 1283.1905 | 0.84413 | 6348.3063 | KTON
PLTU | Priok | INER | MFO | 6.75 | 0.32337 | 0.32337 | 100 | 62.034 | 7.7986 | 2.1912 | 13.2873 | 10.0662 | 25.4315 | 4.1612 | -0.1798 | -0.23902 | -0.2728 | -0.21048 | 0 | 0 | 0.070815 | 20.06 | 1000 KL
PLTU | Tbrok 1-3 | INER | MFO | 6.85 | 0.29 | 0.32311 | 300 | 1255.8246 | 111.9154 | 103.3422 | 97.2637 | 88.297 | 137.1633 | 103.2785 | 120.3685 | 120.6325 | 84.5315 | 87.4905 | 101.0863 | 100.455 | 0.47786 | 364.1891 | 1000 KL
PLTU | Perak 3-4 | INER | MFO | 6.85 | 0.32856 | 0.42626 | 100 | 356.5912 | 18.2635 | 40.6791 | 39.6508 | 37.0866 | 33.6372 | 38.4039 | 30.1532 | 28.3817 | 23.011 | 23.8241 | 23.0071 | 20.493 | 0.40707 | 117.1609 | 1000 KL
PLTGU | Priok (G) | INER | GAS | 1.6665 | 0.0081667 | 0.0085203 | 1180 | 3918.6661 | 343.7138 | 294.2889 | 306.051 | 297.0559 | 366.0676 | 284.1723 | 354.9589 | 370.6286 | 338.2254 | 347.5204 | 307.9917 | 307.9917 | 0.3791 | 32.0024 | 1000 GBTU
PLTGU | Priok (M) | INER | HSD | 1.725 | 0.25093 |  | 1180 | 3342.073 | 367.6328 | 316.5602 | 370.3718 | 326.174 | 311.4397 | 306.6492 | 265.24 | 192.4312 | 105.8229 | 267.6748 | 237.2282 | 274.8482 | 0.32332 | 838.6264 | 1000 KL
PLTGU | Tbrok | INER | HSD | 2.41 | 0.22663 | 0.27077 | 1033.9 | 3387.5563 | 262.5143 | 266.4616 | 363.5847 | 360.4657 | 388.1997 | 232.8114 | 245.4929 | 238.4001 | 300.5372 | 221.0883 | 321.0409 | 186.9597 | 0.37403 | 767.706 | 1000 KL
PLTGU | Grati (CC) | INER | HSD | 3.6 | 0.22663 | 0.2747 | 461.83 | 1149.316 | 133.8197 | 121.3217 | 157.1508 | 44.5027 | 120.6606 | 41.8106 | 18.4342 | 77.453 | 109.4459 | 67.0958 | 178.1276 | 79.4935 | 0.28409 | 260.4641 | 1000 KL
PLTGU | Grati (B-II) | INER | HSD | 3.5 | 0.35475 | 0.45974 | 302.25 | 342.0789 | 9.6128 | 11.4187 | 26.5254 | 81.2472 | 28.5453 | 13.8589 | 30.9062 | 29.1719 | 27.3564 | 19.5175 | 47.3242 | 16.5944 | 0.1292 | 121.3525 | 1000 KL
PLTG | Priok | INER | HSD | 1.65 | 0.45785 | 0.44936 | 52 | 3.5041 | 0.060432 | 0.72715 | 0.37315 | -0.0033137 | 1.7632 | 0.067696 | 0.38422 | 0.17505 | -0.022979 | -0.020549 | 0 | 0 | 0.0076924 | 1.6043 | 1000 KL
PLTG | Sunyaragi (G) | INER | GAS | 2.4 | 0.0149 | 0.017486 | 40.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 GBTU
PLTG | Sunyaragi (M) | INER | HSD | 6 | 0.45311 | 0.48533 | 40.2 | 146.8491 | 9.1224 | 11.0576 | 16.3914 | 16.0519 | 7.3109 | 11.2394 | 13.3069 | 12.3043 | 11.3097 | 11.9562 | 15.8742 | 10.9244 | 0.417 | 66.5382 | 1000 KL
PLTG | Pesanggaran(M) | INER | HSD | 1.52 | 0.43931 | 0.46977 | 125.45 | 544.607 | 39.8939 | 37.3859 | 46.7567 | 42.4372 | 54.3468 | 49.8046 | 53.2283 | 50.2495 | 30.546 | 37.0192 | 49.8324 | 53.1065 | 0.49557 | 239.2534 | 1000 KL
PLTG | Gilimanuk | INER | HSD | 1.5 | 0.43931 | 0.45839 | 133.8 | 621.9394 | 61.8034 | 57.2856 | 58.9399 | 63.7195 | 68.3103 | 41.0335 | -0.12028 | 35.236 | 59.5783 | 59.9576 | 62.941 | 53.2547 | 0.53063 | 273.2266 | 1000 KL
PLTG | Cilacap | INER | HSD | 2.501 | 0.4685 | 0.50471 | 55 | 19.022 | 3.5483 | 1.714 | 2.8655 | 3.9798 | 5.4006 | 0.83146 | 0.16394 | 0.44127 | 0.011536 | 0.065578 | 0 | 0 | 0.039481 | 8.9118 | 1000 KL
PLTG | Pemaron | INER | HSD | 1.52 | 0.43931 | 0.47172 | 97.64 | 117.0632 | 0.16348 | 3.095 | 4.1491 | 8.814 | 9.364 | 13.4983 | 39.1501 | 17.4634 | -0.21527 | 1.6907 | 7.1101 | 12.7803 | 0.13686 | 51.4275 | 1000 KL
PLTD | Pesanggaran(M) | INER | HSD | 6.7486 | 0.30863 | 0.40122 | 75.84 | 108.2029 | 13.424 | 12.9853 | 10.6769 | 11.3488 | 10.0086 | 4.7218 | 4.7002 | 6.1007 | 13.7862 | 11.7783 | 3.3752 | 5.2968 | 0.16287 | 33.3948 | 1000 KL
PLTP | Kamojang | INER | GEOTH | 5.5 | 1 |  | 145 | 1055.2245 | 64.1509 | 55.3369 | 63.5897 | 61.2378 | 84.9934 | 102.1019 | 105.816 | 105.9908 | 102.8277 | 105.2847 | 97.8951 | 105.9995 | 0.83075 | 1055.2245 | GWH
PLTP | Salak | INER | GEOTH | 5.8 | 1 |  | 165 | 1470.0015 | 112.9576 | 115.1604 | 128.5603 | 122.5519 | 129.7687 | 119.7645 | 128.3679 | 127.0203 | 124.3421 | 120.784 | 119.63 | 121.0938 | 1.017 | 1470.0015 | GWH
PLTP | Drajat | INER | GEOTH | 5.5 | 1 |  | 55 | 463.8898 | 41.0407 | 37.0231 | 40.9508 | 18.7456 | 41.5909 | 40.2892 | 41.1192 | 41.7405 | 40.3444 | 41.4201 | 39.1728 | 40.4525 | 0.96283 | 463.8898 | GWH
PLTA | Cirata | PJB | HYDRO | 0.44 | 1 |  | 1008 | 873.4766 | 84.9601 | 98.7906 | 98.5187 | 78.1176 | 69.0739 | 73.2807 | 90.9231 | 60.8798 | 46.6549 | 43.926 | 14.3734 | 113.9777 | 0.098921 | 873.4766 | GWH
PLTA | BrMtas | PJB | HYDRO | 1.7818 | 1 |  | 109 | 845.2481 | 118.9097 | 96.3145 | 107.5753 | 122.3825 | 101.4521 | 60.0911 | 48.5976 | 46.4094 | 33.9786 | 37.6317 | 38.2634 | 33.6422 | 0.88522 | 845.2481 | GWH
PLTA | Area 4 | PJB | HYDRO | 2.09 | 1 |  | 166 | 178.2665 | 16.8269 | 15.508 | 15.8858 | 16.543 | 16.7156 | 14.4678 | 13.6945 | 13.8318 | 14.7122 | 14.1845 | 13.2155 | 12.6809 | 0.12259 | 178.2665 | GWH
PLTU | Paiton | PJB | COAL | 7.55 | 0.5055 | 0.4911 | 800 | 5341.3773 | 498.2161 | 485.1656 | 369.8581 | 276.5041 | 354.5978 | 520.4193 | 498.4346 | 521.0347 | 554.2368 | 524.1385 | 408.1817 | 330.59 | 0.76218 | 2700.0662 | KTON
PLTU | M.Karang 4-5(M) | PJB | MFO | 6.59 | 0.287 | 0.010801 | 400 | 1338.3655 | 97.2037 | 39.987 | 90.3743 | 67.1016 | 107.862 | 62.753 | 59.5108 | 110.7109 | 111.3788 | 209.1276 | 208.4188 | 173.937 | 0.38195 | 384.1109 | 1000 KL
PLTU | M.Karang 1-3(M) | PJB | MFO | 6.84 | 0.2941 | 0.32884 | 300 | 1689.3524 | 163.6599 | 143.0384 | 126.144 | 81.8128 | 131.6117 | 136.0593 | 151.1693 | 146.9572 | 123.2411 | 136.7071 | 182.4415 | 166.5101 | 0.64283 | 496.8351 | 1000 KL
PLTU | Gresik 3-4(M) | PJB | MFO | 6.145 | 0.2488 | 0.269 | 400 | 2410.2929 | 113.8895 | 197.0969 | 219.1693 | 228.4019 | 239.5765 | 202.4264 | 217.6009 | 114.8608 | 161.7177 | 228.4228 | 253.2329 | 233.8973 | 0.68787 | 599.6809 | 1000 KL
PLTU | Gresik 1-2(M) | PJB | MFO | 5.84 | 0.27166 | 0.28416 | 200 | 1319.4602 | 114.9907 | 95.1578 | 77.8315 | 105.9865 | 79.3799 | 62.6757 | 113.4993 | 221.7019 | 100.6963 | 117.5563 | 122.1774 | 107.8069 | 0.75312 | 358.4446 | 1000 KL
PLTGU | M.Karng | PJB | GAS | 2.27 | 0.008965 | 0.0084864 | 508.68 | 3068.551 | 267.8216 | 264.8866 | 323.4514 | 308.1193 | 287.0934 | 282.4817 | 209.7218 | 245.8646 | 257.8091 | 207.7159 | 184.6192 | 228.9664 | 0.68863 | 27.5096 | 1000 GBTU
PLTGU | Gresik Blok 1(G) | PJB | GAS | 2.12 | 0.00865 |  | 526.26 | 2585.2915 | 211.2951 | 199.4323 | 233.535 | 243.3074 | 253.3425 | 241.2333 | 279.5983 | 221.8896 | 254.5361 | 208.0218 | 96.7467 | 142.3535 | 0.5608 | 22.3628 | 1000 GBTU
PLTGU | Gresik Blok 2(G) | PJB | GAS | 2.12 | 0.00865 |  | 175.42 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1000 GBTU
PLTGU | Gresik Blok 2(M) | PJB | HSD | 2.12 | 0.25093 |  | 350.84 | 1509.5441 | 40.4882 | 19.5862 | 197.5723 | 222.6176 | 191.7385 | 161.7197 | 188.0371 | 92.9418 | 63.5965 | 23.66 | 164.99 | 142.5963 | 0.49117 | 378.7899 | 1000 KL
PLTGU | Gresik Blok 3(G) | PJB | GAS | 2.12 | 0.00865 |  | 526.26 | 2889.8275 | 284.1759 | 266.2472 | 213.8718 | 171.8507 | 219.8496 | 222.2243 | 106.7054 | 214.0799 | 282.7583 | 322.2605 | 314.5944 | 271.2095 | 0.62686 | 24.997 | 1000 GBTU
PLTGU | Muaratawar Blok 1 | PJB | HSD | 3.5 | 0.2263 | 0.23278 | 640 | 2711.0044 | 37.4156 | 134.2383 | 213.9304 | 321.7825 | 280.7035 | 307.7532 | 315.5021 | 136.9546 | 220.9448 | 284.4536 | 233.8481 | 223.4776 | 0.48356 | 613.5003 | 1000 KL
PLTGU | Muaratawar Blok 2 | PJB | HSD | 2.55 | 0.35475 | 0.3679 | 280 | 393.3384 | 53.0832 | 34.0705 | 50.6295 | 51.9918 | 69.6236 | 16.895 | 40.7618 | 25.0644 | 9.1744 | 9.6246 | 25.2827 | 7.137 | 0.16036 | 139.5368 | 1000 KL
PLTG | Gresik | PJB | HSD | 2.25 | 0.45785 | 0.46963 | 61.55 | 8.9238 | -0.0015274 | 0.61601 | 1.2967 | 4.1672 | 0 | 0 | 0 | 0.24593 | 0.32075 | 0.042752 | 1.7914 | 0.44453 | 0.016551 | 4.0858 | 1000 GBTU
PLTG | Gili Timur | PJB | HSD | 2.25 | 0.45785 |  | 40.2 | 27.3895 | 5.3 | 4.4728 | 5.1771 | 6.31 | 0 | -0.038953 | -0.039165 | 0.28581 | 0.49571 | 0.10067 | 3.5561 | 1.7695 | 0.077778 | 12.5403 | 1000 KL
PLTGU | Muaratawar 3-4 | PMT | HSD | 1.5228 | 0.35475 | 0.36897 | 858 | 1641.8771 | 91.6368 | 93.6074 | 103.386 | 160.8128 | 223.6078 | 147.4842 | 142.1399 | 154.2847 | 77.099 | 139.7602 | 219.7037 | 88.3546 | 0.21845 | 582.4559 | 1000 KL
PLTA | Jatiluhur | IPP | HYDRO | 0 | 1 |  | 150 | 703.228 | 94.7117 | 62.2538 | 60.6865 | 51.501 | 59.1108 | 64.8403 | 69.9379 | 66.5785 | 59.523 | 52.2038 | 31.4959 | 30.3847 | 0.53518 | 703.228 | GWH
PLTG | Cikarng L. | IPP | GAS | 0 | 0.0164 | 0.0094444 | 150 | 401.3455 | 52.0941 | 38.0216 | 48.4278 | 42.1339 | 47.8981 | 26.8375 | 28.1671 | 18.2388 | 21.9044 | 34.5585 | 20.4431 | 22.6206 | 0.30544 | 6.5821 | 1000 GBTU
PLTP | Dieng | IPP | GEOTH | 0 | 1 |  | 60 | 319.1168 | -0.12395 | 16.778 | 26.7587 | 28.3795 | 30.5096 | 31.4074 | 32.277 | 25.4743 | 31.5727 | 33.2319 | 31.2359 | 31.6156 | 0.60715 | 319.1168 | GWH
PLTP | Salak | IPP | GEOTH | 0 | 1 |  | 182 | 1533.974 | 129.3436 | 123.4657 | 135.9796 | 131.3392 | 135.9176 | 109.6348 | 98.0574 | 134.7974 | 131.8052 | 136.1209 | 131.5477 | 135.9649 | 0.96215 | 1533.974 | GWH
PLTP | W.Windu | IPP | GEOTH | 0 | 1 |  | 110 | 922.2989 | 81.7363 | 73.5225 | 81.5433 | 78.8674 | 81.6358 | 79.0571 | 79.7491 | 48.4067 | 79.4375 | 80.9776 | 78.3431 | 79.0225 | 0.95714 | 922.2989 | GWH
PLTP | Drajat.S | IPP | GEOTH | 0 | 1 |  | 199.2994 | 735.2554 | 62.1112 | 61.0866 | 67.2257 | 65.4406 | 30.6201 | 50.0582 | 66.598 | 67.2016 | 65.2505 | 66.4513 | 65.5105 | 67.701 | 0.42114 | 735.2554 | GWH
PLTU | PEC | IPP | COAL | 3.6461 | 0.48308 | 0.48308 | 1230 | 9451.4815 | 855.5886 | 812.579 | 884.7777 | 907.8997 | 498.1306 | 813.5095 | 918.2632 | 894.6764 | 899.1358 | 756.3968 | 481.6495 | 728.8746 | 0.87718 | 4565.8361 | KTON
PLTU | Jawa Power | IPP | COAL | 3.6461 | 0.47852 | 0.47852 | 1220 | 9446.1785 | 833.3188 | 777.9313 | 840.2869 | 667.834 | 847.8859 | 804.0403 | 824.5708 | 845.7044 | 675.8731 | 702.9348 | 878.5062 | 747.2919 | 0.88388 | 4520.1759 | KTON
PLTU | Tj. Jati. B Unit 1 | IPP | COAL | 3.6461 | 0.47023 | 0.47023 | 1320 | 4013.0743 | 0 | 0 | 0 | 15.4184 | 64.344 | 272.1176 | 378.4631 | 488.3115 | 623.2359 | 676.1454 | 752.9848 | 742.0536 | 0.34706 | 1887.0664 | KTON
PLTU | Tj. Jati. B Unit 2 | IPP | COAL | 0 | 0.47023 | 0.47023 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KTON
PLTU | Cllacap Unit 1 | IPP | COAL | 3.6461 | 0.50752 | 0.50752 | 600 | 1901.659 | 0.086331 | 49.305 | 45.8392 | 173.9393 | 38.113 | 175.1616 | 234.7052 | 241.2798 | 212.7948 | 193.0166 | 305.9125 | 231.5058 | 0.36181 | 965.1271 | KTON
PLTU | Cilacap Unit 2 | IPP | COAL | 0 | 0.50752 | 0.50752 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KTON
PLTU | Cilegon (OC) |  | GAS | 4.6393 | 0.0149 |  | 480 | 1.6187 | 0.0063464 | 0.021991 | 0.086292 | 0.92356 | 0.15138 | 0.023701 | 0.095006 | 0.035743 | 0.03763 | 0.23704 | 0 | 0 | 0.00038497 | 0.024119 | 1000 GBTU
PLTU | Cilegon (CC) | IPP | GAS | 4.6393 | 0.00865 |  | 740 | 772.0568 | 0 | 0 | 0 | 0 | 28.0694 | 96.5331 | 104.3469 | 137.5118 | 131.6991 | 134.3961 | 78.637 | 60.8634 | 0.1191 | 6.6783 | 1000 GBTU
Note on H24: Chek Kapasitas

## RD-2006DataAnalysis
This analysis is derived from the Master Table in RD-2006ALL provided by PT-PLN P3B using PIVOT Table.
Values
Row Labels | Sum of Generation (GWh) | Sum of Fossil Fuel kT | Sum of Total Fuel
COAL | 55423.1516 | 26978.3715 | 26978.3715
GAS | 13637.3572 | 120.1563 | 120.1563
GEOTH | 6499.7609 | 0 | 6499.7609
HSD | 16074.2892 | 3690.4682 | 4393.4145
HYDRO | 5207.6686 | 0 | 5207.6686
MFO | 8431.9208 | 1966.0045 | 2340.4815
Grand Total | 105274.1483 | 32755.0004 | 45539.8533
Fuel Type |  | 2006 Consumption
Fuel Oil (kL=1m3) | High Speed Diesel | 4393414.5426
| Industrial Diesel Oil | 0
| Marine Fuel Oil | 2340481.4915
| Total Fuel Oil | 6733896.0341
Coal (kT) |  | 26978.3715
Natural Gas (MMSCF) |  | 142494.2514
All Power Plants Generations (GWh)
Type | Owner | Total
PLTA | INER | 2607.4494
| IPP | 703.228
| PJB | 1896.9913
PLTA Total |  | 5207.6686
PLTD | INER | 108.2029
PLTD Total |  | 108.2029
PLTG | INER | 1452.9848
| IPP | 401.3455
| PJB | 36.3133
PLTG Total |  | 1890.6436
PLTGU | INER | 12139.6903
| PJB | 13157.557
| PMT | 1641.8771
PLTGU Total |  | 26939.1244
PLTP | INER | 2989.1158
| IPP | 3510.6451
PLTP Total |  | 6499.7609
PLTU | INER | 26943.8308
| IPP | 25584.4501
| PJB | 12098.8483
| (blank) | 1.6187
PLTU Total |  | 64628.7479
Grand Total |  | 105274.1483
IPP Generations (GWh)
Type | Owner | Total
PLTA | IPP | 703.228
PLTA Total |  | 703.228
PLTG | IPP | 401.3455
PLTG Total |  | 401.3455
PLTP | IPP | 3510.6451
PLTP Total |  | 3510.6451
PLTU | IPP | 25584.4501
PLTU Total |  | 25584.4501
Grand Total |  | 30199.6688

## ESAV
Baseline
Heat Generation |  | unit | Value
1 | Steam Enthalpy | MJ/t | 2767.5
2 | Flowrate | t/hr | 9.5
3 | Operation hour | hr/yr | 8000
4 | Residue boiler efficiency | fraction | 0.9
Energy Input for Heat Generation |  | TJ/yr | 233.7
Electrical Generation
1 | Electricity Output | MW | 11.88
2 | Operation hour | hr/yr | 8000
4 | Electrical generation efficiency (Max) | fraction | 0.4
Energy Input for Electricity Generation |  | TJ/yr | 855.36
Total Energy Input |  | TJ/yr | 1089.06
Project
Heat Generation (Waste heat boiler) |  | unit | Value
Energy Input for Heat Generation |  | TJ/yr | 0
Electrical Generation
1 | Electricity Output | MW | 11.88
2 | Operation hour | hr/yr | 8000
4 | Electrical generation efficiency (Max) | fraction | 0.418
Energy Input for Electricity Generation |  | TJ/yr | 818.52
Total Energy Input |  | TJ/yr | 818.52
Total Energy Savings |  |  | 24.84%